{"text_format":"2","workbook":"xls","n_sheets":4,"sheets":["Instructions","Parameters","Enumerations","Registers"],"not_rendered":{"charts":0,"images":4,"macros":0,"external_links":1,"defined_names":1941,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Instructions","index":0,"n_rows":8,"n_cols":1,"rows_kept":8,"cut":false,"hidden":false,"merged":[[5,0,5,10],[6,0,6,10],[7,0,7,10],[0,0,0,10],[1,0,1,10],[2,0,2,10],[4,0,4,10]],"flags":["formulas_cached_only"]}
["BBV51917    ATV12 - Communication Parameters - 1.4IE05"]
["DANGER"]
["UNINTENDED EQUIPMENT OPERATION\n•Read and understand this document, the User Manual and Modbus Manual before installing or operating the Altivar 12 drive.\n•Any changes made to the parameter settings must be performed by qualified personnel.\nFailure to follow these instructions will result in death or serious injury."]
[]
["WARNING"]
["LOSS OF CONTROL\n•The designer of any control scheme must\n    - consider the potential failure modes of control paths and, for certain critical control functions,\n    - provide a means to achieve a safe state during and after a path failure.\nExamples of critical control functions are emergency stop and overtravel stop.\n•Separate or redundant control paths must be provided for critical control functions.\n•System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. (see note a.)\nFailure to follow these instructions can result in death, serious injury, or equipment damage."]
["Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”"]
["Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material."]

{"sheet":"Parameters","index":1,"n_rows":241,"n_cols":16,"rows_kept":241,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Code","Name","Logic\n address","CANopen\n index","INTERBUS\n index","DeviceNet\n path","Link","Category","Access","Type","Units","Factory setting","Range","Display","Menu","Order"]
["CMD","Control word","16#2199 = 8601 (speed)\n16#2135 = 8501 (frequency)","-","-","-","CMD","Control parameters","R/W","WORD (BitString16)","-","-","-","","","1"]
["CMI","Extended control word","16#2138 = 08504","-","-","-","CMI","Control parameters","R/W","WORD (BitString16)","-","-","-","","","2"]
["RPR","Reset counters command","16#0C30 = 03120","-","-","-","RPR","Control parameters","R/W","WORD (Enumeration)","-","\"NO\"","-","(rPr)","(FLt-)","3"]
["LFRD","Speed setpoint","16#219A = 08602","-","-","-","-","Setpoint parameters","R/W","INT (Signed16)","1 rpm","0","-32767 rpm ... 32767 rpm","","","4"]
["LFR","Frequency setpoint","16#2136 = 08502","-","-","-","-","Setpoint parameters","R/W","INT (Signed16)","0.1 Hz","0","-3276.7 Hz ... 3276.7 Hz","(LFr)","(rEF-)\n(MOn-)\n(CtL-)","5"]
["PISP","PID regulator setpoint","16#2137 = 08503","-","-","-","-","Setpoint parameters","R/W","UINT (Unsigned16)","0.1 %","0","0 % ... 100 %","","","6"]
["AIV1","Analog input virtual","16#14A1 = 05281","-","-","-","-","Setpoint parameters","R/W","INT (Signed16)","0.1 %","0","0 % ... 100 %","(AIU1)","(rEF-)\n(MOn-)\n(CtL-)","7"]
["ETA","Status word","16#219B = 8603 (speed)\n16#0C81 = 3201 (frequency)","-","-","-","ETA","Status parameters","R","WORD (BitString16)","-","-","-","","","8"]
["HMIS","Product status","16#0CA8 = 03240","-","-","-","HMIS","Status parameters","R","WORD (Enumeration)","-","\"TUN\"","-","","","9"]
["ETI","Extended status word","16#0C86 = 03206","-","-","-","ETI","Status parameters","R","WORD (BitString16)","-","-","-","","","10"]
["CRC","Active reference channel","16#20F9 = 08441","-","-","-","CCC","Status parameters","R","WORD (BitString16)","-","-","-","","","11"]
["CCC","Active command channel","16#20FA = 08442","-","-","-","CCC","Status parameters","R","WORD (BitString16)","-","-","-","","","12"]
["RFRD","Output velocity","16#219C = 08604","-","-","-","-","Actual values parameters","R","INT (Signed16)","1 rpm","0","-32767 rpm ... 32767 rpm","","","13"]
["RFR","Estimated motor frequency (signed value)","16#0C82 = 03202","-","-","-","-","Actual values parameters","R","INT (Signed16)","0.1 Hz","0","-500 Hz ... 500 Hz","(rFr)","(MOn-)","14"]
["LCR","Estimated motor current","16#0C84 = 03204","-","-","-","-","Actual values parameters","R","UINT (Unsigned16)","0.1 A","0","0 A ... 6553.5 A","(LCr)","(MOn-)","15"]
["OPR","Output power monitoring (100% = nominal motor power)","16#0C8B = 03211","-","-","-","-","Actual values parameters","R","INT (Signed16)","1 %","0","-32767 % ... 32767 %","(OPr)","(MOn-)","16"]
["FRH","Frequency reference before ramp","16#0C83 = 03203","-","-","-","-","Reference parameters","R","INT (Signed16)","0.1 Hz","0","-3276.7 Hz ... 3276.7 Hz","(FrH)","(rEF-)\n(MOn-)","17"]
["RPC","PID reference after ramp","16#2ECE = 11982","-","-","-","-","Reference parameters","R","UINT (Unsigned16)","0.1 %","0","0 % ... 6553.5 %","(rPC)","(rEF-)\n(MOn-)","18"]
["RPF","PID regulator feedback reference","16#2ECD = 11981","-","-","-","-","Reference parameters","R","UINT (Unsigned16)","0.1 %","0","0 % ... 6553.5 %","(rPF)","(MOn-)","19"]
["RPE","PID regulator discrepancy","16#2ECC = 11980","-","-","-","-","Reference parameters","R","INT (Signed16)","0.1 %","0","-3276.7 % ... 3276.7 %","(rPE)","(MOn-)","20"]
["ULN","Main voltage (from DC bus)","16#0C87 = 03207","-","-","-","-","Measurement parameters","R","UINT (Unsigned16)","1 V","0","0 V ... 65535 V","(ULn)","(MOn-)","21"]
["THD","Drive thermal state","16#0C89 = 03209","-","-","-","-","Measurement parameters","R","UINT (Unsigned16)","1 %","0","0 % ... 200 %","(tHd)","(MOn-)","22"]
["THR","Motor thermal state","16#259E = 09630","-","-","-","-","Measurement parameters","R","UINT (Unsigned16)","1 %","0","0 % ... 200 %","(tHr)","(MOn-)","23"]
["PTH","Total drive operating time","16#0CA1 = 03233","-","-","-","-","Measurement parameters","R","UINT (Unsigned16)","0.01 h","0","0 h ... 655.35 h","(PtH)","(MAI-)","24"]
["TAC","IGBT alarm time","16#0CA3 = 03235","-","-","-","-","Measurement parameters","R/WS","UINT (Unsigned16)","1 s","0","0 s ... 65535 s","","","25"]
["TAC2","Time at the minimum frequency","16#0CAA = 03242","-","-","-","-","Measurement parameters","R/WS","UINT (Unsigned16)","1 s","0","0 s ... 65535 s","","","26"]
["FTO","Overload fault duration","16#3857 = 14423","-","-","-","-","Measurement parameters","R/W","UINT (Unsigned16)","1 min","0","0 min ... 6 min","(FtO)","(I_O-)\n(PMP-)","27"]
["NPL","Logic input type","16#1003 = 04099","-","-","-","NPL","I/O parameters","R/WS","WORD (Enumeration)","-","\"POS\"","-","(nPL)","(I_O-)","28"]
["IL1I","Logic inputs state","16#1451 = 05201","-","-","-","IL1I","I/O parameters","R","WORD (BitString16)","-","-","-","","","29"]
["OL1R","Logic outputs state","16#145C = 05212","-","-","-","OL1R","I/O parameters","R/W","WORD (BitString16)","-","-","-","","","30"]
["AI1I","Analogic input state","16#1466 = 05222","-","-","-","-","I/O parameters","R","INT (Signed16)","1","0","-32767 ... 32767","","","31"]
["AI1C","Analog input 1 physical value","16#147A = 05242","-","-","-","-","I/O parameters","R","INT (Signed16)","Refer to programming manual","0","Refer to programming manual","","","32"]
["AI1R","Analog input 1 standardized value","16#1470 = 05232","-","-","-","-","I/O parameters","R","INT (Signed16)","1","0","-32767 ... 32767","","","33"]
["AO1C","Analog output 1 physical value","16#1497 = 05271","-","-","-","-","I/O parameters","R/W","INT (Signed16)","Refer to programming manual","0","Refer to programming manual","","","34"]
["AO1R","Analog output 1 standardized value","16#148D = 05261","-","-","-","-","I/O parameters","R/W","INT (Signed16)","1","0","-32767 ... 32767","","","35"]
["LFT","Altivar fault code","16#1BD1 = 07121","-","-","-","LFT","Fault parameters","R","WORD (Enumeration)","-","\"NOF\"","-","","","36"]
["CIC","Incorrect configuration","16#1BDA = 07130","-","-","-","CIC","Fault parameters","R/WS","WORD (BitString16)","-","-","-","","","37"]
["DP0","Fault code on last fault","16#1C20 = 07200","-","-","-","LFT","History parameters","R","WORD (Enumeration)","-","\"NOF\"","-","","","38"]
["EP0","Status word on last fault","16#1C2A = 07210","-","-","-","EP0","History parameters","R","WORD (BitString16)","-","-","-","","","39"]
["DP1","Fault code on fault n-1","16#1C21 = 07201","-","-","-","LFT","History parameters","R","WORD (Enumeration)","-","\"NOF\"","-","(dP1)","(MAI-)","40"]
["ULP1","Supply voltage on fault n-1","16#1C67 = 07271","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 V","0","0 V ... 65535 V","","","41"]
["LCP1","Motor current on fault n-1","16#1C49 = 07241","-","-","-","-","History parameters","R","INT (Signed16)","0.1 A","0","-3276.7 A ... 3276.7 A","","","42"]
["RFP1","Output frequency on fault n-1","16#1C53 = 07251","-","-","-","-","History parameters","R","INT (Signed16)","0.1 Hz","0","-3276.7 Hz ... 3276.7 Hz","","","43"]
["EP1","Status word on fault n-1","16#1C2B = 07211","-","-","-","EP0","History parameters","R","WORD (BitString16)","-","-","-","(EP1)","(MAI-)","44"]
["RTP1","Motor operating time on fault n-1","16#1C5D = 07261","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 h","0","0 h ... 65535 h","","","45"]
["OTP1","Estimated Motor torque value at fault 1","16#1CA3 = 07331","-","-","-","-","History parameters","R","INT (Signed16)","1 %","0","-32767 % ... 32767 %","","","46"]
["TDP1","Measured drive thermal state at fault 1","16#1CAD = 07341","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 %","0","0 % ... 255 %","","","47"]
["TJP1","Estimated power component temperature (Tj) at fault 1","16#1CB7 = 07351","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 °C","0","0 °C ... 255 °C","","","48"]
["SFP1","Actual motor switching frequency at fault 1","16#1CC1 = 07361","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 Hz","0","0 Hz ... 65535 Hz","","","49"]
["DP2","Fault code on fault n-2","16#1C22 = 07202","-","-","-","LFT","History parameters","R","WORD (Enumeration)","-","\"NOF\"","-","(dP2)","(MAI-)","50"]
["ULP2","Supply voltage on fault n-2","16#1C68 = 07272","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 V","0","0 V ... 65535 V","","","51"]
["LCP2","Motor current on fault n-2","16#1C4A = 07242","-","-","-","-","History parameters","R","INT (Signed16)","0.1 A","0","-3276.7 A ... 3276.7 A","","","52"]
["RFP2","Output frequency on fault n-2","16#1C54 = 07252","-","-","-","-","History parameters","R","INT (Signed16)","0.1 Hz","0","-3276.7 Hz ... 3276.7 Hz","","","53"]
["EP2","Status word on fault n-2","16#1C2C = 07212","-","-","-","EP0","History parameters","R","WORD (BitString16)","-","-","-","(EP2)","(MAI-)","54"]
["RTP2","Motor operating time on fault n-2","16#1C5E = 07262","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 h","0","0 h ... 65535 h","","","55"]
["OTP2","Estimated Motor torque value at fault 2","16#1CA4 = 07332","-","-","-","-","History parameters","R","INT (Signed16)","1 %","0","-32767 % ... 32767 %","","","56"]
["TDP2","Measured drive thermal state at fault 2","16#1CAE = 07342","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 %","0","0 % ... 255 %","","","57"]
["TJP2","Estimated power component temperature (Tj) at fault 2","16#1CB8 = 07352","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 °C","0","0 °C ... 255 °C","","","58"]
["SFP2","Actual motor switching frequency at fault 2","16#1CC2 = 07362","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 Hz","0","0 Hz ... 65535 Hz","","","59"]
["DP3","Fault code on fault n-3","16#1C23 = 07203","-","-","-","LFT","History parameters","R","WORD (Enumeration)","-","\"NOF\"","-","(dP3)","(MAI-)","60"]
["ULP3","Supply voltage on fault n-3","16#1C69 = 07273","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 V","0","0 V ... 65535 V","","","61"]
["LCP3","Motor current on fault n-3","16#1C4B = 07243","-","-","-","-","History parameters","R","INT (Signed16)","0.1 A","0","-3276.7 A ... 3276.7 A","","","62"]
["RFP3","Output frequency on fault n-3","16#1C55 = 07253","-","-","-","-","History parameters","R","INT (Signed16)","0.1 Hz","0","-3276.7 Hz ... 3276.7 Hz","","","63"]
["EP3","Status word on fault n-3","16#1C2D = 07213","-","-","-","EP0","History parameters","R","WORD (BitString16)","-","-","-","(EP3)","(MAI-)","64"]
["RTP3","Motor operating time on fault n-3","16#1C5F = 07263","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 h","0","0 h ... 65535 h","","","65"]
["OTP3","Estimated Motor torque value at fault 3","16#1CA5 = 07333","-","-","-","-","History parameters","R","INT (Signed16)","1 %","0","-32767 % ... 32767 %","","","66"]
["TDP3","Measured drive thermal state at fault 3","16#1CAF = 07343","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 %","0","0 % ... 255 %","","","67"]
["TJP3","Estimated power component temperature (Tj) at fault 3","16#1CB9 = 07353","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 °C","0","0 °C ... 255 °C","","","68"]
["SFP3","Actual motor switching frequency at fault 3","16#1CC3 = 07363","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 Hz","0","0 Hz ... 65535 Hz","","","69"]
["DP4","Fault code on fault n-4","16#1C24 = 07204","-","-","-","LFT","History parameters","R","WORD (Enumeration)","-","\"NOF\"","-","(dP4)","(MAI-)","70"]
["ULP4","Supply voltage on fault n-4","16#1C6A = 07274","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 V","0","0 V ... 65535 V","","","71"]
["LCP4","Motor current on fault n-4","16#1C4C = 07244","-","-","-","-","History parameters","R","INT (Signed16)","0.1 A","0","-3276.7 A ... 3276.7 A","","","72"]
["RFP4","Output frequency on fault n-4","16#1C56 = 07254","-","-","-","-","History parameters","R","INT (Signed16)","0.1 Hz","0","-3276.7 Hz ... 3276.7 Hz","","","73"]
["EP4","Status word on fault n-4","16#1C2E = 07214","-","-","-","EP0","History parameters","R","WORD (BitString16)","-","-","-","(EP4)","(MAI-)","74"]
["RTP4","Motor operating time on fault n-4","16#1C60 = 07264","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 h","0","0 h ... 65535 h","","","75"]
["OTP4","Estimated Motor torque value at fault 4","16#1CA6 = 07334","-","-","-","-","History parameters","R","INT (Signed16)","1 %","0","-32767 % ... 32767 %","","","76"]
["TDP4","Measured drive thermal state at fault 4","16#1CB0 = 07344","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 %","0","0 % ... 255 %","","","77"]
["TJP4","Estimated power component temperature (Tj) at fault 4","16#1CBA = 07354","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 °C","0","0 °C ... 255 °C","","","78"]
["SFP4","Actual motor switching frequency at fault 4","16#1CC4 = 07364","-","-","-","-","History parameters","R","UINT (Unsigned16)","1 Hz","0","0 Hz ... 65535 Hz","","","79"]
["NCV","Drive nominal rating","16#0BC3 = 03011","-","-","-","NCV","Identification parameters","R/WS","WORD (Enumeration)","-","\"NO\"","-","(nCU)","(MAI-)","80"]
["VCAL","Drive line voltage","16#0BC4 = 03012","-","-","-","VCAL","Identification parameters","R/WS","WORD (Enumeration)","-","\"NO\"","-","(UCAL)","(MAI-)","81"]
["INV","Nominal drive current","16#0BC9 = 03017","-","-","-","-","Identification parameters","R","UINT (Unsigned16)","0.1 A","Depends of rating","0 A ... 6553.5 A","","","82"]
["VDP","Drive software version","16#0CE6 = 03302","-","-","-","-","Identification parameters","R","UINT (Unsigned16)","1","0","0 ... 65535","","","83"]
["SPN","Specific product number","16#0CE5 = 03301","-","-","-","-","Identification parameters","R/W","UINT (Unsigned16)","1","0","0 ... 65535","(SPn)","(MAI-)","84"]
["NC1","Communication scanner, value of write word 1","16#31D9 = 12761","-","-","-","-","Communication parameters","R/W","UINT (Unsigned16)","1","0","0 ... 65535","(nC1)","(OSA-)","85"]
["NC2","Communication scanner, value of write word 2","16#31DA = 12762","-","-","-","-","Communication parameters","R/W","UINT (Unsigned16)","1","0","0 ... 65535","(nC2)","(OSA-)","86"]
["NC3","Communication scanner, value of write word 3","16#31DB = 12763","-","-","-","-","Communication parameters","R/W","UINT (Unsigned16)","1","0","0 ... 65535","(nC3)","(OSA-)","87"]
["NC4","Communication scanner, value of write word 4","16#31DC = 12764","-","-","-","-","Communication parameters","R/W","UINT (Unsigned16)","1","0","0 ... 65535","(nC4)","(OSA-)","88"]
["NM1","Communication scanner, value of read word 1","16#31C5 = 12741","-","-","-","-","Communication parameters","R","UINT (Unsigned16)","1","0","0 ... 65535","(nM1)","(ISA-)","89"]
["NM2","Communication scanner, value of read word 2","16#31C6 = 12742","-","-","-","-","Communication parameters","R","UINT (Unsigned16)","1","0","0 ... 65535","(nM2)","(ISA-)","90"]
["NM3","Communication scanner, value of read word 3","16#31C7 = 12743","-","-","-","-","Communication parameters","R","UINT (Unsigned16)","1","0","0 ... 65535","(nM3)","(ISA-)","91"]
["NM4","Communication scanner, value of read word 4","16#31C8 = 12744","-","-","-","-","Communication parameters","R","UINT (Unsigned16)","1","0","0 ... 65535","(nM4)","(ISA-)","92"]
["SCS","Save configuration","16#1F41 = 08001","-","-","-","SCS","Configuration management","R/WS","WORD (Enumeration)","-","\"NO\"","-","(SCS)","(COnF-)","93"]
["FCS","Restore configuration","16#1F42 = 08002","-","-","-","FCS","Configuration management","R/WS","WORD (Enumeration)","-","\"NO\"","-","(FCS)","(COnF-)","94"]
["CFG","Macro configuration","16#0BEC = 03052","-","-","-","CFG","Simply start","R/WS","WORD (Enumeration)","-","\"STS\"","-","(CFG)","(FULL-)","95"]
["LSP","Low speed","16#0C21 = 03105","-","-","-","-","Settings","R/W","UINT (Unsigned16)","0.1 Hz","0","0 Hz ... 400 Hz","(LSP)","(SPL-)","96"]
["HSP","High speed","16#0C20 = 03104","-","-","-","-","Settings","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(HSP)","(SPL-)","97"]
["ITH","Motor thermal current","16#2596 = 09622","-","-","-","-","Settings","R/W","UINT (Unsigned16)","0.1 A","NCR","0 A ... 6553.5 A","(ItH)","(tHt-)","98"]
["SFC","Speed filter coefficient ( 0(IP) to 1(PI) )","16#2391 = 09105","-","-","-","-","Settings","R/W","UINT (Unsigned16)","1","Refer to programming manual","0 ... 100","(SFC)","(drC-)","99"]
["CTD","Motor current threshold","16#2AF9 = 11001","-","-","-","-","Settings","R/W","UINT (Unsigned16)","0.1 A","INV","0 A ... 6553.5 A","(Ctd)","(I_O-)","100"]
["FTD","Motor frequency threshold","16#2AFB = 11003","-","-","-","-","Settings","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(Ftd)","(I_O-)","101"]
["BFR","Basic frequency","16#0BC7 = 03015","-","-","-","BFR","Motor control","R/WS","WORD (Enumeration)","-","\"50\"","-","(bFr)","(drC-)","102"]
["NPR","Nominal Motor Power","16#258D = 09613","-","-","-","-","Motor control","R/WS","UINT (Unsigned16)","Refer to programming manual","Depends of rating","Refer to programming manual","(nPr)","(drC-)","103"]
["UNS","Nominal motor voltage","16#2581 = 09601","-","-","-","-","Motor control","R/WS","UINT (Unsigned16)","1 V","230","100 V ... 480 V","(UnS)","(drC-)","104"]
["NCR","Nominal motor current","16#2583 = 09603","-","-","-","-","Motor control","R/WS","UINT (Unsigned16)","0.1 A","Depends of rating","0 A ... 6553.5 A","(nCr)","(drC-)","105"]
["FRS","Nominal motor frequency","16#2582 = 09602","-","-","-","-","Motor control","R/WS","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","10 Hz ... 400 Hz","(FrS)","(drC-)","106"]
["NSP","Nominal motor speed","16#2584 = 09604","-","-","-","-","Motor control","R/WS","UINT (Unsigned16)","1 rpm","Depends of rating","0 rpm ... 24000 rpm","(nSP)","(drC-)","107"]
["COS","Rated motor cos Phi","16#2586 = 09606","-","-","-","-","Motor control","R/WS","UINT (Unsigned16)","0.01","Depends of rating","0.5 ... 1","(COS)","(drC-)","108"]
["MTM","Motor thermal state memo","16#2590 = 09616","-","-","-","N_Y","Motor control","R/WS","WORD (Enumeration)","-","\"NO\"","-","(MtM)","(tHt-)","109"]
["STUN","Autotune selection store","16#2591 = 09617","-","-","-","ACT","Motor control","R","WORD (Enumeration)","-","\"tAb\"","-","","","110"]
["FLG","Frequency loop gain","16#2594 = 09620","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","1 %","20","0 % ... 100 %","(FLG)","(drC-)","111"]
["STA","Frequency loop stability","16#2595 = 09621","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","1 %","20","0 % ... 100 %","(StA)","(drC-)","112"]
["TFR","Top frequency","16#0C1F = 03103","-","-","-","-","Motor control","R/WS","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","10 Hz ... 400 Hz","(tFr)","(drC-)","113"]
["TUN","Auto-tuning","16#2588 = 09608","-","-","-","TUN","Motor control","R/WS","WORD (Enumeration)","-","\"NO\"","-","(tUn)","(drC-)","114"]
["CTT","Motor control type assignment","16#2587 = 09607","-","-","-","CTT","Motor control","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(Ctt)","(drC-)","115"]
["UFR","IR compensation","16#2597 = 09623","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","1 %","100","25 % ... 200 %","(UFr)","(drC-)","116"]
["PFL","Flux profile","16#2598 = 09624","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","1 %","20","0 % ... 100 %","(PFL)","(drC-)","117"]
["SLP","Slip compensation","16#2599 = 09625","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","1 %","Refer to programming manual","0 % ... 150 %","(SLP)","(drC-)","118"]
["SPGU","Inertia gain for the derivative term of the UF laws","16#259D = 09629","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","1 %","40","0 % ... 1000 %","","","119"]
["RSM","Calculated (cold state) or measured stator resistance","16#25A8 = 09640","-","-","-","-","Motor control","R","UINT (Unsigned16)","1 mOhm","0","0 mOhm ... 65535 mOhm","","","120"]
["RSMI","Measured stator resistance","16#25A9 = 09641","-","-","-","-","Motor control","R","UINT (Unsigned16)","1","0","0 ... 65535","","","121"]
["SFT","Switching frequency type","16#0C1D = 03101","-","-","-","SFT","Motor control","R/WS","WORD (Enumeration)","-","\"HF1\"","-","(SFt)","(drC-)","122"]
["SFR","Switching frequency range","16#0C1E = 03102","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","0.1 kHz","40","2 kHz ... 16 kHz","(SFr)","(drC-)","123"]
["CLI","Current limitation","16#23F1 = 09201","-","-","-","-","Motor control","R/W","UINT (Unsigned16)","0.1 A","Depends of rating","0 A ... 6553.5 A","(CLI)","(CLI-)","124"]
["NRD","Motor noise reduction","16#0C23 = 03107","-","-","-","N_Y","Motor control","R/WS","WORD (Enumeration)","-","\"NO\"","-","(nrd)","(drC-)","125"]
["TCC","Type of control","16#2B5D = 11101","-","-","-","TCC","Inputs / outputs cfg","R/WS","WORD (Enumeration)","-","\"2C\"","-","(tCC)","(I_O-)","126"]
["TCT","2 wire type control","16#2B5E = 11102","-","-","-","TCT","Inputs / outputs cfg","R/WS","WORD (Enumeration)","-","\"TRN\"","-","(tCt)","(I_O-)","127"]
["RRS","Reverse direction","16#2B61 = 11105","-","-","-","PSL","Inputs / outputs cfg","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(rrS)","(FUn-)","128"]
["AI1T","AI1 type","16#1132 = 04402","-","-","-","AIOT","AI1 configuration","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(AI1t)","(AI1-)","129"]
["CRL1","AI1 current scaling parameter of 0%","16#1150 = 04432","-","-","-","-","AI1 configuration","R/WS","UINT (Unsigned16)","0.1 mA","40","0 mA ... 20 mA","(CrL1)","(AI1-)","130"]
["CRH1","AI1 current scaling parameter of 100%","16#115A = 04442","-","-","-","-","AI1 configuration","R/WS","UINT (Unsigned16)","0.1 mA","200","0 mA ... 20 mA","(CrH1)","(AI1-)","131"]
["R1","R1 assignment","16#1389 = 05001","-","-","-","PSL","R1 configuration","R/WS","WORD (Enumeration)","-","\"FLT\"","-","(r1)","(I_O-)","132"]
["R1S","R1 status (output active level)","16#1069 = 04201","-","-","-","NPL","R1 configuration","R/WS","WORD (Enumeration)","-","\"POS\"","-","","","133"]
["LO1","LO1 assignment","16#1391 = 05009","-","-","-","PSL","LO1 configuration","R/WS","WORD (Enumeration)","-","\"NO\"","-","(LO1)","(LO1-)","134"]
["LO1S","LO1 status (output active level)","16#1071 = 04209","-","-","-","NPL","LO1 configuration","R/WS","WORD (Enumeration)","-","\"POS\"","-","(LO1S)","(LO1-)","135"]
["AO1","AO1 assignment","16#139D = 05021","-","-","-","PSA","AO1 configuration","R/WS","WORD (Enumeration)","-","\"NO\"","-","(AO1)","(AO1-)","136"]
["AO1T","AO1 type","16#11F9 = 04601","-","-","-","AIOT","AO1 configuration","R/WS","WORD (Enumeration)","-","\"0A\"","-","(AO1t)","(AO1-)","137"]
["FR1","Reference source 1","16#20DD = 08413","-","-","-","PSA","Command","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(Fr1)","(CtL-)","138"]
["RIN","Reverse inhibition","16#0C24 = 03108","-","-","-","N_Y","Command","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(rIn)","(CtL-)","139"]
["PST","Stop key priority","16#FA02 = 64002","-","-","-","N_Y","Command","R/WS","WORD (Enumeration)","-","\"YES\"","-","(PSt)","(CtL-)","140"]
["CHCF","Channel configuration","16#20D1 = 08401","-","-","-","CHCF","Command","R/WS","WORD (Enumeration)","-","\"SIM\"","-","(CHCF)","(CtL-)","141"]
["CD1","Channel 1 command source","16#20E7 = 08423","-","-","-","CDX","Command","R/WS","WORD (Enumeration)","-","\"TER\"","-","(Cd1)","(CtL-)","142"]
["RPT","Shape ramp assignment","16#232C = 09004","-","-","-","RPT","Ramp","R/W","WORD (Enumeration)","-","\"LIN\"","-","(rPt)","(rPt-)","143"]
["ACC","Acceleration time (between 0 and FRS)","16#2329 = 09001","-","-","-","-","Ramp","R/W","UINT (Unsigned16)","0.1 s","30","0 s ... 999.9 s","(ACC)","(rPt-)","144"]
["DEC","Deceleration time (between FRS and 0)","16#232A = 09002","-","-","-","-","Ramp","R/W","UINT (Unsigned16)","0.1 s","30","0 s ... 999.9 s","(dEC)","(rPt-)","145"]
["RPS","Ramp switch assignment","16#2332 = 09010","-","-","-","PSL","Ramp","R/WS","WORD (Enumeration)","-","\"NO\"","-","(rPS)","(rPt-)","146"]
["AC2","Acceleration time 2 (between 0 and FRS)","16#2334 = 09012","-","-","-","-","Ramp","R/W","UINT (Unsigned16)","0.1 s","50","0 s ... 999.9 s","(AC2)","(rPt-)\n(PId-)","147"]
["DE2","Deceleration time 2 (between FRS and 0)","16#2335 = 09013","-","-","-","-","Ramp","R/W","UINT (Unsigned16)","0.1 s","50","0 s ... 999.9 s","(dE2)","(rPt-)","148"]
["BRA","Braking function assignment","16#232B = 09003","-","-","-","BRA","Ramp","R/WS","WORD (Enumeration)","-","\"YES\"","-","(brA)","(rPt-)","149"]
["STT","Stop mode","16#2BC1 = 11201","-","-","-","STT","Stop configuration","R/WS","WORD (Enumeration)","-","\"RMP\"","-","(Stt)","(Stt-)","150"]
["NST","Free wheel stop assignment","16#2BC2 = 11202","-","-","-","PSL","Stop configuration","R/WS","WORD (Enumeration)","-","\"NO\"","-","(nSt)","(Stt-)","151"]
["FST","Fast stop assignment","16#2BC4 = 11204","-","-","-","PSL","Stop configuration","R/WS","WORD (Enumeration)","-","\"NO\"","-","(FSt)","(Stt-)","152"]
["DCF","Deceleration ramp time reduction","16#2BDE = 11230","-","-","-","-","Stop configuration","R/W","UINT (Unsigned16)","1","4","1 ... 10","(dCF)","(Stt-)","153"]
["ADC","Automatic DC injection","16#28A1 = 10401","-","-","-","ADC","Auto DC injection","R/W","WORD (Enumeration)","-","\"YES\"","-","(AdC)","(AdC-)","154"]
["SDC1","Current level of automatic DC injection","16#28A3 = 10403","-","-","-","-","Auto DC injection","R/W","UINT (Unsigned16)","0.1 A","(0,7 * NCR)","0 A ... 6553.5 A","(SdC1)","(AdC-)","155"]
["TDC1","IDC injection time","16#28A2 = 10402","-","-","-","-","Auto DC injection","R/W","UINT (Unsigned16)","0.1 s","5","0.1 s ... 30 s","(tdC1)","(AdC-)","156"]
["JOG","Jog assignment","16#2B66 = 11110","-","-","-","PSL","JOG","R/WS","WORD (Enumeration)","-","\"NO\"","-","(JOG)","(FUn-)","157"]
["JGF","Jog frequency","16#2B67 = 11111","-","-","-","-","JOG","R/W","UINT (Unsigned16)","0.1 Hz","50","0 Hz ... 10 Hz","","","158"]
["PS2","2 preset speeds","16#2C89 = 11401","-","-","-","PSL","Preset speeds","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(PS2)","(PSS-)","159"]
["PS4","4 preset speeds","16#2C8A = 11402","-","-","-","PSL","Preset speeds","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(PS4)","(PSS-)","160"]
["PS8","8 preset speeds","16#2C8B = 11403","-","-","-","PSL","Preset speeds","R/WS","WORD (Enumeration)","-","\"NO\"","-","(PS8)","(PSS-)","161"]
["SP2","Preset speed 2","16#2C92 = 11410","-","-","-","-","Preset speeds","R/W","UINT (Unsigned16)","0.1 Hz","100","0 Hz ... 400 Hz","(SP2)","(PSS-)","162"]
["SP3","Preset speed 3","16#2C93 = 11411","-","-","-","-","Preset speeds","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(SP3)","(PSS-)","163"]
["SP4","Preset speed 4","16#2C94 = 11412","-","-","-","-","Preset speeds","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(SP4)","(PSS-)","164"]
["SP5","Preset speed 5","16#2C95 = 11413","-","-","-","-","Preset speeds","R/W","UINT (Unsigned16)","0.1 Hz","250","0 Hz ... 400 Hz","(SP5)","(PSS-)","165"]
["SP6","Preset speed 6","16#2C96 = 11414","-","-","-","-","Preset speeds","R/W","UINT (Unsigned16)","0.1 Hz","300","0 Hz ... 400 Hz","(SP6)","(PSS-)","166"]
["SP7","Preset speed 7","16#2C97 = 11415","-","-","-","-","Preset speeds","R/W","UINT (Unsigned16)","0.1 Hz","350","0 Hz ... 400 Hz","(SP7)","(PSS-)","167"]
["SP8","Preset speed 8","16#2C98 = 11416","-","-","-","-","Preset speeds","R/W","UINT (Unsigned16)","0.1 Hz","400","0 Hz ... 400 Hz","(SP8)","(PSS-)","168"]
["JPF","Skip frequency","16#2C25 = 11301","-","-","-","-","Jump frequency","R/W","UINT (Unsigned16)","0.1 Hz","0","0 Hz ... 400 Hz","(JPF)","(FUn-)","169"]
["PIF","PID : PI function feedback assignment","16#2E7D = 11901","-","-","-","PSA","PID regulator","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(PIF)","(PId-)","170"]
["TLS","Time limited speed (LSP)","16#2DB5 = 11701","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.1 s","0","[----](NO) ... 999.9 s","(tLS)","(PId-)\n(SPL-)","171"]
["FBS","PID Feedback scale factor","16#2E7F = 11903","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.1","10","0.1 ... 100","(FbS)","(PId-)","172"]
["PII","PID : PI internal reference selection","16#2E84 = 11908","-","-","-","N_Y","PID regulator","R/WS","WORD (Enumeration)","-","\"NO\"","-","(PII)","(PId-)","173"]
["RPI","PID : Internal reference PI","16#2E90 = 11920","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.1 %","0","0 % ... 100 %","(rPI)","(rEF-)\n(PId-)","174"]
["RPL","PID minimum value reference","16#2E87 = 11911","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.1 %","0","0 % ... 100 %","(rPL)","(PId-)","175"]
["RPH","PID max value reference","16#2E88 = 11912","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.1 %","1000","0 % ... 100 %","(rPH)","(PId-)","176"]
["RPG","PID : PI regulator proportional gain","16#2EA5 = 11941","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.01","100","0.01 ... 100","(rPG)","(PId-)","177"]
["RIG","PID : PI regulator integral gain","16#2EA6 = 11942","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.01","100","0.01 ... 100","(rIG)","(PId-)","178"]
["RDG","PID : PI regulator derivative gain","16#2EA7 = 11943","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.01","0","0 ... 100","(rdG)","(PId-)","179"]
["PRP","PID : ACC/DEC setpoint ramp parameter","16#2ED0 = 11984","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.1 s","0","0 s ... 99.9 s","(PrP)","(PId-)","180"]
["PIC","PID : PI regulator Reversal direction correction","16#2EA4 = 11940","-","-","-","N_Y","PID regulator","R/WS","WORD (Enumeration)","-","\"NO\"","-","(PIC)","(PId-)","181"]
["PAU","PID : Auto-manu","16#2EC2 = 11970","-","-","-","PSL","PID regulator","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(PAU)","(PId-)","182"]
["PIM","PID : Reference input in manual mode","16#2EB2 = 11954","-","-","-","PSA","PID regulator","R/WS","WORD (Enumeration)","-","\"NO\"","-","(PIM)","(PId-)","183"]
["SFS","PID predictive speed","16#2EB3 = 11955","-","-","-","-","PID regulator","R/WS","UINT (Unsigned16)","0.1 Hz","0","[----](NO) ... 400 Hz","(SFS)","(PId-)","184"]
["RSL","PID : Wake up threshold on PI error","16#2EB8 = 11960","-","-","-","-","PID regulator","R/WS","UINT (Unsigned16)","0.1 %","0","0 % ... 100 %","(rSL)","(PId-)","185"]
["UPP","Wake up threshold","16#2EBC = 11964","-","-","-","-","PID regulator","R/W","UINT (Unsigned16)","0.1 %","0","0 % ... 100 %","(UPP)","(PId-)","186"]
["LFF","Withdrawal frequency","16#1BA8 = 07080","-","-","-","-","PID regulator","R/WS","UINT (Unsigned16)","0.1 Hz","0","0 Hz ... 400 Hz","(LFF)","(PId-)\n(EtF-)","187"]
["LPI","Reaction threshold for PI monitoring function","16#2EBD = 11965","-","-","-","-","PID regulator","R/W","INT (Signed16)","0.1 %","-1","[----](NO) ... 100 %","(LPI)","(PId-)","188"]
["MPI","Behaviour of PI monitoring function","16#2EBF = 11967","-","-","-","ECFG","PID regulator","R/WS","WORD (Enumeration)","-","\"YES\"","-","(MPI)","(PId-)","189"]
["NFD","Period for PI state point checking","16#2ED6 = 11990","-","-","-","-","PID regulator","R/WS","UINT (Unsigned16)","1 min","0","[----](NO) ... 20 min","(nFd)","(PMP-)","190"]
["PR2","PID : Assignment for 2 presets PI","16#2E85 = 11909","-","-","-","PSL","PID preset references","R/WS","WORD (Enumeration)","-","\"NO\"","-","(Pr2)","(PId-)","191"]
["PR4","PID : Assignment for 4 presets PI","16#2E86 = 11910","-","-","-","PSL","PID preset references","R/WS","WORD (Enumeration)","-","\"NO\"","-","(Pr4)","(PId-)","192"]
["RP2","PID : Preset PI number 2","16#2E91 = 11921","-","-","-","-","PID preset references","R/W","UINT (Unsigned16)","0.1 %","250","0 % ... 100 %","(rP2)","(PId-)","193"]
["RP3","PID : Preset PI number 3","16#2E92 = 11922","-","-","-","-","PID preset references","R/W","UINT (Unsigned16)","0.1 %","500","0 % ... 100 %","(rP3)","(PId-)","194"]
["RP4","PID : Preset PI number 4","16#2E93 = 11923","-","-","-","-","PID preset references","R/W","UINT (Unsigned16)","0.1 %","750","0 % ... 100 %","(rP4)","(PId-)","195"]
["APO","???","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["FFD","Max speed for PI state point checking","16#2ED7 = 11991","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 Hz","0","0 Hz ... 400 Hz","(FFd)","(PMP-)","197"]
["FOF","Stopping frequency of the auxiliary pump","16#3B63 = 15203","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 Hz","0","0 Hz ... 400 Hz","(FOF)","(PMP-)","198"]
["FON","Starting frequency of the auxiliary pump","16#3B62 = 15202","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(FOn)","(PMP-)","199"]
["FTU","Underload fault duration","16#384D = 14413","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","1 min","0","0 min ... 6 min","(FtU)","(I_O-)\n(PMP-)","200"]
["LFD","Speed reference for PI state point checking","16#2ED8 = 11992","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 Hz","0","0 Hz ... 400 Hz","(LFd)","(PMP-)","201"]
["MDE","Selecting the operating mode","16#3B61 = 15201","-","-","-","N_Y","Pump application","R/WS","WORD (Enumeration)","-","\"NO\"","-","(MdE)","(PMP-)","202"]
["ROF","Ramp for stopping the auxiliary pump","16#3B67 = 15207","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 s","20","0 s ... 999.9 s","(rOF)","(PMP-)","203"]
["RON","Ramp for reaching the nominal speed of the auxiliary pump","16#3B66 = 15206","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 s","20","0 s ... 999.9 s","(rOn)","(PMP-)","204"]
["SLE","Stop on LSP hysteresis","16#2DB6 = 11702","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 Hz","10","0 Hz ... 400 Hz","(SLE)","(PId-)","205"]
["TOF","Time delay before the auxiliary pump stop command","16#3B65 = 15205","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 s","20","0 s ... 999.9 s","(tOF)","(PMP-)","206"]
["TON","Time delay before starting the auxiliary pump","16#3B64 = 15204","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","0.1 s","20","0 s ... 999.9 s","(tOn)","(PMP-)","207"]
["TPI","Reaction time for PI monitoring function","16#2EBE = 11966","-","-","-","-","Pump application","R/W","UINT (Unsigned16)","1 s","0","0 s ... 600 s","(tPI)","(PId-)","208"]
["INH","Fault inhibition assignment","16#1BD5 = 07125","-","-","-","PSL","Fault inhibition","R/WS","WORD (Enumeration)","-","\"NO\"","-","(InH)","(FLt-)","209"]
["SLL","Drive behaviour when ETIx.SLFEvent is detected on Modbus channel","16#1B62 = 07010","-","-","-","ECFG","Com. fault management","R/WS","WORD (Enumeration)","-","\"YES\"","-","(SLL)","(FLt-)","210"]
["LFL1","4-20 mA loos behaviour","16#1B69 = 07017","-","-","-","ECFG","Com. fault management","R/WS","WORD (Enumeration)","-","Refer to programming manual","-","(LFL1)","(FLt-)","211"]
["NCA1","Communication scanner, address of write word 1","16#31B1 = 12721","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","8501","0 ... 65535","(nCA1)","(OCS-)","212"]
["NCA2","Communication scanner, address of write word 2","16#31B2 = 12722","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","8602","0 ... 65535","(nCA2)","(OCS-)","213"]
["NCA3","Communication scanner, address of write word 3","16#31B3 = 12723","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","0","0 ... 65535","(nCA3)","(OCS-)","214"]
["NCA4","Communication scanner, address of write word 4","16#31B4 = 12724","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","0","0 ... 65535","(nCA4)","(OCS-)","215"]
["NMA1","Communication scanner, address of read word 1","16#319D = 12701","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","3201","0 ... 65535","(nMA1)","(ICS-)","216"]
["NMA2","Communication scanner, address of read word 2","16#319E = 12702","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","8604","0 ... 65535","(nMA2)","(ICS-)","217"]
["NMA3","Communication scanner, address of read word 3","16#319F = 12703","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","0","0 ... 65535","(nMA3)","(ICS-)","218"]
["NMA4","Communication scanner, address of read word 4","16#31A0 = 12704","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","0","0 ... 65535","(nMA4)","(ICS-)","219"]
["ADD","Terminal modbus : Drive address","16#1771 = 06001","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","1","0","[----](OFF) ... 247","(Add)","(COM-)","220"]
["TBR","Terminal modbus : Baud-rate","16#1773 = 06003","-","-","-","TBR","Communication","R/WS","WORD (Enumeration)","-","\"19K2\"","-","(tbr)","(COM-)","221"]
["TFO","Terminal modbus : Frame format","16#1774 = 06004","-","-","-","FOR","Communication","R/WS","WORD (Enumeration)","-","\"8E1\"","-","(tFO)","(COM-)","222"]
["TTO","Terminal modbus : Time-out","16#1775 = 06005","-","-","-","-","Communication","R/WS","UINT (Unsigned16)","0.1 s","100","0.1 s ... 30 s","(ttO)","(COM-)","223"]
["FLO","Forced local assignment","16#20EF = 08431","-","-","-","PSL","Communication","R/WS","WORD (Enumeration)","-","\"NO\"","-","(FLO)","(CtL-)","224"]
["FLOC","Forced local reference source assignment","16#20F0 = 08432","-","-","-","PSA","Communication","R/WS","WORD (Enumeration)","-","\"NO\"","-","(FLOC)","(CtL-)","225"]
["RTHI","Run elapsed time display","16#0CA0 = 03232","-","-","-","-","Measurement parameters","R","UINT (Unsigned16)","0.01 h","0","0 h ... 655.35 h","(rtHI)","(MAI-)","226"]
["PET","Process elapsed time","16#0CA4 = 03236","-","-","-","-","Measurement parameters","R/W","UINT (Unsigned16)","0.01 h","0","0 h ... 655.35 h","(PEt)","(MAI-)","227"]
["FTH","Fan time display","16#0CA7 = 03239","-","-","-","-","Measurement parameters","R","UINT (Unsigned16)","0.01 h","0","0 h ... 655.35 h","(FtH)","(MAI-)","228"]
["ULT","Application underload time delay","16#384B = 14411","-","-","-","-","Motor load management","R/WS","UINT (Unsigned16)","1 s","0","0 s ... 100 s","(ULt)","(I_O-)\n(PMP-)","229"]
["LUL","Application underload threshold","16#384F = 14415","-","-","-","-","Motor load management","R/W","UINT (Unsigned16)","1 %","60","20 % ... 100 %","(LUL)","(I_O-)\n(PMP-)","230"]
["TOL","Application Overload time delay","16#3855 = 14421","-","-","-","-","Motor load management","R/WS","UINT (Unsigned16)","1 s","0","0 s ... 100 s","(tOL)","(I_O-)\n(PMP-)","231"]
["LOC","Application overload threshold","16#3859 = 14425","-","-","-","-","Motor load management","R/W","UINT (Unsigned16)","1 %","90","70 % ... 150 %","(LOC)","(I_O-)\n(PMP-)","232"]
["SH2","2 HSP assignment","16#3AFD = 15101","-","-","-","PSL","Preset HSP","R/WS","WORD (Enumeration)","-","\"NO\"","-","(SH2)","(SPL-)","233"]
["SH4","4 HSP assignment","16#3AFE = 15102","-","-","-","PSL","Preset HSP","R/WS","WORD (Enumeration)","-","\"NO\"","-","(SH4)","(SPL-)","234"]
["HSU","Display of High speed value","16#3B05 = 15109","-","-","-","-","Preset HSP","R","UINT (Unsigned16)","0.1 Hz","0","0 Hz ... 400 Hz","(HSU)","(MAI-)","235"]
["HSP2","High speed 2","16#3B06 = 15110","-","-","-","-","Preset HSP","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(HSP2)","(SPL-)","236"]
["HSP3","High speed 3","16#3B07 = 15111","-","-","-","-","Preset HSP","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(HSP3)","(SPL-)","237"]
["HSP4","High speed 4","16#3B08 = 15112","-","-","-","-","Preset HSP","R/W","UINT (Unsigned16)","0.1 Hz","Refer to programming manual","0 Hz ... 400 Hz","(HSP4)","(SPL-)","238"]
["ETF","External fault assignment","16#1BDB = 7131","-","-","-","PSL","Inputs / outputs cfg","R/WS","WORD (Enumeration)","-","\"NO\"","-","(EtF)","(FLt-)","239"]
["EPL","Drive behaviour on external fault detection ","16#1B5E = 7006","-","-","-","ECFG","Stop configuration","R/WS","WORD (Enumeration)","-","\"YES\"","-","(EPL)","(FLt-)","240"]

{"sheet":"Enumerations","index":2,"n_rows":224,"n_cols":4,"rows_kept":224,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Code","Values","Display","Description"]
["ACT","0","(tAb)"]
[null,"1","(PEnd)"]
[null,"2","(PrOG)"]
[null,"3","(FAIL)"]
[null,"4","(dOnE)"]
["ADC","0","(nO)"]
[null,"1","(YES)"]
[null,"2","(Ct)"]
["AIOT","0","(5U)"]
[null,"1","(10U)"]
[null,"2","(0A)"]
[null,"3","(4A)"]
[null,"5","(n10U)"]
[null,"6","(GALU)"]
["BFR","0","(50Hz)"]
[null,"1","(60Hz)"]
["BRA","0","(nO)"]
[null,"1","(YES)"]
[null,"2","(dYnA)"]
["CDX","1","(tEr)"]
[null,"2","(LOC)"]
[null,"3","(LCC)"]
[null,"10","(Mdb)"]
["CFG","0","(StS)"]
[null,"4","(PId)"]
[null,"9","(SPd)"]
["CHCF","1","(SIM)"]
[null,"2","(SEP)"]
["CTT","0","(PErF)"]
[null,"3","(Std)"]
[null,"6","(PUMP)"]
["ECFG","0","(nO)"]
[null,"1","(YES)"]
[null,"4","(LFF)"]
["ERRD","16#0000","(LFF1)"]
[null,"16#0000","(XXXX)"]
[null,"16#0000","(nOF)"]
[null,"16#0000","(InF)"]
[null,"16#1000","(OLF)"]
[null,"16#1000","(CrF1)"]
[null,"16#1000","(SOF)"]
[null,"16#1000","(InFE)"]
[null,"16#2230","(SCF4)"]
[null,"16#2310","(OCF)"]
[null,"16#2311","(OLC)"]
[null,"16#2320","(SCF1)"]
[null,"16#2320","(SCF5)"]
[null,"16#2330","(SCF3)"]
[null,"16#3110","(OSF)"]
[null,"16#3120","(USF)"]
[null,"16#3130","(PHF)"]
[null,"16#3310","(OPF2)"]
[null,"16#3310","(OPF1)"]
[null,"16#3310","(ObF)"]
[null,"16#4210","(tJF)"]
[null,"16#4210","(OHF)"]
[null,"16#5210","(InF9)"]
[null,"16#5210","(InFb)"]
[null,"16#6100","(InF1)"]
[null,"16#6100","(InF4)"]
[null,"16#6100","(InF3)"]
[null,"16#6100","(InF2)"]
[null,"16#6300","(CFI)"]
[null,"16#6300","(CFI2)"]
[null,"16#6300","(CFF)"]
[null,"16#7510","(SLF1)"]
[null,"16#7510","(SLF3)"]
[null,"16#7530","(SLF2)"]
[null,"16#9000","(EPF1)"]
[null,"16#FF00","(tnF)"]
[null,"16#FF03","(ULF)"]
[null,"16#FF04","(SPIF)"]
["FCS","0","(nO)"]
[null,"2","(rEC1)"]
[null,"64","(InI)"]
[null,"71","(InI1)"]
["FOR","2","(8O1)"]
[null,"3","(8E1)"]
[null,"4","(8n1)"]
[null,"5","(8n2)"]
["HMIS","0","(tUn)"]
[null,"1","(dCb)"]
[null,"2","(rdY)"]
[null,"3","(nSt)"]
[null,"4","(rUn)"]
[null,"5","(ACC)"]
[null,"6","(dEC)"]
[null,"7","(CLI)"]
[null,"8","(FSt)"]
[null,"11","(nLP)"]
[null,"13","(CtL)"]
[null,"14","(Obr)"]
[null,"23","(FLt)"]
[null,"24","(FrF)"]
[null,"31","(rEM)"]
[null,"32","(LOC)"]
["LFT","0","(nOF)"]
[null,"1","(InF)"]
[null,"3","(CFF)"]
[null,"4","(CFI)"]
[null,"5","(SLF1)"]
[null,"8","(EPF1)"]
[null,"9","(OCF)"]
[null,"10","(CrF1)"]
[null,"16","(OHF)"]
[null,"17","(OLF)"]
[null,"18","(ObF)"]
[null,"19","(OSF)"]
[null,"20","(OPF1)"]
[null,"21","(PHF)"]
[null,"22","(USF)"]
[null,"23","(SCF1)"]
[null,"24","(SOF)"]
[null,"25","(tnF)"]
[null,"26","(InF1)"]
[null,"27","(InF2)"]
[null,"28","(InF3)"]
[null,"29","(InF4)"]
[null,"32","(SCF3)"]
[null,"33","(OPF2)"]
[null,"42","(SLF2)"]
[null,"45","(SLF3)"]
[null,"51","(InF9)"]
[null,"53","(InFb)"]
[null,"54","(tJF)"]
[null,"55","(SCF4)"]
[null,"56","(SCF5)"]
[null,"69","(InFE)"]
[null,"77","(CFI2)"]
[null,"100","(ULF)"]
[null,"101","(OLC)"]
[null,"102","(SPIF)"]
[null,"106","(LFF1)"]
[null,"253","(XXXX)"]
["N_Y","0","(nO)"]
[null,"1","(YES)"]
["NCV","0","(nO)"]
[null,"1","(U010)"]
[null,"2","(U018)"]
[null,"3","(U025)"]
[null,"4","(U037)"]
[null,"5","(U055)"]
[null,"6","(U075)"]
[null,"7","(U090)"]
[null,"8","(U110)"]
[null,"9","(U150)"]
[null,"10","(U185)"]
[null,"11","(U220)"]
[null,"12","(U300)"]
[null,"13","(U370)"]
[null,"14","(U400)"]
[null,"15","(U550)"]
[null,"16","(U750)"]
["NPL","0","(POS)"]
[null,"1","(nEG)"]
[null,"2","(EnEG)"]
["PSA","0","(nO)"]
[null,"1","(AI1)"]
[null,"129","(OCr)"]
[null,"130","(OFr)"]
[null,"131","(OrP)"]
[null,"135","(OPS)"]
[null,"136","(OPF)"]
[null,"137","(OPE)"]
[null,"139","(OPr)"]
[null,"140","(tHr)"]
[null,"141","(tHd)"]
[null,"163","(LCC)"]
[null,"164","(Mdb)"]
[null,"183","(AIU1)"]
["PSL","0","(nO)"]
[null,"1","(FLt)"]
[null,"2","(rUn)"]
[null,"4","(FtA)"]
[null,"5","(FLA)"]
[null,"6","(CtA)"]
[null,"7","(SrA)"]
[null,"8","(tSA)"]
[null,"10","(PEE)"]
[null,"11","(PFA)"]
[null,"21","(ULA)"]
[null,"22","(OLA)"]
[null,"123","(AP1)"]
[null,"126","(PMP)"]
[null,"129","(LI1)"]
[null,"130","(LI2)"]
[null,"131","(LI3)"]
[null,"132","(LI4)"]
[null,"145","(L1L)"]
[null,"146","(L2L)"]
[null,"147","(L3L)"]
[null,"148","(L4L)"]
["RPR","0","(nO)"]
[null,"3","(rtHI)"]
[null,"4","(PtH)"]
[null,"7","(FtH)"]
["RPT","0","(LIn)"]
[null,"1","(S)"]
[null,"2","(U)"]
["SCS","0","(nO)"]
[null,"2","(Str1)"]
["SFT","1","(HF1)"]
[null,"2","(HF2)"]
["STT","0","(rMP)"]
[null,"8","(FSt)"]
[null,"13","(nSt)"]
["TBR","24","(4800)"]
[null,"28","(9600)"]
[null,"32","(19200)"]
[null,"36","(38400)"]
["TCC","0","(2C)"]
[null,"1","(3C)"]
["TCT","0","(LEL)"]
[null,"1","(trn)"]
[null,"2","(PFO)"]
["TUN","0","(nO)"]
[null,"1","(YES)"]
[null,"2","(dOnE)"]
["VCAL","0","(nO)"]
[null,"1","(110M)"]
[null,"2","(110t)"]
[null,"3","(220M)"]
[null,"4","(220t)"]

{"sheet":"Registers","index":3,"n_rows":207,"n_cols":4,"rows_kept":207,"cut":false,"hidden":false,"merged":[[1,0,21,0],[22,0,49,0],[50,0,80,0],[81,0,105,0],[185,1,185,3],[186,0,206,0],[206,1,206,3],[106,0,126,0],[127,0,145,0],[146,0,164,0],[165,0,185,0]],"flags":["formulas_cached_only"]}
[]
["CMD",null,"bit 0:","= 1 : Switch on"]
[null,null,"bit 1:","= 0 : Disable voltage"]
[null,null,"bit 2:","= 0 : Quick stop/Emergency stop"]
[null,null,"bit 3:","= 1 : Enable operation/Run command"]
[]
[null,null,"bit 4:","Reserved (set to 0)."]
[null,null,"bit 5:","Reserved (set to 0)."]
[null,null,"bit 6:","Reserved (set to 0)."]
[null,null,"bit 7:","Fault reset/Fault acknowledgment active on 0 V 1 rising edge"]
[]
[null,null,"bit 8:","= 0 : RUN asked, 1 : STOP asked"]
[null,null,"bit 9:","Reserved (set to 0)."]
[null,null,"bit 10:","Reserved (set to 0)."]
[null,null,"bit 11:","Direction of rotation command "]
[null,null,null,"= 0: Forward rotation"]
[null,null,null,"= 1: Reverse rotation. Default value, this bit can be assigned to another command."]
[]
[null,null,"bit 12:","Reserved (set to 0)."]
[null,null,"bit 13:","Reserved (set to 0)."]
[null,null,"bit 14:","Reserved (set to 0)."]
[null,null,"bit 15:","Reserved (set to 0)."]
["CMI",null,"bit 0:","Factory setting command (active at 1)."]
[null,null,"bit 1:","Save configuration to EEPROM non-volatile memory command (active at 1)."]
[null,null,null,"This bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in \"5-Operation enabled\" state."]
[null,null,null,"Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations."]
[null,null,null,"Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS)."]
[null,null,"bit 2:","Reserved (= 0)."]
[null,null,"bit 3:","Reserved (= 0)."]
[]
[null,null,"bit 4:","Reserved (= 0)."]
[null,null,"bit 5:","Reserved (= 0)."]
[null,null,"bit 6:","Reserved (= 0)."]
[null,null,"bit 7:","Reserved (= 0)."]
[]
[null,null,"bit 8:","Reserved (= 0)."]
[null,null,"bit 9:","Definition of the frequency reference (LFr) and output frequency (rFr) unit:"]
[null,null,null,"= 0 : 0.1 Hz"]
[null,null,null,"= 1 : Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz."]
[null,null,null,"This function has no effect on the speed reference (LFrd) or the output speed (rFrd)."]
[null,null,"bit 10:","Reserved (= 0)."]
[null,null,"bit 11:","Reserved (= 0)."]
[]
[null,null,"bit 12:","Reserved (= 0)."]
[null,null,"bit 13:","Reserved (= 0)."]
[null,null,"bit 14:","Reserved (= 0)."]
[null,null,"bit 15:","Parameter consistency check"]
[null,null,null,"= 0: 'The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr)."]
[null,null,null,"= 1: 'The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written."]
[null,null,null,"The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive."]
["ETA",null,"bit 0:","= 1 : Ready to switch on"]
[null,null,"bit 1:","= 1 : Switched on, ready"]
[null,null,"bit 2:","= 1 : Operation enabled, running"]
[null,null,"bit 3:","= 1 : Fault detection"]
[]
[null,null,"bit 4:","Voltage enabled (always = 1)."]
[null,null,"bit 5:","= 0 : Quick stop/Emergency stop"]
[null,null,"bit 6:","= 1 : Switched on disabled"]
[null,null,"bit 7:","Reserved (= 0)"]
[]
[null,null,"bit 8:","Reserved (= 0)"]
[null,null,"bit 9:","Remote, command or reference via the network"]
[null,null,null,"= 0 : Command or reference via the terminals"]
[null,null,null,"= 1 : Command or reference via the network"]
[null,null,"bit 10:","Target reached, reference reached"]
[null,null,null,"= 0 : The reference is not reached"]
[null,null,null,"= 1 : The reference has been reached"]
[null,null,null,"When the drive stops, the reference has been reached."]
[null,null,"bit 11:","Internal limit active, reference outside limits"]
[null,null,null,"= 0 : The reference is within the limits"]
[null,null,null,"= 1 : The reference is not within the limits"]
[null,null,null,"The limits are defined by the \"Low speed (LSP)\" and \"High speed (HSP)\" parameters."]
[]
[null,null,"bit 12:","Reserved (= 0)"]
[null,null,"bit 13:","Reserved (= 0)"]
[null,null,"bit 14:","Stop key, STOP via stop key"]
[null,null,null,"= 0 : STOP key not pressed"]
[null,null,null,"= 1 : Stop triggered by the STOP key on the display terminal"]
[null,null,"bit 15:","Direction, direction of rotation"]
[null,null,null,"= 0 : Forward rotation at output"]
[null,null,null,"= 1 : Reverse rotation at output"]
["ETI",null,"bit 0:","= 1 : Access to the EEPROM non-volatile memory in progress"]
[null,null,"bit 1:","= 0 : No parameter consistency check"]
[null,null,null,"= 1 : Parameter consistency check"]
[null,null,"bit 2:","= 0 : The drive is not in fault state or a fault is detected"]
[null,null,null,"= 1 : The drive is in fault state but the fault is no longer present (not reset)"]
[null,null,"bit 3:","Reserved (= 0)."]
[]
[null,null,"bit 4:","= 1 : The drive is in speed mode"]
[null,null,"bit 5:","= 1 : DC injection"]
[null,null,"bit 6:","= 0 : Drive in steady state"]
[null,null,null,"= 1 : Drive in transient state"]
[null,null,"bit 7:","= 1 : Motor thermal state threshold reached for the active motor"]
[]
[null,null,"bit 8:","Reserved (= 0)."]
[null,null,"bit 9:","= 1 : Acceleration in progress"]
[null,null,"bit 10:","= 1 : Deceleration in progress"]
[null,null,"bit 11:","= 1 : Current limit in progress"]
[]
[null,null,"bit 12:","= 1 : Fast stop in progress"]
[null,null,"bit 13:","bit 13 = 0 and bit 14 = 0 : Drive controled by terminal or local keypad"]
[null,null,"bit 14:","bit 13 = 1 and bit 14 = 0 : Drive controled by remote keypad"]
[null,null,null,"bit 13 = 0 and bit 14 = 1 : Drive controled by Modbus"]
[null,null,null,"bit 13 = 1 and bit 14 = 1 : Reserved"]
[null,null,"bit 15:","= 0 : Forward operation applied before the ramp"]
[null,null,null,"= 1 : Reverse operation applied before the ramp"]
["EP0\nEP1\nEP2\nEP3\nEP4",null,"bit 0 :","= 1 : Switched on (Same as ETA.1)"]
[null,null,"bit 1 :","= 0 : Quick stop (Same as ETA.5)"]
[null,null,"bit 2 :","= 1 : Switch on disabled (Same as ETA.6)"]
[null,null,"bit 3 :","= 0 : Forced local mode in progress"]
[]
[null,null,"bit 4 :","= 0 : Motor rotation in forward direction (or stopped) (Same as ETA.15)"]
[null,null,"bit 5 :","= 1 : Run order present (Same as ETI.4)"]
[null,null,"bit 6 :","= 1 : DC injection running (Same as ETI.5)"]
[null,null,"bit 7 :","= 1 : Motor thermal threshold reached (Same as ETI.7)"]
[]
[null,null,"bit 8 :","Reserved (Same as ETI.8)"]
[null,null,"bit 9 :","= 1 : Product in acceleration (Same as ETI.9)"]
[null,null,"bit 10 :","= 1 : Product in deceleration (Same as ETI.10)"]
[null,null,"bit 11 :","= 1 : Current limit is running (Same as ETI.11)"]
[]
[null,null,"bit 12 :","= 1 : Fast stop in progress (Same as ETI.12)"]
[null,null,"bit 13:","bit 13 = 0 and bit 14 = 0 : Drive controled by terminal or local keypad (Same as ETI.13 and ETI.14))"]
[null,null,"bit 14:","bit 13 = 1 and bit 14 = 0 : Drive controled by remote keypad (Same as ETI.13 and ETI.14))"]
[null,null,null,"bit 13 = 0 and bit 14 = 1 : Drive controled by Modbus (Same as ETI.13 and ETI.14))"]
[null,null,null,"bit 13 = 1 and bit 14 = 1 : Reserved  (Same as ETI.13 and ETI.14))"]
[null,null,"bit 15:","= 1: Reverse operation applied before the ramp (Same as ETI.15)"]
["CCC\nCRC",null,"bit 0:","= 1: The terminal board is the active channel."]
[null,null,"bit 1:","= 1: The local keypad is the active channel."]
[null,null,"bit 2:","= 1: The remote keypad is the active channel."]
[null,null,"bit 3:","= 1: Modbus is the active channel."]
[]
[null,null,"bit 4:","Reserved (= 0)."]
[null,null,"bit 5:","Reserved (= 0)."]
[null,null,"bit 6:","Reserved (= 0)."]
[null,null,"bit 7:","Reserved (= 0)."]
[]
[null,null,"bit 8:","Reserved (= 0)."]
[null,null,"bit 9:","Reserved (= 0)."]
[null,null,"bit 10:","Reserved (= 0)."]
[null,null,"bit 11:","Reserved (= 0)."]
[]
[null,null,"bit 12:","Reserved (= 0)."]
[null,null,"bit 13:","Reserved (= 0)."]
[null,null,"bit 14:","Reserved (= 0)."]
[null,null,"bit 15:","= 1: SoMove software is the active channel."]
["IL1I",null,"bit 0:","Value of LI1."]
[null,null,"bit 1:","Value of LI2."]
[null,null,"bit 2:","Value of LI3."]
[null,null,"bit 3:","Value of LI4."]
[]
[null,null,"bit 4:","Reserved (= 0)."]
[null,null,"bit 5:","Reserved (= 0)."]
[null,null,"bit 6:","Reserved (= 0)."]
[null,null,"bit 7:","Reserved (= 0)."]
[]
[null,null,"bit 8:","Reserved (= 0)."]
[null,null,"bit 9:","Reserved (= 0)."]
[null,null,"bit 10:","Reserved (= 0)."]
[null,null,"bit 11:","Reserved (= 0)."]
[]
[null,null,"bit 12:","Reserved (= 0)."]
[null,null,"bit 13:","Reserved (= 0)."]
[null,null,"bit 14:","Reserved (= 0)."]
[null,null,"bit 15:","Reserved (= 0)."]
["OL1R",null,"bit 0:","Value of R1."]
[null,null,"bit 1:","Reserved (= 0)."]
[null,null,"bit 2:","Reserved (= 0)."]
[null,null,"bit 3:","Reserved (= 0)."]
[]
[null,null,"bit 4:","Reserved (= 0)."]
[null,null,"bit 5:","Reserved (= 0)."]
[null,null,"bit 6:","Reserved (= 0)."]
[null,null,"bit 7:","Reserved (= 0)."]
[]
[null,null,"bit 8:","Value of LO1."]
[null,null,"bit 9:","Reserved (= 0)."]
[null,null,"bit 10:","Reserved (= 0)."]
[null,null,"bit 11:","Reserved (= 0)."]
[]
[null,null,"bit 12:","Reserved (= 0)."]
[null,null,"bit 13:","Reserved (= 0)."]
[null,null,"bit 14:","Reserved (= 0)."]
[null,null,"bit 15:","Reserved (= 0)."]
[]
[null,"The outputs (relays or logic ouputs) can be controlled by the network. The outputs to control should not be assigned to a function of the drive, otherwise the writing is without effect."]
["CIC",null,"bit 0:","= 1: Change of rating."]
[null,null,"bit 1:","Reserved (= 0)."]
[null,null,"bit 2:","Reserved (= 0)."]
[null,null,"bit 3:","= 1: Saving to the EEPROM non-volatile memory is inconsistent with power on."]
[]
[null,null,"bit 4:","Reserved (= 0)."]
[null,null,"bit 5:","Reserved (= 0)."]
[null,null,"bit 6:","Reserved (= 0)."]
[null,null,"bit 7:","Reserved (= 0)."]
[]
[null,null,"bit 8:","Reserved (= 0)."]
[null,null,"bit 9:","Reserved (= 0)."]
[null,null,"bit 10:","Reserved (= 0)."]
[null,null,"bit 11:","Reserved (= 0)."]
[]
[null,null,"bit 12:","Reserved (= 0)."]
[null,null,"bit 13:","Reserved (= 0)."]
[null,null,"bit 14:","Reserved (= 0)."]
[null,null,"bit 15:","Reserved (= 0)."]
[]
[null,"If one of these events occurs, the drive will indicate a fault [Invalid config.] (CFI) and then automatically applies a factory setting."]