## Instructions
BQT67538_V3.6 | Altivar Solar ATV320 - Communication Parameters
WARNING
UNEXPECTED MOVEMENT Drive systems may perform unexpected movements because of incorrect wiring, incorrect settings, incorrect data or other errors. • Only appropriately trained persons who are familiar with and understand the contents of all pertinent product documentation and who have received safety training to recognize and avoid hazards involved are authorized to work on and with this drive system. Installation, adjustment, repair and maintenance must be performed by qualified personnel. • Carefully install the wiring in accordance with the EMC requirements. • Do not operate the product with unknown or unsuitable settings or data. • Perform a comprehensive commissioning test. Failure to follow these instructions can result in death, serious injury, or equipment damage.
WARNING
LOSS OF CONTROL • The designer of any control scheme must consider the potential failure modes of control paths and, for critical control functions, provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop, overtravel stop, power outage and restart. • Separate or redundant control paths must be provided for critical control functions. • System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. • Observe all accident prevention regulations and local safety guidelines (1). • Each implementation of the product must be individually and thoroughly tested for proper operation before being placed into service. Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the programming manual, which includes an index of parameter codes.
Additional information can be found in the Communication Manuals (Modbus, CANopen....etc.....)
Name: Parameter designation
Logic address: Addresses for Modbus, Profibus, Profinet and Ethernet TCP
Address for the messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index: Addresses for CANopen, PowerLink and EtherCAT.
CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
DeviceNet path : Address for DeviceNet and Ethernet IP.
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link: For WORD (listing), a dynamic link opens its description. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI). For WORD (bit register), in the Type column, a dynamic link opens its description.
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier.
Factory setting: Value of the parameter set at the factory.
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Range: Possible values.
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | DeviceNet path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 |  | Control parameters | R/W | WORD (BitString16) | -
CMD | Command register | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 |  | Control parameters | R/W | WORD (BitString16) | - |  |  | [Cmd Register] (CMD) | [Communication map] (CMM)
RPR | Counter reset | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] NO |  | [Counter Reset] (RPR) | [Power-On time] (PET) [Volume Counters] (VOLC)
LFRD | Speed setpoint | 16#219A = 8602 | 16#2038/3 | 16#8C/01/03 = 140/01/03 |  | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 rpm | -32767 rpm ... 32767 rpm
LFR | Reference frequency | 16#2136 = 8502 | 16#2037/3 | 16#8B/01/67 = 139/01/103 |  | Setpoint parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -599.0 Hz ... 599.0 Hz | [Ref Frequency] (LFR) | [Reference speed] (rEF) [MONITORING] (MON)
PISP | PIDSet point | 16#2137 = 8503 | 16#2037/4 | 16#8B/01/68 = 139/01/104 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 1000
AIV1 | AIV1 Image input | 16#14A1 = 5281 | 16#2016/52 | 16#7B/01/52 = 123/01/82 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [AIV1 Image input] (AIV1) | [Reference speed] (rEF) [MONITORING] (MON)
MFR | Multiplying coefficient | 16#2E37 = 11831 | 16#2058/20 | 16#9C/01/20 = 156/01/32 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [Multiplying coeff.] (MFR) | [Reference speed] (rEF) [MONITORING] (MON) [Settings] (SET)
ETA | Status Register | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 |  | Status parameters | R | WORD (BitString16) | - |  |  | [Status Register] (ETA) | [Communication map] (CMM)
HMIS | Device state | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | -
ETI | Internal State register | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 |  | Status parameters | R | WORD (BitString16) | -
CRC | Channel for reference frequency | 16#20F9 = 8441 | 16#2036/2A | 16#8B/01/2A = 139/01/42 |  | Status parameters | R | WORD (BitString16) | -
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 |  | Status parameters | R | WORD (BitString16) | -
CNFS | Active configuration | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | - |  |  | [Config. active] (CNFS) | [MONITORING] (MON)
STUN | Tune selection | 16#2591 = 9617 | 16#2042/12 | 16#91/01/12 = 145/01/18 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] TAB |  | [Tune selection] (STUN) | [Simply start] (SIM) [Asynchronous motor] (ASY) [Synchronous motor] (SYN)
SMOT | Status of motor tune in term of saliency | 16#25AD = 9645 | 16#2042/2E | 16#91/01/2E = 145/01/46 | SMOT | Status parameters | R | WORD (Enumeration) | - |  |  | [Saliency mot. state] (SMOT) | [Synchronous motor] (SYN)
ECSS | EtherCAT slave status | 16#1A22 = 6690 | 16#2024/5B | 16#82/01/5B = 130/01/91 | ETST | Status parameters | R/W | WORD (Enumeration) | - |  |  | [EthCat slave status] (ECSS) | [Communication module] (CBD)
ECAA | EtherCAT address | 16#1A24 = 6692 | 16#2024/5D | 16#82/01/5D = 130/01/93 |  | Status parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat addr] (ECAA) | [Communication module] (CBD)
RFRD | Output velocity | 16#219C = 8604 | 16#2038/5 | 16#8C/01/05 = 140/01/05 |  | Actual values parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
RFR | Motor frequency | 16#0C82 = 3202 | 16#2002/3 | 16#71/01/03 = 113/01/03 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor Frequency] (RFR) | [MONITORING] (MON)
OTR | Motor torque | 16#0C85 = 3205 | 16#2002/6 | 16#71/01/06 = 113/01/06 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor torque] (OTR) | [MONIT. MOTOR] (MMO)
LCR | Motor current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A | [Motor Current] (LCR) | [MONIT. MOTOR] (MMO)
UOP | Motor voltage | 16#0C88 = 3208 | 16#2002/9 | 16#71/01/09 = 113/01/09 |  | Actual values parameters | R | UINT (Unsigned16) | 1 V |  | 0 V ... 65535 V | [Motor voltage] (UOP) | [MONIT. MOTOR] (MMO)
OPR | Motor power in % | 16#0C8B = 3211 | 16#2002/C | 16#71/01/0C = 113/01/12 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Mot Mech Power in %] (OPR) | [MONIT. MOTOR] (MMO)
FRHD | Speed reference before ramp | 16#219D = 8605 | 16#2038/6 | 16#8C/01/06 = 140/01/06 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FROD | Speed reference after ramp | 16#21C1 = 8641 | 16#2038/2A | 16#8C/01/2A = 140/01/42 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FRH | Reference frequency before ramp | 16#0C83 = 3203 | 16#2002/4 | 16#71/01/04 = 113/01/04 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -599.0 Hz ... 599.0 Hz | [Pre-Ramp Ref Freq] (FRH) | [Reference speed] (rEF) [MONITORING] (MON) [Communication map] (CMM)
FRO | Frequency reference after ramp | 16#233D = 9021 | 16#203C/16 | 16#8E/01/16 = 142/01/22 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
RPC | PID reference | 16#2ECE = 11982 | 16#2059/53 | 16#9C/01/B7 = 156/01/183 |  | Reference parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [PID reference] (RPC) | [Reference speed] (rEF) [MONIT. PI] (MPI)
RPF | PID feedback | 16#2ECD = 11981 | 16#2059/52 | 16#9C/01/B6 = 156/01/182 |  | Reference parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [PID feedback] (RPF) | [MONIT. PI] (MPI)
RPE | PID error | 16#2ECC = 11980 | 16#2059/51 | 16#9C/01/B5 = 156/01/181 |  | Reference parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 | [PID Error] (RPE) | [MONIT. PI] (MPI)
RPO | PID output | 16#2ECF = 11983 | 16#2059/54 | 16#9C/01/B8 = 156/01/184 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [PID Output] (RPO) | [MONIT. PI] (MPI)
ULN | Mains voltage | 16#0C87 = 3207 | 16#2002/8 | 16#71/01/08 = 113/01/08 |  | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULN) | [MONITORING] (MON)
THD | Drive thermal state | 16#0C89 = 3209 | 16#2002/A | 16#71/01/0A = 113/01/10 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Drive Therm State] (THD) | [MONITORING] (MON)
THR | Motor thermal state | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Motor Therm State] (THR) | [MONITORING] (MON)
RTH | Motor run time | 16#0C9F = 3231 | 16#2002/20 | 16#71/01/20 = 113/01/32 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Run Time] (RTH) | [Power-On time] (PET)
PTH | Power-on time | 16#0CA1 = 3233 | 16#2002/22 | 16#71/01/22 = 113/01/34 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Power-on time] (PTH) | [Power-On time] (PET)
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 |  | I/O parameters | R | WORD (BitString16) | -
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 |  | I/O parameters | R/W | WORD (BitString16) | -
AI1C | Physical value AI1 | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 |  | I/O parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2C | Physical value AI2 | 16#147B = 5243 | 16#2016/2C | 16#7B/01/2C = 123/01/44 |  | I/O parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
AI2R | Analog input 2 standardized value | 16#1471 = 5233 | 16#2016/22 | 16#7B/01/22 = 123/01/34 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3C | Physical value AI3 | 16#147C = 5244 | 16#2016/2D | 16#7B/01/2D = 123/01/45 |  | I/O parameters | R | INT (Signed16) | 0.001 mA |  | -32.767 mA ... 32.767 mA
AI3R | Analog input 3 standardized value | 16#1472 = 5234 | 16#2016/23 | 16#7B/01/23 = 123/01/35 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1C | AQ1 physical value | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
FQS | Pulse input measured frequency | 16#390B = 14603 | 16#2074/4 | 16#AA/01/04 = 170/01/04 |  | I/O parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 20000 Hz | [Measured Freq] (FQS) | [MONITORING] (MON)
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 | ERRD | Fault parameters | R | WORD (BitString16) | -
LFT | Last error occurred | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | -
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 |  | Fault parameters | R/WS | WORD (BitString16) | -
CNF | Fieldbus module Communication interruption | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Fieldbus Com Interrupt] (CNF) | [More error info] (AFI) [Communication module] (CBD)
ILF1 | Internal communication interruption 1 | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [InternCom Error1] (ILF1) | [More error info] (AFI) [Communication module] (CBD)
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
ULP0 | Mains voltage | 16#1C66 = 7270 | 16#202A/47 | 16#85/01/47 = 133/01/71 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
LCP0 | Motor current | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A
RFP0 | Output frequency | 16#1C52 = 7250 | 16#202A/33 | 16#85/01/33 = 133/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
THP0 | Motor thermal state | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
EP0 | State word | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 |  | History parameters | R | WORD (BitString16) | -
IP0 | ETI state word | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 |  | History parameters | R | WORD (BitString16) | -
CMP0 | Cmd word | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 |  | History parameters | R | WORD (BitString16) | -
DCC0 | Command channel | 16#FB2C = 64300 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
DRC0 | Channel for reference frequency | 16#FB36 = 64310 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
CRP0 | Channels active on last fault | 16#1C7A = 7290 | 16#202A/5B | 16#85/01/5B = 133/01/91 |  | History parameters | R | WORD (BitString16) | -
RTP0 | Run Elapsed time | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
OTP0 | Motor torque | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP0 | Drive thermal state | 16#1CAC = 7340 | 16#202B/29 | 16#85/01/8D = 133/01/141 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP0 | IGBT junction temp | 16#1CB6 = 7350 | 16#202B/33 | 16#85/01/97 = 133/01/151 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP0 | Switching frequency | 16#1CC0 = 7360 | 16#202B/3D | 16#85/01/A1 = 133/01/161 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
ULP1 | Mains voltage | 16#1C67 = 7271 | 16#202A/48 | 16#85/01/48 = 133/01/72 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP1) | [None] (DP1)
LCP1 | Motor current | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP1) | [None] (DP1)
RFP1 | Output frequency | 16#1C53 = 7251 | 16#202A/34 | 16#85/01/34 = 133/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP1) | [None] (DP1)
THP1 | Motor thermal state | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP1) | [None] (DP1)
EP1 | Status of last error 1 | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 1 Status] (EP1) | [None] (DP1)
IP1 | ETI state word | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP1) | [None] (DP1)
CMP1 | Cmd word | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP1) | [None] (DP1)
DCC1 | Command channel | 16#FB2D = 64301 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC1) | [None] (DP1)
DRC1 | Channel for reference frequency | 16#FB37 = 64311 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC1) | [None] (DP1)
CRP1 | Active channels on fault n-1 | 16#1C7B = 7291 | 16#202A/5C | 16#85/01/5C = 133/01/92 |  | History parameters | R | WORD (BitString16) | -
RTP1 | Run Elapsed time | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP1) | [None] (DP1)
OTP1 | Motor torque | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP1 | Drive thermal state | 16#1CAD = 7341 | 16#202B/2A | 16#85/01/8E = 133/01/142 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP1 | IGBT junction temp | 16#1CB7 = 7351 | 16#202B/34 | 16#85/01/98 = 133/01/152 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP1 | Switching frequency | 16#1CC1 = 7361 | 16#202B/3E | 16#85/01/A2 = 133/01/162 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
ULP2 | Mains voltage | 16#1C68 = 7272 | 16#202A/49 | 16#85/01/49 = 133/01/73 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP2) | [None] (DP2)
LCP2 | Motor current | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP2) | [None] (DP2)
RFP2 | Output frequency | 16#1C54 = 7252 | 16#202A/35 | 16#85/01/35 = 133/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP2) | [None] (DP2)
THP2 | Motor thermal state | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP2) | [None] (DP2)
EP2 | Status of last error 2 | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 2 Status] (EP2) | [None] (DP2)
IP2 | ETI state word | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP2) | [None] (DP2)
CMP2 | Cmd word | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP2) | [None] (DP2)
DCC2 | Command channel | 16#FB2E = 64302 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC2) | [None] (DP2)
DRC2 | Channel for reference frequency | 16#FB38 = 64312 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC2) | [None] (DP2)
CRP2 | Active channels on fault n-2 | 16#1C7C = 7292 | 16#202A/5D | 16#85/01/5D = 133/01/93 |  | History parameters | R | WORD (BitString16) | -
RTP2 | Run Elapsed time | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP2) | [None] (DP2)
OTP2 | Motor torque | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP2 | Drive thermal state | 16#1CAE = 7342 | 16#202B/2B | 16#85/01/8F = 133/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP2 | IGBT junction temp | 16#1CB8 = 7352 | 16#202B/35 | 16#85/01/99 = 133/01/153 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP2 | Switching frequency | 16#1CC2 = 7362 | 16#202B/3F | 16#85/01/A3 = 133/01/163 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
ULP3 | Mains voltage | 16#1C69 = 7273 | 16#202A/4A | 16#85/01/4A = 133/01/74 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP3) | [None] (DP3)
LCP3 | Motor current | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP3) | [None] (DP3)
RFP3 | Output frequency | 16#1C55 = 7253 | 16#202A/36 | 16#85/01/36 = 133/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP3) | [None] (DP3)
THP3 | Motor thermal state | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP3) | [None] (DP3)
EP3 | Status of last error 3 | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 3 Status] (EP3) | [None] (DP3)
IP3 | ETI state word | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP3) | [None] (DP3)
CMP3 | Cmd word | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP3) | [None] (DP3)
DCC3 | Command channel | 16#FB2F = 64303 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC3) | [None] (DP3)
DRC3 | Channel for reference frequency | 16#FB39 = 64313 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC3) | [None] (DP3)
CRP3 | Active channels on fault n-3 | 16#1C7D = 7293 | 16#202A/5E | 16#85/01/5E = 133/01/94 |  | History parameters | R | WORD (BitString16) | -
RTP3 | Run Elapsed time | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP3) | [None] (DP3)
OTP3 | Motor torque | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP3 | Drive thermal state | 16#1CAF = 7343 | 16#202B/2C | 16#85/01/90 = 133/01/144 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP3 | IGBT junction temp | 16#1CB9 = 7353 | 16#202B/36 | 16#85/01/9A = 133/01/154 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP3 | Switching frequency | 16#1CC3 = 7363 | 16#202B/40 | 16#85/01/A4 = 133/01/164 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
ULP4 | Mains voltage | 16#1C6A = 7274 | 16#202A/4B | 16#85/01/4B = 133/01/75 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP4) | [None] (DP4)
LCP4 | Motor current | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP4) | [None] (DP4)
RFP4 | Output frequency | 16#1C56 = 7254 | 16#202A/37 | 16#85/01/37 = 133/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP4) | [None] (DP4)
THP4 | Motor thermal state | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP4) | [None] (DP4)
EP4 | Status of last error 4 | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 4 Status] (EP4) | [None] (DP4)
IP4 | ETI state word | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP4) | [None] (DP4)
CMP4 | Cmd word | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP4) | [None] (DP4)
DCC4 | Command channel | 16#FB30 = 64304 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC4) | [None] (DP4)
DRC4 | Channel for reference frequency | 16#FB3A = 64314 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC4) | [None] (DP4)
CRP4 | Active channels on fault n-4 | 16#1C7E = 7294 | 16#202A/5F | 16#85/01/5F = 133/01/95 |  | History parameters | R | WORD (BitString16) | -
RTP4 | Run Elapsed time | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP4) | [None] (DP4)
OTP4 | Motor torque | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP4 | Drive thermal state | 16#1CB0 = 7344 | 16#202B/2D | 16#85/01/91 = 133/01/145 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP4 | IGBT junction temp | 16#1CBA = 7354 | 16#202B/37 | 16#85/01/9B = 133/01/155 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP4 | Switching frequency | 16#1CC4 = 7364 | 16#202B/41 | 16#85/01/A5 = 133/01/165 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
ULP5 | Mains voltage | 16#1C6B = 7275 | 16#202A/4C | 16#85/01/4C = 133/01/76 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP5) | [None] (DP5)
LCP5 | Motor current | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP5) | [None] (DP5)
RFP5 | Output frequency | 16#1C57 = 7255 | 16#202A/38 | 16#85/01/38 = 133/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP5) | [None] (DP5)
THP5 | Motor thermal state | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP5) | [None] (DP5)
EP5 | State word | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP5) | [None] (DP5)
IP5 | ETI state word | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP5) | [None] (DP5)
CMP5 | Cmd word | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP5) | [None] (DP5)
DCC5 | Command channel | 16#FB31 = 64305 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC5) | [None] (DP5)
DRC5 | Channel for reference frequency | 16#FB3B = 64315 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC5) | [None] (DP5)
CRP5 | Active channels on fault n-5 | 16#1C7F = 7295 | 16#202A/60 | 16#85/01/60 = 133/01/96 |  | History parameters | R | WORD (BitString16) | -
RTP5 | Run Elapsed time | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP5) | [None] (DP5)
OTP5 | Motor torque | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP5 | Drive thermal state | 16#1CB1 = 7345 | 16#202B/2E | 16#85/01/92 = 133/01/146 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP5 | IGBT junction temp | 16#1CBB = 7355 | 16#202B/38 | 16#85/01/9C = 133/01/156 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP5 | Switching frequency | 16#1CC5 = 7365 | 16#202B/42 | 16#85/01/A6 = 133/01/166 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | -
ULP6 | Mains voltage | 16#1C6C = 7276 | 16#202A/4D | 16#85/01/4D = 133/01/77 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP6) | [None] (DP6)
LCP6 | Motor current | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP6) | [None] (DP6)
RFP6 | Output frequency | 16#1C58 = 7256 | 16#202A/39 | 16#85/01/39 = 133/01/57 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP6) | [None] (DP6)
THP6 | Motor thermal state | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP6) | [None] (DP6)
EP6 | State word | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP6) | [None] (DP6)
IP6 | ETI state word | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP6) | [None] (DP6)
CMP6 | Cmd word | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP6) | [None] (DP6)
DCC6 | Command channel | 16#FB32 = 64306 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC6) | [None] (DP6)
DRC6 | Channel for reference frequency | 16#FB3C = 64316 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC6) | [None] (DP6)
CRP6 | Active channels on fault n-6 | 16#1C80 = 7296 | 16#202A/61 | 16#85/01/61 = 133/01/97 |  | History parameters | R | WORD (BitString16) | -
RTP6 | Run Elapsed time | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP6) | [None] (DP6)
OTP6 | Motor torque | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP6 | Drive thermal state | 16#1CB2 = 7346 | 16#202B/2F | 16#85/01/93 = 133/01/147 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP6 | IGBT junction temp | 16#1CBC = 7356 | 16#202B/39 | 16#85/01/9D = 133/01/157 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP6 | Switching frequency | 16#1CC6 = 7366 | 16#202B/43 | 16#85/01/A7 = 133/01/167 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | -
ULP7 | Mains voltage | 16#1C6D = 7277 | 16#202A/4E | 16#85/01/4E = 133/01/78 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP7) | [None] (DP7)
LCP7 | Motor current | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP7) | [None] (DP7)
RFP7 | Output frequency | 16#1C59 = 7257 | 16#202A/3A | 16#85/01/3A = 133/01/58 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP7) | [None] (DP7)
THP7 | Motor thermal state | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP7) | [None] (DP7)
EP7 | State word | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP7) | [None] (DP7)
IP7 | ETI state word | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP7) | [None] (DP7)
CMP7 | Cmd word | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP7) | [None] (DP7)
DCC7 | Command channel | 16#FB33 = 64307 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC7) | [None] (DP7)
DRC7 | Channel for reference frequency | 16#FB3D = 64317 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC7) | [None] (DP7)
CRP7 | Active channels on fault n-7 | 16#1C81 = 7297 | 16#202A/62 | 16#85/01/62 = 133/01/98 |  | History parameters | R | WORD (BitString16) | -
RTP7 | Run Elapsed time | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP7) | [None] (DP7)
OTP7 | Motor torque | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP7 | Drive thermal state | 16#1CB3 = 7347 | 16#202B/30 | 16#85/01/94 = 133/01/148 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP7 | IGBT junction temp | 16#1CBD = 7357 | 16#202B/3A | 16#85/01/9E = 133/01/158 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP7 | Switching frequency | 16#1CC7 = 7367 | 16#202B/44 | 16#85/01/A8 = 133/01/168 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | -
ULP8 | Mains voltage | 16#1C6E = 7278 | 16#202A/4F | 16#85/01/4F = 133/01/79 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULP8) | [None] (DP8)
LCP8 | Motor current | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 |  | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A | [Motor current] (LCP8) | [None] (DP8)
RFP8 | Output frequency | 16#1C5A = 7258 | 16#202A/3B | 16#85/01/3B = 133/01/59 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP8) | [None] (DP8)
THP8 | Motor thermal state | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP8) | [None] (DP8)
EP8 | State word | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP8) | [None] (DP8)
IP8 | ETI state word | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP8) | [None] (DP8)
CMP8 | Cmd word | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP8) | [None] (DP8)
DCC8 | Command channel | 16#FB34 = 64308 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC8) | [None] (DP8)
DRC8 | Channel for reference frequency | 16#FB3E = 64318 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC8) | [None] (DP8)
CRP8 | Active channels on fault n-8 | 16#1C82 = 7298 | 16#202A/63 | 16#85/01/63 = 133/01/99 |  | History parameters | R | WORD (BitString16) | -
RTP8 | Run Elapsed time | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP8) | [None] (DP8)
OTP8 | Motor torque | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP8 | Drive thermal state | 16#1CB4 = 7348 | 16#202B/31 | 16#85/01/95 = 133/01/149 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP8 | IGBT junction temp | 16#1CBE = 7358 | 16#202B/3B | 16#85/01/9F = 133/01/159 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP8 | Switching frequency | 16#1CC8 = 7368 | 16#202B/45 | 16#85/01/A9 = 133/01/169 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
NCV | Drive nominal rating | 16#0BC3 = 3011 | 16#2000/C | 16#70/01/0C = 112/01/12 | NCV | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] NO
VCAL | Drive mains voltage | 16#0BC4 = 3012 | 16#2000/D | 16#70/01/0D = 112/01/13 | VCAL | Identification parameters | R | WORD (Enumeration) | - | [Unkown voltage] NO
INV | Nominal Drive current | 16#0BC9 = 3017 | 16#2000/12 | 16#70/01/12 = 112/01/18 |  | Identification parameters | R | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A
VDP | Device software version | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
PAN0 | Device name (char 1 and 2) | 16#0D0C = 3340 | 16#2003/29 | 16#71/01/8D = 113/01/141 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN1 | Device name (char 3 and 4) | 16#0D0D = 3341 | 16#2003/2A | 16#71/01/8E = 113/01/142 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN2 | Device name (char 5 and 6) | 16#0D0E = 3342 | 16#2003/2B | 16#71/01/8F = 113/01/143 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN3 | Device name (char 7 and 8) | 16#0D0F = 3343 | 16#2003/2C | 16#71/01/90 = 113/01/144 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN4 | Device name (char 9 and 10) | 16#0D10 = 3344 | 16#2003/2D | 16#71/01/91 = 113/01/145 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN5 | Device name (char 11 and 12) | 16#0D11 = 3345 | 16#2003/2E | 16#71/01/92 = 113/01/146 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN6 | Device name (char 13 and 14) | 16#0D12 = 3346 | 16#2003/2F | 16#71/01/93 = 113/01/147 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN7 | Device name (char 15 and 16) | 16#0D13 = 3347 | 16#2003/30 | 16#71/01/94 = 113/01/148 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NC1 | Com scan output 1 value | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (NC1) | [Com scan output map] (OSA)
NC2 | Com scan output 2 value | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (NC2) | [Com scan output map] (OSA)
NC3 | Com scan output 3 value | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (NC3) | [Com scan output map] (OSA)
NC4 | Com scan output 4 value | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (NC4) | [Com scan output map] (OSA)
NC5 | Com scan output 5 value | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (NC5) | [Com scan output map] (OSA)
NC6 | Com scan output 6 value | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (NC6) | [Com scan output map] (OSA)
NC7 | Com scan output 7 value | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (NC7) | [Com scan output map] (OSA)
NC8 | Com scan output 8 value | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (NC8) | [Com scan output map] (OSA)
NM1 | Com scan input 1 value | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (NM1) | [Com. scanner input map] (ISA)
NM2 | Com scan input 2 value | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (NM2) | [Com. scanner input map] (ISA)
NM3 | Com scan input 3 value | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (NM3) | [Com. scanner input map] (ISA)
NM4 | Com scan input 4 value | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (NM4) | [Com. scanner input map] (ISA)
NM5 | Com scan input 5 value | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (NM5) | [Com. scanner input map] (ISA)
NM6 | Com scan input 6 value | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (NM6) | [Com. scanner input map] (ISA)
NM7 | Com scan input 7 value | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (NM7) | [Com. scanner input map] (ISA)
NM8 | Com scan input 8 value | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (NM8) | [Com. scanner input map] (ISA)
SMAL | Velocity min amount | 16#21A1 = 8609 | 16#2038/A | 16#8C/01/0A = 140/01/10 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
SMIL | Velocity max amount | 16#219F = 8607 | 16#2038/8 | 16#8C/01/08 = 140/01/08 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
SPAL | Acceleration delta speed | 16#21A3 = 8611 | 16#2038/C | 16#8C/01/0C = 140/01/12 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 1 rpm ... 65535 rpm
SPAT | Acceleration delta time | 16#21A5 = 8613 | 16#2038/E | 16#8C/01/0E = 140/01/14 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s
SPDL | Deceleration delta speed | 16#21A6 = 8614 | 16#2038/F | 16#8C/01/0F = 140/01/15 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 1 rpm ... 65535 rpm
SPFN | Setpoint factor numerator | 16#21C2 = 8642 | 16#2038/2B | 16#8C/01/2B = 140/01/43 |  | CiA 402 settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 65535
SPFD | Setpoint factor denominator | 16#21C3 = 8643 | 16#2038/2C | 16#8C/01/2C = 140/01/44 |  | CiA 402 settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 65535
DOTD | Type of switchOn Disable Stop | 16#21CC = 8652 | 16#2038/35 | 16#8C/01/35 = 140/01/53 | DOTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [SwitchOnDisable Stp] (DOTD) | [Stop configuration] (STT)
QSTD | Quick stop option code | 16#21CB = 8651 | 16#2038/34 | 16#8C/01/34 = 140/01/52 | QSTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Fast stop then stay in quick stop state] FST6
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 |  | Configuration management | R/WS | WORD (BitString16) | - | BIT1
CHA1 | Parameter set sel 1 | 16#3266 = 12902 | 16#2063/3 | 16#A1/01/67 = 161/01/103 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Parameter sets] (CHA1) | [Parameters switching] (MLP)
CHA2 | Parameter set sel 2 | 16#3267 = 12903 | 16#2063/4 | 16#A1/01/68 = 161/01/104 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Parameter sets] (CHA2) | [Parameters switching] (MLP)
CFPS | Used parameter set | 16#3264 = 12900 | 16#2063/1 | 16#A1/01/65 = 161/01/101 | CFPS | Parameter set switching | R | WORD (Enumeration) | - |  |  | [Used param. set] (CFPS) | [MONITORING] (MON)
VAL | Load parameter set command | 16#3265 = 12901 | 16#2063/2 | 16#A1/01/66 = 161/01/102 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 1
AD01 | Parameter set address 1 | 16#326F = 12911 | 16#2063/C | 16#A1/01/70 = 161/01/112 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD02 | Parameter set address 2 | 16#3270 = 12912 | 16#2063/D | 16#A1/01/71 = 161/01/113 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD03 | Parameter set address 3 | 16#3271 = 12913 | 16#2063/E | 16#A1/01/72 = 161/01/114 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD04 | Parameter set address 4 | 16#3272 = 12914 | 16#2063/F | 16#A1/01/73 = 161/01/115 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD05 | Parameter set address 5 | 16#3273 = 12915 | 16#2063/10 | 16#A1/01/74 = 161/01/116 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD06 | Parameter set address 6 | 16#3274 = 12916 | 16#2063/11 | 16#A1/01/75 = 161/01/117 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD07 | Parameter set address 7 | 16#3275 = 12917 | 16#2063/12 | 16#A1/01/76 = 161/01/118 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD08 | Parameter set address 8 | 16#3276 = 12918 | 16#2063/13 | 16#A1/01/77 = 161/01/119 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD09 | Parameter set address 9 | 16#3277 = 12919 | 16#2063/14 | 16#A1/01/78 = 161/01/120 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD10 | Parameter set address 10 | 16#3278 = 12920 | 16#2063/15 | 16#A1/01/79 = 161/01/121 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD11 | Parameter set address 11 | 16#3279 = 12921 | 16#2063/16 | 16#A1/01/7A = 161/01/122 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD12 | Parameter set address 12 | 16#327A = 12922 | 16#2063/17 | 16#A1/01/7B = 161/01/123 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD13 | Parameter set address 13 | 16#327B = 12923 | 16#2063/18 | 16#A1/01/7C = 161/01/124 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD14 | Parameter set address 14 | 16#327C = 12924 | 16#2063/19 | 16#A1/01/7D = 161/01/125 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD15 | Parameter set address 15 | 16#327D = 12925 | 16#2063/1A | 16#A1/01/7E = 161/01/126 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
S101 | Parameter set 1 value 1 | 16#3283 = 12931 | 16#2063/20 | 16#A1/01/84 = 161/01/132 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 1] (S101) | [Set 1] (PS1)
S102 | Parameter set 1 value 2 | 16#3284 = 12932 | 16#2063/21 | 16#A1/01/85 = 161/01/133 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 2] (S102) | [Set 1] (PS1)
S103 | Parameter set 1 value 3 | 16#3285 = 12933 | 16#2063/22 | 16#A1/01/86 = 161/01/134 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 3] (S103) | [Set 1] (PS1)
S104 | Parameter set 1 value 4 | 16#3286 = 12934 | 16#2063/23 | 16#A1/01/87 = 161/01/135 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 4] (S104) | [Set 1] (PS1)
S105 | Parameter set 1 value 5 | 16#3287 = 12935 | 16#2063/24 | 16#A1/01/88 = 161/01/136 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 5] (S105) | [Set 1] (PS1)
S106 | Parameter set 1 value 6 | 16#3288 = 12936 | 16#2063/25 | 16#A1/01/89 = 161/01/137 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 6] (S106) | [Set 1] (PS1)
S107 | Parameter set 1 value 7 | 16#3289 = 12937 | 16#2063/26 | 16#A1/01/8A = 161/01/138 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 7] (S107) | [Set 1] (PS1)
S108 | Parameter set 1 value 8 | 16#328A = 12938 | 16#2063/27 | 16#A1/01/8B = 161/01/139 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 8] (S108) | [Set 1] (PS1)
S109 | Parameter set 1 value 9 | 16#328B = 12939 | 16#2063/28 | 16#A1/01/8C = 161/01/140 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 9] (S109) | [Set 1] (PS1)
S110 | Parameter set 1 value 10 | 16#328C = 12940 | 16#2063/29 | 16#A1/01/8D = 161/01/141 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 10] (S110) | [Set 1] (PS1)
S111 | Parameter set 1 value 11 | 16#328D = 12941 | 16#2063/2A | 16#A1/01/8E = 161/01/142 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 11] (S111) | [Set 1] (PS1)
S112 | Parameter set 1 value 12 | 16#328E = 12942 | 16#2063/2B | 16#A1/01/8F = 161/01/143 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 12] (S112) | [Set 1] (PS1)
S113 | Parameter set 1 value 13 | 16#328F = 12943 | 16#2063/2C | 16#A1/01/90 = 161/01/144 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 13] (S113) | [Set 1] (PS1)
S114 | Parameter set 1 value 14 | 16#3290 = 12944 | 16#2063/2D | 16#A1/01/91 = 161/01/145 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 14] (S114) | [Set 1] (PS1)
S115 | Parameter set 1 value 15 | 16#3291 = 12945 | 16#2063/2E | 16#A1/01/92 = 161/01/146 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 15] (S115) | [Set 1] (PS1)
S201 | Parameter set 2 value 1 | 16#3297 = 12951 | 16#2063/34 | 16#A1/01/98 = 161/01/152 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 1] (S201) | [Set 2] (PS2)
S202 | Parameter set 2 value 2 | 16#3298 = 12952 | 16#2063/35 | 16#A1/01/99 = 161/01/153 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 2] (S202) | [Set 2] (PS2)
S203 | Parameter set 2 value 3 | 16#3299 = 12953 | 16#2063/36 | 16#A1/01/9A = 161/01/154 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 3] (S203) | [Set 2] (PS2)
S204 | Parameter set 2 value 4 | 16#329A = 12954 | 16#2063/37 | 16#A1/01/9B = 161/01/155 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 4] (S204) | [Set 2] (PS2)
S205 | Parameter set 2 value 5 | 16#329B = 12955 | 16#2063/38 | 16#A1/01/9C = 161/01/156 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 5] (S205) | [Set 2] (PS2)
S206 | Parameter set 2 value 6 | 16#329C = 12956 | 16#2063/39 | 16#A1/01/9D = 161/01/157 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 6] (S206) | [Set 2] (PS2)
S207 | Parameter set 2 value 7 | 16#329D = 12957 | 16#2063/3A | 16#A1/01/9E = 161/01/158 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 7] (S207) | [Set 2] (PS2)
S208 | Parameter set 2 value 8 | 16#329E = 12958 | 16#2063/3B | 16#A1/01/9F = 161/01/159 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 8] (S208) | [Set 2] (PS2)
S209 | Parameter set 2 value 9 | 16#329F = 12959 | 16#2063/3C | 16#A1/01/A0 = 161/01/160 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 9] (S209) | [Set 2] (PS2)
S210 | Parameter set 2 value 10 | 16#32A0 = 12960 | 16#2063/3D | 16#A1/01/A1 = 161/01/161 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 10] (S210) | [Set 2] (PS2)
S211 | Parameter set 2 value 11 | 16#32A1 = 12961 | 16#2063/3E | 16#A1/01/A2 = 161/01/162 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 11] (S211) | [Set 2] (PS2)
S212 | Parameter set 2 value 12 | 16#32A2 = 12962 | 16#2063/3F | 16#A1/01/A3 = 161/01/163 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 12] (S212) | [Set 2] (PS2)
S213 | Parameter set 2 value 13 | 16#32A3 = 12963 | 16#2063/40 | 16#A1/01/A4 = 161/01/164 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 13] (S213) | [Set 2] (PS2)
S214 | Parameter set 2 value 14 | 16#32A4 = 12964 | 16#2063/41 | 16#A1/01/A5 = 161/01/165 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 14] (S214) | [Set 2] (PS2)
S215 | Parameter set 2 value 15 | 16#32A5 = 12965 | 16#2063/42 | 16#A1/01/A6 = 161/01/166 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 15] (S215) | [Set 2] (PS2)
S301 | Parameter set 3 value 1 | 16#32AB = 12971 | 16#2063/48 | 16#A1/01/AC = 161/01/172 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 1] (S301) | [Set 3] (PS3)
S302 | Parameter set 3 value 2 | 16#32AC = 12972 | 16#2063/49 | 16#A1/01/AD = 161/01/173 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 2] (S302) | [Set 3] (PS3)
S303 | Parameter set 3 value 3 | 16#32AD = 12973 | 16#2063/4A | 16#A1/01/AE = 161/01/174 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 3] (S303) | [Set 3] (PS3)
S304 | Parameter set 3 value 4 | 16#32AE = 12974 | 16#2063/4B | 16#A1/01/AF = 161/01/175 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 4] (S304) | [Set 3] (PS3)
S305 | Parameter set 3 value 5 | 16#32AF = 12975 | 16#2063/4C | 16#A1/01/B0 = 161/01/176 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 5] (S305) | [Set 3] (PS3)
S306 | Parameter set 3 value 6 | 16#32B0 = 12976 | 16#2063/4D | 16#A1/01/B1 = 161/01/177 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 6] (S306) | [Set 3] (PS3)
S307 | Parameter set 3 value 7 | 16#32B1 = 12977 | 16#2063/4E | 16#A1/01/B2 = 161/01/178 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 7] (S307) | [Set 3] (PS3)
S308 | Parameter set 3 value 8 | 16#32B2 = 12978 | 16#2063/4F | 16#A1/01/B3 = 161/01/179 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 8] (S308) | [Set 3] (PS3)
S309 | Parameter set 3 value 9 | 16#32B3 = 12979 | 16#2063/50 | 16#A1/01/B4 = 161/01/180 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 9] (S309) | [Set 3] (PS3)
S310 | Parameter set 3 value 10 | 16#32B4 = 12980 | 16#2063/51 | 16#A1/01/B5 = 161/01/181 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 10] (S310) | [Set 3] (PS3)
S311 | Parameter set 3 value 11 | 16#32B5 = 12981 | 16#2063/52 | 16#A1/01/B6 = 161/01/182 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 11] (S311) | [Set 3] (PS3)
S312 | Parameter set 3 value 12 | 16#32B6 = 12982 | 16#2063/53 | 16#A1/01/B7 = 161/01/183 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 12] (S312) | [Set 3] (PS3)
S313 | Parameter set 3 value 13 | 16#32B7 = 12983 | 16#2063/54 | 16#A1/01/B8 = 161/01/184 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 13] (S313) | [Set 3] (PS3)
S314 | Parameter set 3 value 14 | 16#32B8 = 12984 | 16#2063/55 | 16#A1/01/B9 = 161/01/185 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 14] (S314) | [Set 3] (PS3)
S315 | Parameter set 3 value 15 | 16#32B9 = 12985 | 16#2063/56 | 16#A1/01/BA = 161/01/186 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 15] (S315) | [Set 3] (PS3)
LSP | Low speed | 16#0C21 = 3105 | 16#2001/6 | 16#70/01/6A = 112/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Low Speed] (LSP) | [Simply start] (SIM) [Settings] (SET)
HSP | High speed | 16#0C20 = 3104 | 16#2001/5 | 16#70/01/69 = 112/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High Speed] (HSP) | [Simply start] (SIM) [Settings] (SET) [High Speed Switching] (CHS)
HSP2 | High speed 2 | 16#3B06 = 15110 | 16#2079/B | 16#AC/01/6F = 172/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 2] (HSP2) | [Settings] (SET) [High Speed Switching] (CHS)
HSP3 | High speed 3 | 16#3B07 = 15111 | 16#2079/C | 16#AC/01/70 = 172/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 3] (HSP3) | [Settings] (SET) [High Speed Switching] (CHS)
HSP4 | High speed 4 | 16#3B08 = 15112 | 16#2079/D | 16#AC/01/71 = 172/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 4] (HSP4) | [Settings] (SET) [High Speed Switching] (CHS)
SH2 | 2 high speed assign. | 16#3AFD = 15101 | 16#2079/2 | 16#AC/01/66 = 172/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 High speed] (SH2) | [High Speed Switching] (CHS)
SH4 | 4 high speed assign. | 16#3AFE = 15102 | 16#2079/3 | 16#AC/01/67 = 172/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [4 High speed] (SH4) | [High Speed Switching] (CHS)
ITH | Motor Thermal current | 16#2596 = 9622 | 16#2042/17 | 16#91/01/17 = 145/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Motor Th Current] (ITH) | [Simply start] (SIM) [Settings] (SET)
SPGU | Inertia factor | 16#259D = 9629 | 16#2042/1E | 16#91/01/1E = 145/01/30 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Inertia Factor] (SPGU) | [Settings] (SET) [Motor control] (DRC)
SPG | Speed proportional gain | 16#238F = 9103 | 16#203D/4 | 16#8E/01/68 = 142/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Speed prop. gain] (SPG) | [Settings] (SET) [Motor control] (DRC)
SIT | Speed time integral | 16#2390 = 9104 | 16#203D/5 | 16#8E/01/69 = 142/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 63 ms | 1 ms ... 65535 ms | [Speed time integral] (SIT) | [Settings] (SET) [Motor control] (DRC)
SFC | K speed loop filter | 16#2391 = 9105 | 16#203D/6 | 16#8E/01/6A = 142/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 65 | 0 ... 100 | [K speed loop filter] (SFC) | [Settings] (SET) [Motor control] (DRC)
FFH | Filter time of the estimated speed | 16#239B = 9115 | 16#203D/10 | 16#8E/01/74 = 142/01/116 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 6.4 ms | 0.0 ms ... 100.0 ms | [Spd est. filter time] (FFH) | [Motor control] (DRC)
CRTF | Filter time of the current | 16#239C = 9116 | 16#203D/11 | 16#8E/01/75 = 142/01/117 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 3.2 ms | 0.0 ms ... 100.0 ms | [Current Filter Time] (CRTF) | [Motor control] (DRC)
CTD | High current threshold | 16#2AF9 = 11001 | 16#2050/2 | 16#98/01/02 = 152/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [High Current Thd] (CTD) | [Settings] (SET) [Warning setting] (ALS)
TTH | High torque threshold | 16#2B08 = 11016 | 16#2050/11 | 16#98/01/11 = 152/01/17 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | -300 % ... 300 % | [High torque thd.] (TTH) | [Settings] (SET) [Warning setting] (ALS)
TTL | Low torque threshold | 16#2B07 = 11015 | 16#2050/10 | 16#98/01/10 = 152/01/16 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 50 % | -300 % ... 300 % | [Low torque thd.] (TTL) | [Settings] (SET) [Warning setting] (ALS)
FQL | Pulse warning threshold | 16#3911 = 14609 | 16#2074/A | 16#AA/01/0A = 170/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 20000 Hz | [Pulse warning thd.] (FQL) | [Settings] (SET) [Warning setting] (ALS)
FTD | Motor frequency threshold | 16#2AFB = 11003 | 16#2050/4 | 16#98/01/04 = 152/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Motor Freq Thd] (FTD) | [Settings] (SET) [Warning setting] (ALS)
F2D | Frequency threshold 2 | 16#2AFC = 11004 | 16#2050/5 | 16#98/01/05 = 152/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Freq. threshold 2] (F2D) | [Settings] (SET) [Warning setting] (ALS)
JF2 | Skip frequency 2 | 16#2C26 = 11302 | 16#2053/3 | 16#99/01/67 = 153/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency 2] (JF2) | [Settings] (SET) [Preset speeds] (PSS)
JPF | Skip frequency | 16#2C25 = 11301 | 16#2053/2 | 16#99/01/66 = 153/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency] (JPF) | [Settings] (SET) [Preset speeds] (PSS)
JFH | Skip Freq. hysteresis | 16#2C2F = 11311 | 16#2053/C | 16#99/01/70 = 153/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.1 Hz ... 10.0 Hz | [Skip Freq.Hysteresis] (JFH) | [Settings] (SET) [Preset speeds] (PSS)
JF3 | 3rd Skip frequency | 16#2C27 = 11303 | 16#2053/4 | 16#99/01/68 = 153/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [3rd Skip Frequency] (JF3) | [Settings] (SET) [Preset speeds] (PSS)
BFR | Motor Standard | 16#0BC7 = 3015 | 16#2000/10 | 16#70/01/10 = 112/01/16 | BFR | Configuration and settings | R/WS | WORD (Enumeration) | - | [50Hz motor frequency] 50Hz |  | [Motor Standard] (BFR) | [Simply start] (SIM) [Motor control] (DRC)
NPR | Nominal motor power | 16#258D = 9613 | 16#2042/E | 16#91/01/0E = 145/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Nominal Motor Power] (NPR) | [Simply start] (SIM) [Asynchronous motor] (ASY)
COS | Motor 1 Cosinus Phi | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | Refer to programming manual | 0.50 ... 1.00 | [Motor 1 Cosinus Phi] (COS) | [Simply start] (SIM) [Asynchronous motor] (ASY)
UNS | Nominal motor voltage | 16#2581 = 9601 | 16#2042/2 | 16#91/01/02 = 145/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 690 V | [Nom Motor Voltage] (UNS) | [Simply start] (SIM) [Asynchronous motor] (ASY)
NCR | Nominal motor current | 16#2583 = 9603 | 16#2042/4 | 16#91/01/04 = 145/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Nom Motor Current] (NCR) | [Simply start] (SIM) [Asynchronous motor] (ASY)
FRS | Nominal motor frequency | 16#2582 = 9602 | 16#2042/3 | 16#91/01/03 = 145/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 800.0 Hz | [Nominal Motor Freq] (FRS) | [Simply start] (SIM) [Asynchronous motor] (ASY)
NSP | Nominal motor speed | 16#2584 = 9604 | 16#2042/5 | 16#91/01/05 = 145/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nominal Motor Speed] (NSP) | [Simply start] (SIM) [Asynchronous motor] (ASY)
TFR | Max frequency | 16#0C1F = 3103 | 16#2001/4 | 16#70/01/68 = 112/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 599.0 Hz | [Max Frequency] (TFR) | [Simply start] (SIM) [Motor control] (DRC)
TUN | Autotuning | 16#2588 = 9608 | 16#2042/9 | 16#91/01/09 = 145/01/09 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] NO |  | [Autotuning] (TUN) | [Simply start] (SIM) [Asynchronous motor] (ASY) [Synchronous motor] (SYN)
AUT | Automatic autotune | 16#258F = 9615 | 16#2042/10 | 16#91/01/10 = 145/01/16 | AUT | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Automatic autotune] (AUT) | [Asynchronous motor] (ASY) [Synchronous motor] (SYN)
TUS | Autotuning status | 16#2589 = 9609 | 16#2042/A | 16#91/01/0A = 145/01/10 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Not done] TAB |  | [Autotuning Status] (TUS) | [Simply start] (SIM) [Asynchronous motor] (ASY) [Synchronous motor] (SYN)
CTT | Motor control type | 16#2587 = 9607 | 16#2042/8 | 16#91/01/08 = 145/01/08 | CTT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Motor control type] (CTT) | [Motor control] (DRC)
U1 | Volt point 1 on 5pt V/F | 16#3073 = 12403 | 16#205E/4 | 16#9F/01/04 = 159/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U1] (U1) | [Motor control] (DRC)
F1 | Freq point 1on 5pt V/F | 16#3074 = 12404 | 16#205E/5 | 16#9F/01/05 = 159/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F1] (F1) | [Motor control] (DRC)
U2 | Volt point 2 on 5pt V/F | 16#3075 = 12405 | 16#205E/6 | 16#9F/01/06 = 159/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U2] (U2) | [Motor control] (DRC)
F2 | Freq point 2 on 5pt V/F | 16#3076 = 12406 | 16#205E/7 | 16#9F/01/07 = 159/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F2] (F2) | [Motor control] (DRC)
U3 | Volt point 3 on 5pt V/F | 16#3077 = 12407 | 16#205E/8 | 16#9F/01/08 = 159/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U3] (U3) | [Motor control] (DRC)
F3 | Freq point 3 on 5pt V/F | 16#3078 = 12408 | 16#205E/9 | 16#9F/01/09 = 159/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F3] (F3) | [Motor control] (DRC)
U4 | Volt point 4 on 5pt V/F | 16#3079 = 12409 | 16#205E/A | 16#9F/01/0A = 159/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U4] (U4) | [Motor control] (DRC)
F4 | Freq point 4 on 5pt V/F | 16#307A = 12410 | 16#205E/B | 16#9F/01/0B = 159/01/11 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F4] (F4) | [Motor control] (DRC)
U5 | Volt point 5 on 5pt V/F | 16#307B = 12411 | 16#205E/C | 16#9F/01/0C = 159/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U5] (U5) | [Motor control] (DRC)
F5 | Freq point 5 on 5pt V/F | 16#307C = 12412 | 16#205E/D | 16#9F/01/0D = 159/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F5] (F5) | [Motor control] (DRC)
NCRS | Sync motor nominal current | 16#25C6 = 9670 | 16#2042/47 | 16#91/01/47 = 145/01/71 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Sync Nominal I] (NCRS) | [Synchronous motor] (SYN)
NSPS | Nominal synchronous motor speed | 16#25C7 = 9671 | 16#2042/48 | 16#91/01/48 = 145/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nom SyncMotor Speed] (NSPS) | [Synchronous motor] (SYN)
PPNS | Pole pairs number (sync) | 16#25C8 = 9672 | 16#2042/49 | 16#91/01/49 = 145/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 50 | [Pole pairs] (PPNS) | [Synchronous motor] (SYN)
TQS | Nominal motor torque | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Nm | Refer to programming manual | 0.1 Nm ... 6553.5 Nm | [Nom Motor torque] (TQS) | [Synchronous motor] (SYN)
PHS | Sync. EMF constant | 16#25C9 = 9673 | 16#2042/4A | 16#91/01/4A = 145/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mV/rpm | 0.0 mV/rpm | 0.0 mV/rpm ... 6553.5 mV/rpm | [Syn. EMF constant] (PHS) | [Synchronous motor] (SYN)
LDS | Sync motor d inductance | 16#25CA = 9674 | 16#2042/4B | 16#91/01/4B = 145/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Autotune L d-axis] (LDS) | [Synchronous motor] (SYN)
LQS | Sync motor q inductance | 16#25CB = 9675 | 16#2042/4C | 16#91/01/4C = 145/01/76 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Autotune L q-axis] (LQS) | [Synchronous motor] (SYN)
RSAS | Calculated SyncMotor Stator R | 16#25D2 = 9682 | 16#2042/53 | 16#91/01/53 = 145/01/83 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 mOhm | 0 mOhm | 0 mOhm ... 65535 mOhm | [SyncMotor Stator R] (RSAS) | [Synchronous motor] (SYN)
UFR | IR compensation | 16#2597 = 9623 | 16#2042/18 | 16#91/01/18 = 145/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [IR compensation] (UFR) | [Settings] (SET) [Motor control] (DRC)
SLP | Slip Compensation | 16#2599 = 9625 | 16#2042/1A | 16#91/01/1A = 145/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 300 % | [Slip compensation] (SLP) | [Settings] (SET) [Motor control] (DRC)
PPN | Number of pairs of poles calculated | 16#2592 = 9618 | 16#2042/13 | 16#91/01/13 = 145/01/19 |  | Configuration and settings | R | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 100
RSA | AsyncMotor Stator resistance | 16#25AA = 9642 | 16#2042/2B | 16#91/01/2B = 145/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 mOhm | 0 mOhm | 0 mOhm ... 65535 mOhm | [AsyncMotor R Stator] (RSA) | [Asynchronous motor] (ASY)
IDA | Magnetizing current | 16#25B4 = 9652 | 16#2042/35 | 16#91/01/35 = 145/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Magnetizing Current] (IDA) | [Asynchronous motor] (ASY)
LFA | AsyncMotor Leakage inductance | 16#25BE = 9662 | 16#2042/3F | 16#91/01/3F = 145/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [AsyncMotor Lf Induct] (LFA) | [Asynchronous motor] (ASY)
TRA | Rotor time constant | 16#25C3 = 9667 | 16#2042/44 | 16#91/01/44 = 145/01/68 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 65535 ms | [Rotor Time Const] (TRA) | [Asynchronous motor] (ASY)
FRSS | Synchronous motor nominal freq | 16#25CF = 9679 | 16#2042/50 | 16#91/01/50 = 145/01/80 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 800.0 Hz | [Sync Nominal Freq] (FRSS) | [Synchronous motor] (SYN)
SFR | Switching frequency | 16#0C1E = 3102 | 16#2001/3 | 16#70/01/67 = 112/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 kHz | 4.0 kHz | 2.0 kHz ... 16.0 kHz | [Switching frequency] (SFR) | [Settings] (SET) [Motor control] (DRC)
CLI | Current limitation | 16#23F1 = 9201 | 16#203E/2 | 16#8F/01/02 = 143/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Current Limitation] (CLI) | [Settings] (SET) [Motor control] (DRC) [2nd current limit.] (CLI)
SFT | Switching frequency type | 16#0C1D = 3101 | 16#2001/2 | 16#70/01/66 = 112/01/102 | SFT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Switch.frequency type 1] HF1 |  | [Switch Freq Type] (SFT) | [Motor control] (DRC)
NRD | Motor Noise Reduction | 16#0C23 = 3107 | 16#2001/8 | 16#70/01/6C = 112/01/108 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Noise Reduction] (NRD) | [Motor control] (DRC)
BOA | Boost activation | 16#3656 = 13910 | 16#206D/B | 16#A6/01/6F = 166/01/111 | BOA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Dynamic] DYNA |  | [Boost activation] (BOA) | [Motor control] (DRC)
SVL | Motor surge limitation | 16#3139 = 12601 | 16#2060/2 | 16#A0/01/02 = 160/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Motor surge limit.] (SVL) | [Motor control] (DRC)
SOP | Attenuation time | 16#313A = 12602 | 16#2060/3 | 16#A0/01/03 = 160/01/03 | SOP | Configuration and settings | R/WS | WORD (Enumeration) | - | [10 µs] 10 |  | [Attenuation Time] (SOP) | [Motor control] (DRC)
VBR | Braking level | 16#3715 = 14101 | 16#206F/2 | 16#A7/01/66 = 167/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 V | Refer to programming manual | 335 V ... 995 V | [Braking level] (VBR) | [Motor control] (DRC) [DC bus] (DCC)
LBA | Load sharing | 16#37DD = 14301 | 16#2071/2 | 16#A8/01/66 = 168/01/102 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Load sharing] (LBA) | [Motor control] (DRC)
LBC | Load correction | 16#37DE = 14302 | 16#2071/3 | 16#A8/01/67 = 168/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Load correction] (LBC) | [Settings] (SET) [Motor control] (DRC)
LBC1 | Correction min speed | 16#37DF = 14303 | 16#2071/4 | 16#A8/01/68 = 168/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 598.9 Hz | [Correction min spd] (LBC1) | [Motor control] (DRC)
LBC2 | Correction max speed | 16#37E0 = 14304 | 16#2071/5 | 16#A8/01/69 = 168/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.1 Hz | 0.1 Hz ... 599.0 Hz | [Correction max spd] (LBC2) | [Motor control] (DRC)
LBC3 | Torque offset | 16#37E1 = 14305 | 16#2071/6 | 16#A8/01/6A = 168/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Torque offset] (LBC3) | [Motor control] (DRC)
LBF | Sharing filter | 16#37E2 = 14306 | 16#2071/7 | 16#A8/01/6B = 168/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 100 ms | 0 ms ... 20000 ms | [Sharing filter] (LBF) | [Motor control] (DRC)
FFM | Fan mode | 16#0C3A = 3130 | 16#2001/1F | 16#70/01/83 = 112/01/131 | FFM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Fan mode] (FFM) | [Settings] (SET)
TCC | 2/3-wire control | 16#2B5D = 11101 | 16#2051/2 | 16#98/01/66 = 152/01/102 | TCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [2-wire control] 2C |  | [2/3-Wire Control] (TCC) | [Simply start] (SIM) [Inputs / Outputs] (I_O)
TCT | Type of 2-wire control | 16#2B5E = 11102 | 16#2051/3 | 16#98/01/67 = 152/01/103 | TCT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2-wire type] (TCT) | [Inputs / Outputs] (I_O)
RRS | Reverse assignment | 16#2B61 = 11105 | 16#2051/6 | 16#98/01/6A = 152/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Reverse Assign] (RRS) | [Inputs / Outputs] (I_O)
BSP | Reference frequency template selection | 16#0C22 = 3106 | 16#2001/7 | 16#70/01/6B = 112/01/107 | BSP | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard ref template] BSD |  | [Ref Freq template] (BSP) | [Inputs / Outputs] (I_O)
AI1T | Configuration of AI1 | 16#1132 = 4402 | 16#200E/3 | 16#77/01/03 = 119/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI1 Type] (AI1T) | [AI1 configuration] (AI1)
UIL1 | AI1 voltage scaling parameter of 0% | 16#113C = 4412 | 16#200E/D | 16#77/01/0D = 119/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI1 Min. Value] (UIL1) | [AI1] (AI1C) [AI1 configuration] (AI1)
UIH1 | AI1 voltage scaling parameter of 100% | 16#1146 = 4422 | 16#200E/17 | 16#77/01/17 = 119/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI1 Max Value] (UIH1) | [AI1] (AI1C) [AI1 configuration] (AI1)
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [AI1] (AI1C) [AI1 configuration] (AI1)
AI1E | AI1 intermediate point X | 16#116E = 4462 | 16#200E/3F | 16#77/01/3F = 119/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 X Interm. Point] (AI1E) | [AI1 configuration] (AI1)
AI1S | AI1 intermediate point Y | 16#1178 = 4472 | 16#200E/49 | 16#77/01/49 = 119/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point Y] (AI1S) | [AI1 configuration] (AI1)
AI2T | Configuration of AI2 | 16#1133 = 4403 | 16#200E/4 | 16#77/01/04 = 119/01/04 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [AI2 Type] (AI2T) | [AI2 configuration] (AI2)
UIL2 | AI2 voltage scaling parameter of 0% | 16#113D = 4413 | 16#200E/E | 16#77/01/0E = 119/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI2 Min. Value] (UIL2) | [AI2] (AI2C) [AI2 configuration] (AI2)
UIH2 | AI2 voltage scaling parameter of 100% | 16#1147 = 4423 | 16#200E/18 | 16#77/01/18 = 119/01/24 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI2 Max value] (UIH2) | [AI2] (AI2C) [AI2 configuration] (AI2)
AI2F | AI2 filter | 16#1165 = 4453 | 16#200E/36 | 16#77/01/36 = 119/01/54 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI2 filter] (AI2F) | [AI2] (AI2C) [AI2 configuration] (AI2)
AI2E | AI2 intermediate point X | 16#116F = 4463 | 16#200E/40 | 16#77/01/40 = 119/01/64 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 X Interm. Point] (AI2E) | [AI2 configuration] (AI2)
AI2S | AI2 intermediate point Y | 16#1179 = 4473 | 16#200E/4A | 16#77/01/4A = 119/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point Y] (AI2S) | [AI2 configuration] (AI2)
AI3T | Configuration of AI3 | 16#1134 = 4404 | 16#200E/5 | 16#77/01/05 = 119/01/05 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AI3 Type] (AI3T) | [AI3 configuration] (AI3)
CRL3 | AI3 current scaling parameter of 0% | 16#1152 = 4434 | 16#200E/23 | 16#77/01/23 = 119/01/35 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI3 Min. Value] (CRL3) | [AI3] (AI3C) [AI3 configuration] (AI3)
CRH3 | AI3 current scaling parameter of 100% | 16#115C = 4444 | 16#200E/2D | 16#77/01/2D = 119/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI3 Max Value] (CRH3) | [AI3] (AI3C) [AI3 configuration] (AI3)
AI3F | AI3 filter | 16#1166 = 4454 | 16#200E/37 | 16#77/01/37 = 119/01/55 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI3 filter] (AI3F) | [AI3] (AI3C) [AI3 configuration] (AI3)
AI3E | AI3 intermediate point X | 16#1170 = 4464 | 16#200E/41 | 16#77/01/41 = 119/01/65 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 X Interm. point] (AI3E) | [AI3 configuration] (AI3)
AI3S | AI3 intermediate point Y | 16#117A = 4474 | 16#200E/4B | 16#77/01/4B = 119/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Y Interm. point] (AI3S) | [AI3 configuration] (AI3)
AO1 | AQ1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [AQ1 assignment] (AO1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1T | AQ1 Type | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [AQ1 Type] (AO1T) | [AQ1 configuration] (AO1)
AOF1 | Enable AQ1 fallback | 16#10C5 = 4293 | 16#200C/5E | 16#76/01/5E = 118/01/94 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable AQ1 fallback] (AOF1) | [AQ1 configuration] (AO1)
AOL1 | AQ1 min output value | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ1 min output] (AOL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AOH1 | AQ1 max output value | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ1 max output] (AOH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
UOL1 | AQ1 minimum output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ1 min Output] (UOL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
UOH1 | AQ1 maximum output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ1 max Output] (UOH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
ASL1 | Scaling AQ1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 Min] (ASL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
ASH1 | Scaling AQ1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 Max] (ASH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1F | AQ1 filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ1 Filter] (AO1F) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
FR1 | Configuration reference frequency 1 | 16#20DD = 8413 | 16#2036/E | 16#8B/01/0E = 139/01/14 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 1 Config] (FR1) | [Command] (CTL)
RIN | Reverse direction disable | 16#0C24 = 3108 | 16#2001/9 | 16#70/01/6D = 112/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Reverse Disable] (RIN) | [Command] (CTL)
PST | Stop key enable | 16#FA02 = 64002 |  |  | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Stop Key Enable] (PST) | [Command] (CTL)
CHCF | Channel mode config. | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Profile] (CHCF) | [Command] (CTL)
CCS | Command switching | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Command Switching] (CCS) | [Command] (CTL)
CD1 | Command channel 1 assign | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminal block] TER |  | [Cmd channel 1] (CD1) | [Command] (CTL)
CD2 | Command channel 2 assign | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus communication] MDB |  | [Cmd channel 2] (CD2) | [Command] (CTL)
RFC | Freq switching assignment | 16#20DB = 8411 | 16#2036/C | 16#8B/01/0C = 139/01/12 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Freq Switch Assign] (RFC) | [Command] (CTL)
FR2 | Configuration reference frequency 2 | 16#20DE = 8414 | 16#2036/F | 16#8B/01/0F = 139/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 2 Config] (FR2) | [Command] (CTL)
COP | Copy Ch.1-Ch.2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No copy] NO |  | [Copy Ch1-Ch2] (COP) | [Command] (CTL)
FN1 | F1 key assignment | 16#34BD = 13501 | 16#2069/2 | 16#A4/01/66 = 164/01/102 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F1 key assignment] (FN1) | [Command] (CTL)
FN2 | F2 key assignment | 16#34BE = 13502 | 16#2069/3 | 16#A4/01/67 = 164/01/103 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F2 key assignment] (FN2) | [Command] (CTL)
FN3 | F3 key assignment | 16#34BF = 13503 | 16#2069/4 | 16#A4/01/68 = 164/01/104 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F3 key assignment] (FN3) | [Command] (CTL)
FN4 | F4 key assignment | 16#34C0 = 13504 | 16#2069/5 | 16#A4/01/69 = 164/01/105 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F4 key assignment] (FN4) | [Command] (CTL)
BMP | HMI local/remote command | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop on switching] STOP |  | [HMI L/R cmd] (BMP) | [Command] (CTL)
RCB | Select switching (1 to 1B) | 16#20DC = 8412 | 16#2036/D | 16#8B/01/0D = 139/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Reference frequency channel 1] FR1 |  | [Ref 1B switching] (RCB) | [Ref Freq switch] (REF)
FR1B | Configuration ref. 1B | 16#20DF = 8415 | 16#2036/10 | 16#8B/01/10 = 139/01/16 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref.1B channel] (FR1B) | [Ref Freq switch] (REF)
SA2 | Summing input 2 | 16#2E19 = 11801 | 16#2058/2 | 16#9C/01/02 = 156/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Summing Input 2] (SA2) | [Ref. operations] (OAI)
SA3 | Summing input 3 | 16#2E1A = 11802 | 16#2058/3 | 16#9C/01/03 = 156/01/03 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Summing Input 3] (SA3) | [Ref. operations] (OAI)
DA2 | Subtract reference frequency 2 | 16#2E23 = 11811 | 16#2058/C | 16#9C/01/0C = 156/01/12 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 2] (DA2) | [Ref. operations] (OAI)
DA3 | Subtract reference frequency 3 | 16#2E24 = 11812 | 16#2058/D | 16#9C/01/0D = 156/01/13 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 3] (DA3) | [Ref. operations] (OAI)
MA2 | Reference frequency 2 multiply | 16#2E2D = 11821 | 16#2058/16 | 16#9C/01/16 = 156/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 2 Multiply] (MA2) | [Ref. operations] (OAI)
MA3 | Reference frequency 3 multiply | 16#2E2E = 11822 | 16#2058/17 | 16#9C/01/17 = 156/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 3 Multiply] (MA3) | [Ref. operations] (OAI)
RPT | Type of ramp | 16#232C = 9004 | 16#203C/5 | 16#8E/01/05 = 142/01/05 | RPT | Configuration and settings | R/W | WORD (Enumeration) | - | [Linear ramp] LIN |  | [Ramp Type] (RPT) | [Ramp switching] (RPT)
INR | Ramp increment | 16#233C = 9020 | 16#203C/15 | 16#8E/01/15 = 142/01/21 | INR | Configuration and settings | R/W | WORD (Enumeration) | - | [Tenths of seconds] 01 |  | [Ramp increment] (INR) | [Settings] (SET) [Ramp switching] (RPT)
ACC | Acceleration ramp time | 16#2329 = 9001 | 16#203C/2 | 16#8E/01/02 = 142/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 9999 | [Acceleration] (ACC) | [Simply start] (SIM) [Settings] (SET) [Ramp switching] (RPT)
DEC | Deceleration ramp time | 16#232A = 9002 | 16#203C/3 | 16#8E/01/03 = 142/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 9999 | [Deceleration] (DEC) | [Simply start] (SIM) [Settings] (SET) [Ramp switching] (RPT) [Time delay control] (TDC)
TA1 | Start ACC ramp rounding | 16#232D = 9005 | 16#203C/6 | 16#8E/01/06 = 142/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Acc round] (TA1) | [Settings] (SET) [Ramp switching] (RPT)
TA2 | End ACC ramp rounding | 16#232E = 9006 | 16#203C/7 | 16#8E/01/07 = 142/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Acc round] (TA2) | [Settings] (SET) [Ramp switching] (RPT)
TA3 | Start DEC ramp rounding | 16#232F = 9007 | 16#203C/8 | 16#8E/01/08 = 142/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Dec round] (TA3) | [Settings] (SET) [Ramp switching] (RPT)
TA4 | End DEC ramp rounding | 16#2330 = 9008 | 16#203C/9 | 16#8E/01/09 = 142/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Dec round] (TA4) | [Settings] (SET) [Ramp switching] (RPT)
FRT | Ramp 2 frequency threshold | 16#2333 = 9011 | 16#203C/C | 16#8E/01/0C = 142/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Ramp 2 Thd] (FRT) | [Ramp switching] (RPT)
RPS | Ramp switching assignment | 16#2332 = 9010 | 16#203C/B | 16#8E/01/0B = 142/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ramp Switch Assign] (RPS) | [Ramp switching] (RPT)
AC2 | Acceleration 2 ramp time | 16#2334 = 9012 | 16#203C/D | 16#8E/01/0D = 142/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Acceleration 2] (AC2) | [Settings] (SET) [Ramp switching] (RPT) [+/- speed around ref] (SRE) [PID controller] (PID)
DE2 | Deceleration 2 | 16#2335 = 9013 | 16#203C/E | 16#8E/01/0E = 142/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Deceleration 2] (DE2) | [Settings] (SET) [Ramp switching] (RPT) [+/- speed around ref] (SRE)
BRA | Decel ramp adaptation | 16#232B = 9003 | 16#203C/4 | 16#8E/01/04 = 142/01/04 | BRA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Dec.Ramp Adapt] (BRA) | [Ramp switching] (RPT)
STT | Type of stop | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [On ramp] RMP |  | [Type of stop] (STT) | [Stop configuration] (STT)
FFT | Freewheel stop threshold | 16#2BD4 = 11220 | 16#2052/15 | 16#99/01/15 = 153/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.2 Hz ... 599.0 Hz | [Freewheel stop Thd] (FFT) | [Settings] (SET) [Stop configuration] (STT)
NST | Freewheel stop | 16#2BC2 = 11202 | 16#2052/3 | 16#99/01/03 = 153/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Freewheel Stop] (NST) | [Stop configuration] (STT)
FST | Fast stop assignment | 16#2BC4 = 11204 | 16#2052/5 | 16#99/01/05 = 153/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fast Stop Assign] (FST) | [Stop configuration] (STT)
DCF | Fast Stop ramp Divider | 16#2BDE = 11230 | 16#2052/1F | 16#99/01/1F = 153/01/31 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 4 | 0 ... 10 | [Ramp Divider] (DCF) | [Settings] (SET) [Stop configuration] (STT) [Ramp divider] (FST)
DCI | DC injection assignment | 16#2BC3 = 11203 | 16#2052/4 | 16#99/01/04 = 153/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DC Injection Assign] (DCI) | [Stop configuration] (STT)
IDC | DC injection level 1 | 16#2BCA = 11210 | 16#2052/B | 16#99/01/0B = 153/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [DC Inj Level 1] (IDC) | [Settings] (SET) [Stop configuration] (STT) [DC injection] (DCI)
TDI | DC injection time 1 | 16#2BCD = 11213 | 16#2052/E | 16#99/01/0E = 153/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 1] (TDI) | [Settings] (SET) [Stop configuration] (STT) [DC injection] (DCI)
IDC2 | DC injection level 2 | 16#2BCC = 11212 | 16#2052/D | 16#99/01/0D = 153/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [DC Inj Level 2] (IDC2) | [Settings] (SET) [Stop configuration] (STT) [DC injection] (DCI)
TDC | DC injection time 2 | 16#2BCB = 11211 | 16#2052/C | 16#99/01/0C = 153/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 2] (TDC) | [Settings] (SET) [Stop configuration] (STT) [DC injection] (DCI)
ADC | Automatic DC injection | 16#28A1 = 10401 | 16#204A/2 | 16#95/01/02 = 149/01/02 | ADC | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Auto DC Injection] (ADC) | [Auto DC injection] (ADC)
SDC1 | Auto DC injection level 1 | 16#28A3 = 10403 | 16#204A/4 | 16#95/01/04 = 149/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Auto DC inj Level 1] (SDC1) | [Settings] (SET) [Auto DC injection] (ADC) [Brake logic control] (BLC)
TDC1 | Auto DC injection time 1 | 16#28A2 = 10402 | 16#204A/3 | 16#95/01/03 = 149/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [Auto DC Inj Time 1] (TDC1) | [Settings] (SET) [Auto DC injection] (ADC)
SDC2 | Auto DC injection level 2 | 16#28A5 = 10405 | 16#204A/6 | 16#95/01/06 = 149/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Auto DC inj Level 2] (SDC2) | [Settings] (SET) [Auto DC injection] (ADC)
TDC2 | Auto DC injection time 2 | 16#28A4 = 10404 | 16#204A/5 | 16#95/01/05 = 149/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 30.0 s | [Auto DC Inj Time 2] (TDC2) | [Settings] (SET) [Auto DC injection] (ADC)
JOG | Jog assignment | 16#2B66 = 11110 | 16#2051/B | 16#98/01/6F = 152/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Jog Assign] (JOG) | [Jog] (JOG)
JGF | Jog frequency | 16#2B67 = 11111 | 16#2051/C | 16#98/01/70 = 152/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 10.0 Hz | [Jog Frequency] (JGF) | [Settings] (SET) [Jog] (JOG)
JGT | Jog delay | 16#2B68 = 11112 | 16#2051/D | 16#98/01/71 = 152/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 2.0 s | [Jog Delay] (JGT) | [Settings] (SET) [Jog] (JOG)
PS2 | 2 Preset Freq assignment | 16#2C89 = 11401 | 16#2054/2 | 16#9A/01/02 = 154/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 Preset Freq] (PS2) | [Preset speeds] (PSS)
PS4 | 4 Preset Freq assignment | 16#2C8A = 11402 | 16#2054/3 | 16#9A/01/03 = 154/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 Preset Freq] (PS4) | [Preset speeds] (PSS)
PS8 | 8 Preset Freq assignment | 16#2C8B = 11403 | 16#2054/4 | 16#9A/01/04 = 154/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [8 Preset Freq] (PS8) | [Preset speeds] (PSS)
PS16 | 16 Preset Freq assignment | 16#2C8C = 11404 | 16#2054/5 | 16#9A/01/05 = 154/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [16 Preset Freq] (PS16) | [Preset speeds] (PSS)
SP2 | Preset speed 2 | 16#2C92 = 11410 | 16#2054/B | 16#9A/01/0B = 154/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 2] (SP2) | [Settings] (SET) [Preset speeds] (PSS)
SP3 | Preset speed 3 | 16#2C93 = 11411 | 16#2054/C | 16#9A/01/0C = 154/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 3] (SP3) | [Settings] (SET) [Preset speeds] (PSS)
SP4 | Preset speed 4 | 16#2C94 = 11412 | 16#2054/D | 16#9A/01/0D = 154/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 4] (SP4) | [Settings] (SET) [Preset speeds] (PSS)
SP5 | Preset speed 5 | 16#2C95 = 11413 | 16#2054/E | 16#9A/01/0E = 154/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 5] (SP5) | [Settings] (SET) [Preset speeds] (PSS)
SP6 | Preset speed 6 | 16#2C96 = 11414 | 16#2054/F | 16#9A/01/0F = 154/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 30.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 6] (SP6) | [Settings] (SET) [Preset speeds] (PSS)
SP7 | Preset speed 7 | 16#2C97 = 11415 | 16#2054/10 | 16#9A/01/10 = 154/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 7] (SP7) | [Settings] (SET) [Preset speeds] (PSS)
SP8 | Preset speed 8 | 16#2C98 = 11416 | 16#2054/11 | 16#9A/01/11 = 154/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 8] (SP8) | [Settings] (SET) [Preset speeds] (PSS)
SP9 | Preset speed 9 | 16#2C99 = 11417 | 16#2054/12 | 16#9A/01/12 = 154/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 45.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 9] (SP9) | [Settings] (SET) [Preset speeds] (PSS)
SP10 | Preset speed 10 | 16#2C9A = 11418 | 16#2054/13 | 16#9A/01/13 = 154/01/19 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 50.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 10] (SP10) | [Settings] (SET) [Preset speeds] (PSS)
SP11 | Preset speed 11 | 16#2C9B = 11419 | 16#2054/14 | 16#9A/01/14 = 154/01/20 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 55.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 11] (SP11) | [Settings] (SET) [Preset speeds] (PSS)
SP12 | Preset speed 12 | 16#2C9C = 11420 | 16#2054/15 | 16#9A/01/15 = 154/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 12] (SP12) | [Settings] (SET) [Preset speeds] (PSS)
SP13 | Preset speed 13 | 16#2C9D = 11421 | 16#2054/16 | 16#9A/01/16 = 154/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 70.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 13] (SP13) | [Settings] (SET) [Preset speeds] (PSS)
SP14 | Preset speed 14 | 16#2C9E = 11422 | 16#2054/17 | 16#9A/01/17 = 154/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 80.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 14] (SP14) | [Settings] (SET) [Preset speeds] (PSS)
SP15 | Preset speed 15 | 16#2C9F = 11423 | 16#2054/18 | 16#9A/01/18 = 154/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 90.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 15] (SP15) | [Settings] (SET) [Preset speeds] (PSS)
SP16 | Preset speed 16 | 16#2CA0 = 11424 | 16#2054/19 | 16#9A/01/19 = 154/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 100.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 16] (SP16) | [Settings] (SET) [Preset speeds] (PSS)
USP | + speed assignment | 16#2CED = 11501 | 16#2055/2 | 16#9A/01/66 = 154/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ Speed Assign] (USP) | [+/- speed] (UPD)
DSP | - speed assignment | 16#2CEE = 11502 | 16#2055/3 | 16#9A/01/67 = 154/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [- Speed Assign] (DSP) | [+/- speed] (UPD)
STR | Reference frequency save | 16#2CEF = 11503 | 16#2055/4 | 16#9A/01/68 = 154/01/104 | STR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No save] NO |  | [Ref Frequency Save] (STR) | [+/- speed] (UPD)
USI | + speed assignment | 16#2D00 = 11520 | 16#2055/15 | 16#9A/01/79 = 154/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ Speed Assign] (USI) | [+/- speed around ref] (SRE)
DSI | - speed assignment | 16#2D01 = 11521 | 16#2055/16 | 16#9A/01/7A = 154/01/122 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [- Speed Assign] (DSI) | [+/- speed around ref] (SRE)
SRP | +/- speed limitation | 16#2CF1 = 11505 | 16#2055/6 | 16#9A/01/6A = 154/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 50 % | [+/- Speed limitation] (SRP) | [Settings] (SET) [+/- speed around ref] (SRE)
SPM | Reference frequency memory assignment | 16#212B = 8491 | 16#2036/5C | 16#8B/01/5C = 139/01/92 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ref Freq Memo assign] (SPM) | [Memo reference frequency] (SPM)
FLU | Motor fluxing configure | 16#364E = 13902 | 16#206D/3 | 16#A6/01/67 = 166/01/103 | FLU | Configuration and settings | R/W | WORD (Enumeration) | - | [No] FNO |  | [Motor fluxing] (FLU) | [Settings] (SET) [Asynchronous motor] (ASY) [Fluxing by DI] (FLI)
FLI | Fluxing input assignment | 16#364D = 13901 | 16#206D/2 | 16#A6/01/66 = 166/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fluxing assignment] (FLI) | [Fluxing by DI] (FLI)
AST | Auto angle setting type | 16#3665 = 13925 | 16#206D/1A | 16#A6/01/7E = 166/01/126 | AST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pulse Signal injection - Optimized] PSIO |  | [Angle setting type] (AST) | [Synchronous motor] (SYN) [Fluxing by DI] (FLI)
HFI | Activation of HF injection | 16#3CF0 = 15600 | 16#207E/1 | 16#AF/01/01 = 175/01/01 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [HF inj. activation] (HFI) | [Synchronous motor] (SYN)
HIR | Current level of the HF injection signal | 16#3CF2 = 15602 | 16#207E/3 | 16#AF/01/03 = 175/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 25 % | 0 % ... 200 % | [HF current level] (HIR) | [Synchronous motor] (SYN)
SPB | Bandwidth of the HF PLL | 16#3CF3 = 15603 | 16#207E/4 | 16#AF/01/04 = 175/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 25 Hz | 0 Hz ... 100 Hz | [HF pll bandwidth] (SPB) | [Synchronous motor] (SYN)
ILR | Current level of the HF alignment | 16#3CF5 = 15605 | 16#207E/6 | 16#AF/01/06 = 175/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 200 % | [Current Level Align] (ILR) | [Synchronous motor] (SYN)
SIR | Boost level for IPMA alignment | 16#3CF6 = 15606 | 16#207E/7 | 16#AF/01/07 = 175/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [Boost level align.] (SIR) | [Synchronous motor] (SYN)
MCR | Maximum current of PSI alignment | 16#3CF7 = 15607 | 16#207E/8 | 16#AF/01/08 = 175/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [PSI Align Curr Max] (MCR) | [Synchronous motor] (SYN)
PEC | Angle position error compensation | 16#3CF8 = 15608 | 16#207E/9 | 16#AF/01/09 = 175/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 500 % | [Angle error Comp.] (PEC) | [Synchronous motor] (SYN)
BLC | Brake assignment | 16#2711 = 10001 | 16#2046/2 | 16#93/01/02 = 147/01/02 | BLC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Brake assignment] (BLC) | [Brake logic control] (BLC)
BST | Motion type selection | 16#2718 = 10008 | 16#2046/9 | 16#93/01/09 = 147/01/09 | BST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Hoisting motion] VER |  | [Movement type] (BST) | [Brake logic control] (BLC)
BCI | Brake contact input | 16#2719 = 10009 | 16#2046/A | 16#93/01/0A = 147/01/10 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Brake Contact] (BCI) | [Brake logic control] (BLC)
BIP | Brake release pulse | 16#2717 = 10007 | 16#2046/8 | 16#93/01/08 = 147/01/08 | BIP | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Brake Release Pulse] (BIP) | [Brake logic control] (BLC)
IBR | Brake Release current | 16#2716 = 10006 | 16#2046/7 | 16#93/01/07 = 147/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Brk Release Current] (IBR) | [Settings] (SET) [Brake logic control] (BLC)
IRD | Rev. brake release curr. | 16#271B = 10011 | 16#2046/C | 16#93/01/0C = 147/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Brake release I Rev] (IRD) | [Settings] (SET) [Brake logic control] (BLC)
BRT | Brake release time | 16#2714 = 10004 | 16#2046/5 | 16#93/01/05 = 147/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake Release time] (BRT) | [Settings] (SET) [Brake logic control] (BLC)
BIR | Brake release frequency | 16#271C = 10012 | 16#2046/D | 16#93/01/0D = 147/01/13 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Brake release freq] (BIR) | [Settings] (SET) [Brake logic control] (BLC)
BEN | Brake engage frequency | 16#2713 = 10003 | 16#2046/4 | 16#93/01/04 = 147/01/04 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | -0.1 Hz | -0.1 Hz ... 10.0 Hz | [Brake engage freq] (BEN) | [Settings] (SET) [Brake logic control] (BLC)
TBE | Brake engage delay | 16#271A = 10010 | 16#2046/B | 16#93/01/0B = 147/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage delay] (TBE) | [Settings] (SET) [Brake logic control] (BLC)
BET | Brake engage time | 16#2715 = 10005 | 16#2046/6 | 16#93/01/06 = 147/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage time] (BET) | [Settings] (SET) [Brake logic control] (BLC)
BED | Brake engage at reversal | 16#2724 = 10020 | 16#2046/15 | 16#93/01/15 = 147/01/21 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Engage at reversal] (BED) | [Brake logic control] (BLC)
JDC | Jump at reversal | 16#271D = 10013 | 16#2046/E | 16#93/01/0E = 147/01/14 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Jump at reversal] (JDC) | [Settings] (SET) [Brake logic control] (BLC)
TTR | Time to restart | 16#2726 = 10022 | 16#2046/17 | 16#93/01/17 = 147/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 15.00 s | [Time to restart] (TTR) | [Settings] (SET) [Brake logic control] (BLC)
BRH | Brake hidden | 16#2742 = 10050 | 16#2046/33 | 16#93/01/33 = 147/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
BRR | Current ramp time | 16#271F = 10015 | 16#2046/10 | 16#93/01/10 = 147/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Current ramp time] (BRR) | [Brake logic control] (BLC)
HSO | High speed hoisting | 16#300D = 12301 | 16#205D/2 | 16#9E/01/66 = 158/01/102 | HSO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [High speed hoisting] (HSO) | [High speed hoisting] (HSH)
COF | Motor speed coefficient | 16#300F = 12303 | 16#205D/4 | 16#9E/01/68 = 158/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 100 % | [Motor speed coeff.] (COF) | [High speed hoisting] (HSH)
COR | Generator speed coefficient | 16#3010 = 12304 | 16#205D/5 | 16#9E/01/69 = 158/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 100 % | [Gen. speed coeff] (COR) | [High speed hoisting] (HSH)
TOS | Load measuring time | 16#3013 = 12307 | 16#205D/8 | 16#9E/01/6C = 158/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.50 s | 0.10 s ... 65.00 s | [Load measuring tm.] (TOS) | [High speed hoisting] (HSH)
OSP | Measurement speed | 16#3011 = 12305 | 16#205D/6 | 16#9E/01/6A = 158/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Measurement spd] (OSP) | [High speed hoisting] (HSH)
CLO | High speed I limit | 16#300E = 12302 | 16#205D/3 | 16#9E/01/67 = 158/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [High speed I Limit] (CLO) | [High speed hoisting] (HSH)
SCL | Current limit. frequency | 16#3012 = 12306 | 16#205D/7 | 16#9E/01/6B = 158/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [I Limit. frequency] (SCL) | [High speed hoisting] (HSH)
RSTL | Rope slack torque level | 16#3022 = 12322 | 16#205D/17 | 16#9E/01/7B = 158/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Rope slack trq level] (RSTL) | [High speed hoisting] (HSH)
RSD | Rope slack configuration | 16#3021 = 12321 | 16#205D/16 | 16#9E/01/7A = 158/01/122 | RSD | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Rope slack config.] (RSD) | [High speed hoisting] (HSH)
PIF | PID controller feedback | 16#2E7D = 11901 | 16#2059/2 | 16#9C/01/66 = 156/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID feedback Assign] (PIF) | [PID controller] (PID)
PIF1 | Minimum PID feedback | 16#2E80 = 11904 | 16#2059/5 | 16#9C/01/69 = 156/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 32767 | [Min PID feedback] (PIF1) | [PID controller] (PID)
PIF2 | Maximum PID feedback | 16#2E81 = 11905 | 16#2059/6 | 16#9C/01/6A = 156/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1000 | 0 ... 32767 | [Max PID feedback] (PIF2) | [PID controller] (PID)
PIP1 | Minimum PID process | 16#2E82 = 11906 | 16#2059/7 | 16#9C/01/6B = 156/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 150 | 0 ... 32767 | [Min PID Process] (PIP1) | [PID controller] (PID)
PIP2 | Maximum PID process | 16#2E83 = 11907 | 16#2059/8 | 16#9C/01/6C = 156/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 900 | 0 ... 32767 | [Max PID Process] (PIP2) | [PID controller] (PID)
PII | Internal PID reference | 16#2E84 = 11908 | 16#2059/9 | 16#9C/01/6D = 156/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Intern PID Ref] (PII) | [PID controller] (PID)
RPI | Internal PID reference | 16#2E90 = 11920 | 16#2059/15 | 16#9C/01/79 = 156/01/121 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 150 | 0 ... 32767 | [Internal PID ref] (RPI) | [Reference speed] (rEF) [MONIT. PI] (MPI) [PID controller] (PID)
RPG | PID Proportional gain | 16#2EA5 = 11941 | 16#2059/2A | 16#9C/01/8E = 156/01/142 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Prop.Gain] (RPG) | [Settings] (SET) [PID controller] (PID)
RIG | PID controller integral gain | 16#2EA6 = 11942 | 16#2059/2B | 16#9C/01/8F = 156/01/143 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Intgl.Gain] (RIG) | [Settings] (SET) [PID controller] (PID)
RDG | PID derivative gain | 16#2EA7 = 11943 | 16#2059/2C | 16#9C/01/90 = 156/01/144 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 0.00 | 0.00 ... 100.00 | [PID derivative gain] (RDG) | [Settings] (SET) [PID controller] (PID)
PRP | PID ramp | 16#2ED0 = 11984 | 16#2059/55 | 16#9C/01/B9 = 156/01/185 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [PID ramp] (PRP) | [Settings] (SET) [PID controller] (PID)
PIC | PID inversion | 16#2EA4 = 11940 | 16#2059/29 | 16#9C/01/8D = 156/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID Inversion] (PIC) | [PID controller] (PID)
POL | PID controller min. output | 16#2EB0 = 11952 | 16#2059/35 | 16#9C/01/99 = 156/01/153 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -599.0 Hz ... 599.0 Hz | [PID Min Output] (POL) | [Settings] (SET) [PID controller] (PID)
POH | PID controller max. output | 16#2EB1 = 11953 | 16#2059/36 | 16#9C/01/9A = 156/01/154 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [PID Max Output] (POH) | [Settings] (SET) [PID controller] (PID)
PAL | Minimum feedback level warning | 16#2EB9 = 11961 | 16#2059/3E | 16#9C/01/A2 = 156/01/162 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 65535 | [Min fbk Warning] (PAL) | [Settings] (SET) [PID controller] (PID)
PAH | Maximum feedback level warning | 16#2EBA = 11962 | 16#2059/3F | 16#9C/01/A3 = 156/01/163 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1000 | 0 ... 65535 | [Max fbk Warning] (PAH) | [Settings] (SET) [PID controller] (PID)
PER | PID error warning | 16#2EBB = 11963 | 16#2059/40 | 16#9C/01/A4 = 156/01/164 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 65535 | [PID error Warning] (PER) | [Settings] (SET) [PID controller] (PID)
PIS | PID integral disabled | 16#2EA8 = 11944 | 16#2059/2D | 16#9C/01/91 = 156/01/145 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID Integral OFF] (PIS) | [PID controller] (PID)
FPI | Speed ref. assignment | 16#2EAE = 11950 | 16#2059/33 | 16#9C/01/97 = 156/01/151 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Speed ref. assign.] (FPI) | [PID controller] (PID)
PSR | PID speed input % ref | 16#2EAF = 11951 | 16#2059/34 | 16#9C/01/98 = 156/01/152 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Speed input %] (PSR) | [Settings] (SET) [PID controller] (PID)
PAU | Auto/Manual select input | 16#2EC2 = 11970 | 16#2059/47 | 16#9C/01/AB = 156/01/171 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Auto/Manual assign.] (PAU) | [PID controller] (PID)
PIM | Manual PID reference | 16#2EB2 = 11954 | 16#2059/37 | 16#9C/01/9B = 156/01/155 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Manual PID reference] (PIM) | [PID controller] (PID)
TLS | Low speed timeout | 16#2DB5 = 11701 | 16#2057/2 | 16#9B/01/66 = 155/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Low Speed Timeout] (TLS) | [Settings] (SET) [PID controller] (PID)
PR2 | 2 PID Preset assignment | 16#2E85 = 11909 | 16#2059/A | 16#9C/01/6E = 156/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 PID Preset Assign] (PR2) | [PID preset references] (PRI)
PR4 | 4 PID Preset assignment | 16#2E86 = 11910 | 16#2059/B | 16#9C/01/6F = 156/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 PID Preset Assign] (PR4) | [PID preset references] (PRI)
RP2 | 2nd PID preset reference | 16#2E91 = 11921 | 16#2059/16 | 16#9C/01/7A = 156/01/122 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 300 | 0 ... 32767 | [Ref PID Preset 2] (RP2) | [Settings] (SET) [PID preset references] (PRI)
RP3 | 3rd PID preset reference | 16#2E92 = 11922 | 16#2059/17 | 16#9C/01/7B = 156/01/123 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 600 | 0 ... 32767 | [Ref PID Preset 3] (RP3) | [Settings] (SET) [PID preset references] (PRI)
RP4 | 4th PID preset reference | 16#2E93 = 11923 | 16#2059/18 | 16#9C/01/7C = 156/01/124 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 900 | 0 ... 32767 | [Ref PID Preset 4] (RP4) | [Settings] (SET) [PID preset references] (PRI)
TLA | Torque limit. activation | 16#23FA = 9210 | 16#203E/B | 16#8F/01/0B = 143/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque limit activ.] (TLA) | [Torque limitation] (TOL)
INTP | Torque increment | 16#23FF = 9215 | 16#203E/10 | 16#8F/01/10 = 143/01/16 | INCPER | Configuration and settings | R/WS | WORD (Enumeration) | - | [1%] 1 |  | [Torque increment] (INTP) | [Torque limitation] (TOL)
TLIM | Motoring torque limit | 16#23FB = 9211 | 16#203E/C | 16#8F/01/0C = 143/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 3000 | [Motor torque limit] (TLIM) | [Settings] (SET) [Torque limitation] (TOL)
TLIG | Generator torque limit | 16#23FC = 9212 | 16#203E/D | 16#8F/01/0D = 143/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 3000 | [Gen. torque limit] (TLIG) | [Settings] (SET) [Torque limitation] (TOL)
TAA | Reference torque assignment | 16#23FE = 9214 | 16#203E/F | 16#8F/01/0F = 143/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Torque Assign] (TAA) | [Torque limitation] (TOL)
TLC | Torque analog limit. activ | 16#23FD = 9213 | 16#203E/E | 16#8F/01/0E = 143/01/14 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Analog limit activ.] (TLC) | [Torque limitation] (TOL)
LC2 | Current limitation 2 | 16#23F2 = 9202 | 16#203E/3 | 16#8F/01/03 = 143/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Current Limitation2] (LC2) | [2nd current limit.] (CLI)
CL2 | Current limitation 2 value | 16#23F3 = 9203 | 16#203E/4 | 16#8F/01/04 = 143/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Current Limit2 Value] (CL2) | [Settings] (SET) [2nd current limit.] (CLI)
LLC | Mains contactor control | 16#3522 = 13602 | 16#206A/3 | 16#A5/01/03 = 165/01/03 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Mains Contactor] (LLC) | [Mains contactor command] (LLC)
LES | Device lock assignment | 16#3521 = 13601 | 16#206A/2 | 16#A5/01/02 = 165/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Device Lock] (LES) | [Mains contactor command] (LLC)
LCT | Mains V. time out | 16#3523 = 13603 | 16#206A/4 | 16#A5/01/04 = 165/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 5 s | 5 s ... 999 s | [Mains V. time out] (LCT) | [Mains contactor command] (LLC)
SAF | Fwd stop limit input assig | 16#30D5 = 12501 | 16#205F/2 | 16#9F/01/66 = 159/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop FW limit sw.] (SAF) | [Positioning by sensors] (LPO)
SAR | RV stop limit input assign | 16#30D6 = 12502 | 16#205F/3 | 16#9F/01/67 = 159/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop RV limit sw.] (SAR) | [Positioning by sensors] (LPO)
DAF | Forward slowdown limit | 16#30D7 = 12503 | 16#205F/4 | 16#9F/01/68 = 159/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forward Slowdown] (DAF) | [Positioning by sensors] (LPO)
DAR | Reverse slowdown limit | 16#30D8 = 12504 | 16#205F/5 | 16#9F/01/69 = 159/01/105 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Reverse Slowdown] (DAR) | [Positioning by sensors] (LPO)
CLS | Disable limit switch | 16#30DB = 12507 | 16#205F/8 | 16#9F/01/6C = 159/01/108 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Disable limit sw.] (CLS) | [Positioning by sensors] (LPO)
PAS | Stop type | 16#30DA = 12506 | 16#205F/7 | 16#9F/01/6B = 159/01/107 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [On ramp] RMP |  | [Stop type] (PAS) | [Positioning by sensors] (LPO)
DSF | Deceleration type | 16#30D9 = 12505 | 16#205F/6 | 16#9F/01/6A = 159/01/106 | DSF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] STD |  | [Deceleration type] (DSF) | [Positioning by sensors] (LPO)
STD | Stop distance | 16#30E9 = 12521 | 16#205F/16 | 16#9F/01/7A = 159/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m | 0.00 m | 0.00 m ... 10.00 m | [Stop distance] (STD) | [Positioning by sensors] (LPO)
NLS | Rated linear speed | 16#30DF = 12511 | 16#205F/C | 16#9F/01/70 = 159/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m/s | 1.00 m/s | 0.20 m/s ... 5.00 m/s | [Nom linear speed] (NLS) | [Positioning by sensors] (LPO)
SFD | Distance stop corrector | 16#30EA = 12522 | 16#205F/17 | 16#9F/01/7B = 159/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 50 % ... 200 % | [Stop corrector] (SFD) | [Positioning by sensors] (LPO)
CHM | Multimotors selection | 16#1F59 = 8025 | 16#2032/1A | 16#89/01/1A = 137/01/26 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Multimotors] (CHM) | [Multimotors config] (MMC)
CNF1 | 2 configurations assignt. | 16#1F55 = 8021 | 16#2032/16 | 16#89/01/16 = 137/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Configurations] (CNF1) | [Multimotors config] (MMC)
CNF2 | 3 configurations assignt. | 16#1F56 = 8022 | 16#2032/17 | 16#89/01/17 = 137/01/23 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Configurations] (CNF2) | [Multimotors config] (MMC)
TUL | Autotuning input assignment | 16#258A = 9610 | 16#2042/B | 16#91/01/0B = 145/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Autotuning Assign] (TUL) | [Autotuning by DI] (TNL)
RSF | Fault reset input assignment | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Fault Reset Assign] (RSF) | [Fault reset] (RST)
RP | Product restart | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Product restart] (RP) | [Fault reset] (RST)
RPA | Product restart assignment | 16#1BD9 = 7129 | 16#2029/1E | 16#84/01/82 = 132/01/130 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Prod Restart Assign] (RPA) | [Fault reset] (RST)
ATR | Automatic fault reset | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Auto Fault Reset] (ATR) | [Auto Fault Reset] (ATR)
TAR | Fault Reset time | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] 5 |  | [Fault Reset Time] (TAR) | [Auto Fault Reset] (ATR)
FLR | Catch on fly | 16#0C26 = 3110 | 16#2001/B | 16#70/01/6F = 112/01/111 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Catch On Fly] (FLR) | [Catch on the fly] (FLR)
THT | Motor thermal monitoring mode | 16#258C = 9612 | 16#2042/D | 16#91/01/0D = 145/01/13 | THT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Self cooled motor] ACL |  | [Motor Thermal Mode] (THT) | [Motor thermal monit] (THT)
TTD | Motor thermal threshold | 16#2AFA = 11002 | 16#2050/3 | 16#98/01/03 = 152/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor Therm Thd] (TTD) | [Settings] (SET) [Motor thermal monit] (THT) [Thermal warning stop] (SAT)
TTD2 | Motor 2 thermal threshold | 16#2AFE = 11006 | 16#2050/7 | 16#98/01/07 = 152/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor2 Therm Thd] (TTD2) | [Motor thermal monit] (THT) [Thermal warning stop] (SAT)
TTD3 | Motor 3 thermal threshold | 16#2AFF = 11007 | 16#2050/8 | 16#98/01/08 = 152/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor3 Therm Thd] (TTD3) | [Motor thermal monit] (THT) [Thermal warning stop] (SAT)
OLL | Motor overtemp error response | 16#1B61 = 7009 | 16#2028/A | 16#84/01/0A = 132/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorTemp ErrorResp] (OLL) | [Motor thermal monit] (THT)
OPL | Output Phase Loss assignment | 16#258B = 9611 | 16#2042/C | 16#91/01/0C = 145/01/12 | OPL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [OutPhaseLoss Assign] (OPL) | [Output phase loss] (OPL)
ODT | Output Phase Loss delay | 16#1BA9 = 7081 | 16#2028/52 | 16#84/01/52 = 132/01/82 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.5 s ... 10.0 s | [OutPhaseLoss Delay] (ODT) | [Output phase loss] (OPL)
IPL | Input Phase Loss assignment | 16#1B5A = 7002 | 16#2028/3 | 16#84/01/03 = 132/01/03 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [InPhaseLoss Assign] (IPL) | [Input phase loss] (IPL) [Simply start] (SIM) [DC bus] (DCC)
OHL | Drive overtemp error response | 16#1B60 = 7008 | 16#2028/9 | 16#84/01/09 = 132/01/09 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [DriveTemp ErrorResp] (OHL) | [Drive overheat] (OHL)
THA | Device thermal state warning | 16#2B01 = 11009 | 16#2050/A | 16#98/01/0A = 152/01/10 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Dev Thermal Warning] (THA) | [Drive overheat] (OHL) [Thermal warning stop] (SAT)
ETF | External error assignment | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ext Error assign] (ETF) | [External error] (ETF)
EPL | Device response to external error | 16#1B5E = 7006 | 16#2028/7 | 16#84/01/07 = 132/01/07 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Ext Error Resp] (EPL) | [External error] (ETF)
USB | Response to undervoltage | 16#35EB = 13803 | 16#206C/4 | 16#A6/01/04 = 166/01/04 | USB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error triggered] 0 |  | [Undervoltage Resp] (USB) | [Undervoltage handling] (USB)
URES | Evacuation mains voltage | 16#35E9 = 13801 | 16#206C/2 | 16#A6/01/02 = 166/01/02 | URES | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Mains voltage] (URES) | [Undervoltage handling] (USB) [DC bus] (DCC)
USL | Undervoltage level | 16#35EA = 13802 | 16#206C/3 | 16#A6/01/03 = 166/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 304 V | [Undervoltage level] (USL) | [Undervoltage handling] (USB) [DC bus] (DCC)
UST | Undervoltage timeout | 16#35EC = 13804 | 16#206C/5 | 16#A6/01/05 = 166/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.2 s | 0.2 s ... 999.9 s | [UnderVolt timeout] (UST) | [Undervoltage handling] (USB)
STP | Ctrld stop on power loss | 16#1B5C = 7004 | 16#2028/5 | 16#84/01/05 = 132/01/05 | STP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [UnderV. prevention] (STP) | [Undervoltage handling] (USB)
TSM | Undervolt. restart time | 16#35F5 = 13813 | 16#206C/E | 16#A6/01/0E = 166/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 1.0 s ... 999.9 s | [UnderV. restart tm] (TSM) | [Undervoltage handling] (USB)
UPL | Under V prevention level | 16#35F3 = 13811 | 16#206C/C | 16#A6/01/0C = 166/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 141 V ... 368 V | [Prevention level] (UPL) | [Undervoltage handling] (USB)
SDD | Load slip detection | 16#1B5D = 7005 | 16#2028/6 | 16#84/01/06 = 132/01/06 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Load slip detection] (SDD) | [Encoder monitoring] (SDD)
STM | Maximum stop time | 16#35F6 = 13814 | 16#206C/F | 16#A6/01/0F = 166/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.01 s ... 60.00 s | [Max stop time] (STM) | [Undervoltage handling] (USB)
TBS | DC bus maintain time | 16#35F4 = 13812 | 16#206C/D | 16#A6/01/0D = 166/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 9999 s | 1 s ... 9999 s | [DC bus maintain time] (TBS) | [Undervoltage handling] (USB)
STRT | Output short circuit test | 16#0C28 = 3112 | 16#2001/D | 16#70/01/71 = 112/01/113 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Output Short Circuit Test] (STRT) | [IGBT tests] (TIT)
LFL3 | Response to 4-20mA loss on AI3 | 16#1B65 = 7013 | 16#2028/E | 16#84/01/0E = 132/01/14 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI3 4-20mA loss] (LFL3) | [4-20 mA loss] (LFL)
INH | Disable error detection | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Disable Error Detect] (INH) | [Error detect disabling] (INH)
CLL | Response to Fieldbus module communication interruption | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Fieldbus Interrupt Resp] (CLL) | [Fieldbus monitoring] (CLL)
COL | Response to CANopen error | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CANopen Error Resp] (COL) | [Fieldbus monitoring] (CLL)
SLL | Response to Modbus interruption | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Modbus Error Resp] (SLL) | [Fieldbus monitoring] (CLL)
SSB | Stop type - torque/I limit | 16#2418 = 9240 | 16#203E/29 | 16#8F/01/29 = 143/01/41 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [Trq/I limit. stop] (SSB) | [Torque or I limit detect] (TID)
STO | Torque/I limit. timeout | 16#2419 = 9241 | 16#203E/2A | 16#8F/01/2A = 143/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 1000 ms | 0 ms ... 9999 ms | [Trq/I Limit Timeout] (STO) | [Torque or I limit detect] (TID)
TNL | Response to Autotuning error | 16#1B64 = 7012 | 16#2028/D | 16#84/01/0D = 132/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Tuning Error Resp] (TNL) | [Autotuning error] (TNF)
PPI | Pairing password | 16#36B1 = 14001 | 16#206E/2 | 16#A7/01/02 = 167/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [Pairing password] (PPI) | [Boards pairing] (PPI)
LFF | Fall back speed | 16#1BA8 = 7080 | 16#2028/51 | 16#84/01/51 = 132/01/81 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [FallbackSpeed] (LFF) | [Fallback speed] (LFF)
FQF | Frequency meter | 16#3909 = 14601 | 16#2074/2 | 16#AA/01/02 = 170/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Frequency meter] (FQF) | [Frequency meter] (FQF)
FQC | Pulse scaling divisor | 16#390A = 14602 | 16#2074/3 | 16#AA/01/03 = 170/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 1.0 | 1.0 ... 100.0 | [Pulse scal. divider] (FQC) | [Frequency meter] (FQF)
FQA | Overspd. pulse threshold | 16#390C = 14604 | 16#2074/5 | 16#AA/01/05 = 170/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 20000 Hz | [Overspd. pulse thd.] (FQA) | [Frequency meter] (FQF)
TDS | Pulse Overspeed delay | 16#390D = 14605 | 16#2074/6 | 16#AA/01/06 = 170/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse overspd delay] (TDS) | [Frequency meter] (FQF)
FDT | Level freq. pulse ctrl | 16#390E = 14606 | 16#2074/7 | 16#AA/01/07 = 170/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Level fr. pulse ctrl] (FDT) | [Frequency meter] (FQF)
FQT | Pulse threshold wo Run | 16#390F = 14607 | 16#2074/8 | 16#AA/01/08 = 170/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 1000 Hz | [Pulse thd. wo Run] (FQT) | [Frequency meter] (FQF)
TLD | Dynamic load time | 16#3018 = 12312 | 16#205D/D | 16#9E/01/71 = 158/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 0.01 s | -0.01 s | -0.01 s ... 10.00 s | [Dynamic load time] (TLD) | [Dynamic load detect.] (DLD)
DLD | Dynamic load threshold | 16#3017 = 12311 | 16#205D/C | 16#9E/01/70 = 158/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Dyn. load threshold] (DLD) | [Dynamic load detect.] (DLD)
DLB | Dynamic load Mgt. | 16#3019 = 12313 | 16#205D/E | 16#9E/01/72 = 158/01/114 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Dyn. load Mgt.] (DLB) | [Dynamic load detect.] (DLD)
NCA1 | Scan output 1 address | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
NCA2 | Scan output 2 address | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535
NCA3 | Scan output 3 address | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA4 | Scan output 4 address | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA5 | Scan output 5 address | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA6 | Scan output 6 address | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA7 | Scan output 7 address | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA8 | Scan output 8 address | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA1 | Scan input 1 address | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
NMA2 | Scan input 2 address | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535
NMA3 | Scan input 3 address | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA4 | Scan input 4 address | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA5 | Scan input 5 address | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA6 | Scan input 6 address | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA7 | Scan input 7 address | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA8 | Scan input 8 address | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA1 | Scan input 1 address | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
OMA2 | Scan input 2 address | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535
OMA3 | Scan input 3 address | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA4 | Scan input 4 address | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA5 | Scan input 5 address | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA6 | Scan input 6 address | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA1 | Scan output 1 address | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
OCA2 | Scan output 2 address | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535
OCA3 | Scan output 3 address | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA4 | Scan output 4 address | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA5 | Scan output 5 address | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA6 | Scan output 6 address | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ADD | Device modbus address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus Address] (ADD) | [Modbus Fieldbus] (MD1)
AMOC | Mdb add comm. module | 16#19FB = 6651 | 16#2024/34 | 16#82/01/34 = 130/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus add Com.C.] (AMOC) | [Modbus Fieldbus] (MD1)
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [Modbus Baud Rate] (TBR) | [Modbus Fieldbus] (MD1)
TFO | Modbus format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [Modbus Format] (TFO) | [Modbus Fieldbus] (MD1)
TTO | Modbus timeout | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [ModbusTimeout] (TTO) | [Modbus Fieldbus] (MD1)
ADCO | Device CANopen address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 127 | [CANopen Address] (ADCO) | [CANopen] (CNO)
BDCO | CANopen baudrate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Baud rate 250kbps] 250K |  | [CANopen Baudrate] (BDCO) | [CANopen] (CNO)
ERCO | CANopen error | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [CANopen Error] (ERCO) | [CANopen map] (CNM) [CANopen] (CNO)
FLO | Forced local assignment | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forced Local Assign] (FLO) | [Forced local] (LCF)
FLOC | Forced Local channel assignment | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Forced Local Chan] (FLOC) | [Forced local] (LCF)
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOT) | [Forced local] (LCF)
ADRC | Device address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (ADRC) | [Communication module] (CBD)
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [PPO profile used] (PRFL) | [Communication module] (CBD)
DPMA | DP Master active | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | R/W | WORD (Enumeration) | - | [Master 1] 1 |  | [DP Master Active] (DPMA) | [Communication module] (CBD)
ECSA | EtherCAT second address | 16#1A23 = 6691 | 16#2024/5C | 16#82/01/5C = 130/01/92 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat 2nd addr] (ECSA) | [Communication module] (CBD)
CIOA | Configured assembly | 16#1A0B = 6667 | 16#2024/44 | 16#82/01/44 = 130/01/68 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] 21 |  | [Conf. Assembly] (CIOA) | [Communication module] (CBD)
BDR | Comm. option baudrate | 16#19CB = 6603 | 16#2024/4 | 16#82/01/04 = 130/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Baudrate] (BDR) | [Communication module] (CBD)
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | R/W | WORD (Enumeration) | - | [Automatic] AUTO |  | [Data rate used] (BDRU) | [Communication module] (CBD)
RDS | Rate and duplex setting | 16#FAFB = 64251 |  |  | RDS | Configuration and settings | R/W | WORD (Enumeration) | - | [Auto detected] AUTO |  | [Rate setting] (RDS) | [Communication module] (CBD)
EWE | Enable web and/or email | 16#FB08 = 64264 |  |  |  | Configuration and settings | R/W | WORD (BitString16) | - | 1
ARD | Actual rate and duplex | 16#FB0A = 64266 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | -
L1D | DI1 delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | Refer to programming manual | 0 ms ... 200 ms | [DI1 Delay] (L1D) | [DI1 assignment] (L1A) [DI1 configuration] (L1)
R1 | R1 assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Device in operating state "Fault"] FLT |  | [R1 Assignment] (R1) | [R1 configuration] (R1)
R2 | R2 assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [R2 Assignment] (R2) | [R2 configuration] (R2)
L2D | DI2 delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [DI2 Delay] (L2D) | [DI2 assignment] (L2A) [DI2 configuration] (L2)
R1D | R1 delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Delay time] (R1D) | [R1 configuration] (R1)
R2D | R2 delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Delay time] (R2D) | [R2 configuration] (R2)
L3D | DI3 delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [DI3 Delay] (L3D) | [DI3 assignment] (L3A) [DI3 configuration] (L3)
R1S | R1 active level | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R1 Active at] (R1S) | [R1 configuration] (R1)
R2S | R2 active level | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R2 Active at] (R2S) | [R2 configuration] (R2)
L4D | DI4 delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [DI4 Delay] (L4D) | [DI4 assignment] (L4A) [DI4 configuration] (L4)
R1H | R1 holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R1 Holding time] (R1H) | [R1 configuration] (R1)
R2H | R2 holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R2 Holding time] (R2H) | [R2 configuration] (R2)
L5D | DI5 delay | 16#0FA5 = 4005 | 16#200A/6 | 16#75/01/06 = 117/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [DI5 Delay] (L5D) | [DI5 assignment] (L5A) [DI5 configuration] (L5)
L6D | DI6 delay | 16#0FA6 = 4006 | 16#200A/7 | 16#75/01/07 = 117/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [DI6 Delay] (L6D) | [DI6 assignment] (L6A) [DI6 configuration] (L6)
DO1 | DQ1 assignment | 16#13A7 = 5031 | 16#2014/20 | 16#7A/01/20 = 122/01/32 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ1 Assignment] (DO1) | [DQ1 configuration] (DO1)
DO1D | DQ1 delay time | 16#10B9 = 4281 | 16#200C/52 | 16#76/01/52 = 118/01/82 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ1 Delay time] (DO1D) | [DQ1 configuration] (DO1)
DO1H | DQ1 holding time | 16#10AF = 4271 | 16#200C/48 | 16#76/01/48 = 118/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ1 Holding time] (DO1H) | [DQ1 configuration] (DO1)
DO1S | DQ1 active level | 16#10A5 = 4261 | 16#200C/3E | 16#76/01/3E = 118/01/62 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [DQ1 Active at] (DO1S) | [DQ1 configuration] (DO1)
FRHT | FRH high resolution | 16#0C96 = 3222 | 16#2002/17 | 16#71/01/17 = 113/01/23 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SLCR | LCR without filter | 16#0C98 = 3224 | 16#2002/19 | 16#71/01/19 = 113/01/25 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A
SRFR | RFR without filter | 16#0C99 = 3225 | 16#2002/1A | 16#71/01/1A = 113/01/26 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
MMF | Measured output freq. | 16#0C93 = 3219 | 16#2002/14 | 16#71/01/14 = 113/01/20 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Measured output fr.] (MMF) | [MONITORING] (MON)
SOTR | Motor torque (% of Cn motor in Q12) without filter | 16#0C9A = 3226 | 16#2002/1B | 16#71/01/1B = 113/01/27 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SULN | ULN without filter | 16#0C9D = 3229 | 16#2002/1E | 16#71/01/1E = 113/01/30 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
SOPR | OPR without filter | 16#0CDA = 3290 | 16#2002/5B | 16#71/01/5B = 113/01/91 |  | Configuration and settings | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 %
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 |  | Measurement parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
SAI2 | AI2 physical value without filter | 16#14AC = 5292 | 16#2016/5D | 16#7B/01/5D = 123/01/93 |  | Measurement parameters | R | INT (Signed16) | 0.001 V |  | -32.767 V ... 32.767 V
SAI3 | AI3 physical value without filter | 16#14AD = 5293 | 16#2016/5E | 16#7B/01/5E = 123/01/94 |  | Measurement parameters | R | INT (Signed16) | 0.001 mA |  | -32.767 mA ... 32.767 mA
SAO1 | AO1 physical value without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
PGI | Number of pulses | 16#15E4 = 5604 | 16#201A/5 | 16#7D/01/05 = 125/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1024 | 100 ... 3600 | [Number of pulses] (PGI) | [Encoder configuration] (IEN)
ENS | Encoder type configure | 16#15E8 = 5608 | 16#201A/9 | 16#7D/01/09 = 125/01/09 | ENS | Configuration and settings | R/WS | WORD (Enumeration) | - | [For signals A/A-/B/B-] AABB |  | [Encoder type] (ENS) | [Encoder configuration] (IEN)
ENU | Encoder usage | 16#15E6 = 5606 | 16#201A/7 | 16#7D/01/07 = 125/01/07 | ENU | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [Encoder usage] (ENU) | [Encoder configuration] (IEN)
ULT | Underload detection delay | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Unld Detect Delay] (ULT) | [Process underload] (ULD) [Process underload] (ULD)
SRB | Hysteresis frequency | 16#3841 = 14401 | 16#2072/2 | 16#A9/01/02 = 169/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.3 Hz ... 599.0 Hz | [Hysteresis Freq] (SRB) | [Process underload] (ULD) [Settings] (SET) [Process underload] (ULD) [Process overload] (OLD)
UDL | Response to underload error | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Underload ErrorResp] (UDL) | [Process underload] (ULD) [Process underload] (ULD)
RMUD | Unld. Freq.Thr. Detection | 16#384E = 14414 | 16#2072/F | 16#A9/01/0F = 169/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Unld. FreqThr. Det.] (RMUD) | [Process underload] (ULD) [Settings] (SET) [Process underload] (ULD)
LUL | Unld.Thr. at O speed | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Unld.Thr.0.Speed] (LUL) | [Process underload] (ULD) [Settings] (SET) [Process underload] (ULD)
LUN | Unld.Thr. at Nom. speed | 16#3850 = 14416 | 16#2072/11 | 16#A9/01/11 = 169/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 20 % ... 100 % | [Unld.Thr.Nom.Speed] (LUN) | [Process underload] (ULD) [Settings] (SET) [Process underload] (ULD)
TOL | Overload detection delay | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Ovld Detection Delay] (TOL) | [Process overload] (OLD)
ODL | Response to overload error | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Overload ErrorResp] (ODL) | [Process overload] (OLD)
STOS | Safe torque Off function Status | 16#3BDA = 15322 | 16#207B/17 | 16#AD/01/7B = 173/01/123 | STOS | Safety function | R | WORD (Enumeration) | - |  |  | [STO fct status] (STOS) | [MONIT. SAFETY] (SAF)
AI1I | AI1 input physical image (MAX = 8192) | 16#1466 = 5222 | 16#2016/17 | 16#7B/01/17 = 123/01/23 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2I | AI2 input physical image (MAX = 8192) | 16#1467 = 5223 | 16#2016/18 | 16#7B/01/18 = 123/01/24 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3I | AI3 input physical image (MAX = 8192) | 16#1468 = 5224 | 16#2016/19 | 16#7B/01/19 = 123/01/25 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1I | AO1 output physical image (MAX = 8192) | 16#1483 = 5251 | 16#2016/34 | 16#7B/01/34 = 123/01/52 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
ERR | Ethernet error Code | 16#FB0E = 64270 |  |  |  | Fault parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Ethernet Error Code] (ERR) | [Communication module] (CBD)
ETAD | DRIVECOM : Status word | 16#219B = 8603 | 16#2038/4 | 16#8C/01/04 = 140/01/04 |  | Status parameters | R | WORD (BitString16) | -
FEM | Flow Estimation mode | 16#3E80 = 16000 | 16#2082/1 | 16#B1/01/01 = 177/01/01 | FEM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Activate power vs flow curve] PQ
FTO | Ovld time Before Restart | 16#3857 = 14423 | 16#2072/18 | 16#A9/01/18 = 169/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Overload T.B.Rest.] (FTO) | [Settings] (SET) [Process overload] (OLD)
FTU | Unld time Before Restart | 16#384D = 14413 | 16#2072/E | 16#A9/01/0E = 169/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Underload T.B.Rest.] (FTU) | [Process underload] (ULD) [Settings] (SET) [Process underload] (ULD)
HSC | Device state | 16#33FC = 13308 | 16#2067/9 | 16#A3/01/6D = 163/01/109 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
IL1I | Logic inputs physical image | 16#1451 = 5201 | 16#2016/2 | 16#7B/01/02 = 123/01/02 |  | I/O parameters | R | WORD (BitString16) | -
IPAD | iPar detected error code | 16#FB18 = 64280 |  |  |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [iPar Error Code] (IPAD) | [Communication module] (CBD)
JACC | Anti-Jam forward acceleration | 16#3E37 = 15927 | 16#2081/1C | 16#B0/01/80 = 176/01/128 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 3.0 s | 0.0 s ... 300.0 s | [Anti-Jam Fwd Acc] (JACC) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JACR | Anti-Jam reverse acceleration | 16#3E38 = 15928 | 16#2081/1D | 16#B0/01/81 = 176/01/129 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 3.0 s | 0.0 s ... 300.0 s | [Anti-Jam Rv Acc] (JACR) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JDEC | Anti-Jam forward deceleration | 16#3E35 = 15925 | 16#2081/1A | 16#B0/01/7E = 176/01/126 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 3.0 s | 0.0 s ... 300.0 s | [Anti-Jam Fwd Dec] (JDEC) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JDER | Anti-Jam reverse deceleration | 16#3E36 = 15926 | 16#2081/1B | 16#B0/01/7F = 176/01/127 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 3.0 s | 0.0 s ... 300.0 s | [Anti-Jam Rv Dec] (JDER) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JETC | External Anti-Jam trigger | 16#3E30 = 15920 | 16#2081/15 | 16#B0/01/79 = 176/01/121 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ext Anti-Jam Trigger] (JETC) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JFDS | Anti-Jam forward speed | 16#3E3B = 15931 | 16#2081/20 | 16#B0/01/84 = 176/01/132 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Anti-Jam Fwd Speed] (JFDS) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JFDT | Anti-Jam forward time | 16#3E39 = 15929 | 16#2081/1E | 16#B0/01/82 = 176/01/130 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 1 s | 0 s ... 300 s | [Anti-Jam Fwd Time] (JFDT) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JNBC | Anti-Jam cycle number | 16#3E3E = 15934 | 16#2081/23 | 16#B0/01/87 = 176/01/135 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 0 ... 100 | [Anti-Jam Cycle Nb] (JNBC) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JRVS | Anti-Jam reverse speed | 16#3E3C = 15932 | 16#2081/21 | 16#B0/01/85 = 176/01/133 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Anti-Jam Rv Speed] (JRVS) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JRVT | Anti-Jam reverse time | 16#3E3A = 15930 | 16#2081/1F | 16#B0/01/83 = 176/01/131 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 1 s | 0 s ... 300 s | [Anti-Jam Rv Time] (JRVT) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
JZST | Anti-Jam stop time between forward and reverse | 16#3E3D = 15933 | 16#2081/22 | 16#B0/01/86 = 176/01/134 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [Anti-Jam Stop Time] (JZST) | [Anti-Jam] (AJM) [Anti-Jam] (AJM)
LOC | Current overload threshold | 16#3859 = 14425 | 16#2072/1A | 16#A9/01/1A = 169/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 70 % ... 150 % | [Overload Threshold] (LOC) | [Settings] (SET) [Process overload] (OLD)
PCP1 | Mechanical power entered at point y | 16#3D92 = 15762 | 16#207F/3F | 16#AF/01/A3 = 175/01/163 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kW | 0.00 kW | 0.00 kW ... 327.67 kW | [Power 1] (PCP1) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCP2 | Mechanical power entered at point y | 16#3D93 = 15763 | 16#207F/40 | 16#AF/01/A4 = 175/01/164 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kW | 0.00 kW | 0.00 kW ... 327.67 kW | [Power 2] (PCP2) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCP3 | Mechanical power entered at point y | 16#3D94 = 15764 | 16#207F/41 | 16#AF/01/A5 = 175/01/165 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kW | 0.00 kW | 0.00 kW ... 327.67 kW | [Power 3] (PCP3) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCP4 | Mechanical power entered at point y | 16#3D95 = 15765 | 16#207F/42 | 16#AF/01/A6 = 175/01/166 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kW | 0.00 kW | 0.00 kW ... 327.67 kW | [Power 4] (PCP4) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCP5 | Mechanical power entered at point y | 16#3D96 = 15766 | 16#207F/43 | 16#AF/01/A7 = 175/01/167 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kW | 0.00 kW | 0.00 kW ... 327.67 kW | [Power 5] (PCP5) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCQ1 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D88 = 15752 | 16#207F/35 | 16#AF/01/99 = 175/01/153 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 m³/h | 0.0 m³/h | 0.0 m³/h ... 3276.7 m³/h | [Flow 1] (PCQ1) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCQ2 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D89 = 15753 | 16#207F/36 | 16#AF/01/9A = 175/01/154 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 m³/h | 0.0 m³/h | 0.0 m³/h ... 3276.7 m³/h | [Flow 2] (PCQ2) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCQ3 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8A = 15754 | 16#207F/37 | 16#AF/01/9B = 175/01/155 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 m³/h | 0.0 m³/h | 0.0 m³/h ... 3276.7 m³/h | [Flow 3] (PCQ3) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCQ4 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8B = 15755 | 16#207F/38 | 16#AF/01/9C = 175/01/156 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 m³/h | 0.0 m³/h | 0.0 m³/h ... 3276.7 m³/h | [Flow 4] (PCQ4) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCQ5 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8C = 15756 | 16#207F/39 | 16#AF/01/9D = 175/01/157 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 m³/h | 0.0 m³/h | 0.0 m³/h ... 3276.7 m³/h | [Flow 5] (PCQ5) | [Flow estimation] (FEM) [Flow estimation] (FEM)
PCSP | Pump speed for which curves are entered | 16#3D87 = 15751 | 16#207F/34 | 16#AF/01/98 = 175/01/152 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | 0 rpm | 0 rpm ... 65535 rpm
PFL | U/F Profile | 16#2598 = 9624 | 16#2042/19 | 16#91/01/19 = 145/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 %
SLFV | Estimated pump flow value | 16#3E87 = 16007 | 16#2082/8 | 16#B1/01/08 = 177/01/08 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 m³/h |  | 0.0 m³/h ... 3276.7 m³/h | [Est. Pump Flow] (SLFV) | [MONITORING] (MON) [Flow estimation] (FEM) [Flow estimation] (FEM)
SPD | Motor speed | 16#2EE4 = 12004 | 16#205A/5 | 16#9D/01/05 = 157/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Speed] (SPD) | [MONIT. MOTOR] (MMO)
TQB | Pulse without Run delay | 16#3910 = 14608 | 16#2074/9 | 16#AA/01/09 = 170/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse wo Run delay] (TQB) | [Frequency meter] (FQF)
PUC | Encoder pulse count | 16#15EB = 5611 | 16#201A/C | 16#7D/01/0C = 125/01/12 |  | Actual values parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
SPD1 | Output value customer | 16#2EE8 = 12008 | 16#205A/9 | 16#9D/01/09 = 157/01/09 |  | Actual values parameters | R | UINT (Unsigned16) | 0.01 |  | 0.00 ... 655.35 | [Cust. output value] (SPD1) | [MONITORING] (MON)
MSTP | Memo stop | 16#30EB = 12523 | 16#205F/18 | 16#9F/01/7C = 159/01/124 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Memo Stop] (MSTP) | [Positioning by sensors] (LPO)
PRST | Priority restart | 16#30EC = 12524 | 16#205F/19 | 16#9F/01/7D = 159/01/125 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Priority restart] (PRST) | [Positioning by sensors] (LPO)
INF6 | Internal error 6 (Module identification error) information | 16#0E73 = 3699 | 16#2006/64 | 16#73/01/64 = 115/01/100 |  | History parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
HS1 | HMI status | 16#1C99 = 7321 | 16#202B/16 | 16#85/01/7A = 133/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS1) | [None] (DP1)
HS2 | HMI status | 16#1C9A = 7322 | 16#202B/17 | 16#85/01/7B = 133/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS2) | [None] (DP2)
HS3 | HMI status | 16#1C9B = 7323 | 16#202B/18 | 16#85/01/7C = 133/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS3) | [None] (DP3)
HS4 | HMI status | 16#1C9C = 7324 | 16#202B/19 | 16#85/01/7D = 133/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS4) | [None] (DP4)
HS5 | HMI status | 16#1C9D = 7325 | 16#202B/1A | 16#85/01/7E = 133/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS5) | [None] (DP5)
HS6 | HMI status | 16#1C9E = 7326 | 16#202B/1B | 16#85/01/7F = 133/01/127 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS6) | [None] (DP6)
HS7 | HMI status | 16#1C9F = 7327 | 16#202B/1C | 16#85/01/80 = 133/01/128 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS7) | [None] (DP7)
HS8 | HMI status | 16#1CA0 = 7328 | 16#202B/1D | 16#85/01/81 = 133/01/129 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS8) | [None] (DP8)
MPC | Motor parameter choice | 16#258E = 9614 | 16#2042/F | 16#91/01/0F = 145/01/15 | MPC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Nominal motor power] NPR |  | [Motor param choice] (MPC) | [Simply start] (SIM) [Asynchronous motor] (ASY)
RDAE | Relative d-axis error in % | 16#25CC = 9676 | 16#2042/4D | 16#91/01/4D = 145/01/77 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Relative d-axis error] (RDAE) | [Synchronous motor] (SYN)
TUNU | Autotuning usage | 16#2593 = 9619 | 16#2042/14 | 16#91/01/14 = 145/01/20 | TUNU | Configuration and settings | R/WS | WORD (Enumeration) | - | [Use the motor thermal evolution] TM |  | [Autotuning Usage] (TUNU) | [Asynchronous motor] (ASY) [Synchronous motor] (SYN)
BOO | Boost | 16#3658 = 13912 | 16#206D/D | 16#A6/01/71 = 166/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 0 % | -100 % ... 100 % | [Boost] (BOO) | [Motor control] (DRC)
FAB | Frequency boost | 16#3657 = 13911 | 16#206D/C | 16#A6/01/70 = 166/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Freq Boost] (FAB) | [Motor control] (DRC)
FRI | Frequency of the HF injection signal | 16#3CF1 = 15601 | 16#207E/2 | 16#AF/01/02 = 175/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 500 Hz | 250 Hz ... 1000 Hz | [HF injection freq.] (FRI) | [Synchronous motor] (SYN)
AIV2 | AIV2 Image input | 16#14A3 = 5283 | 16#2016/54 | 16#7B/01/54 = 123/01/84 |  | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -8192 ... 8192
AIC2 | Channel assignment for virtual Analog input AIV2 | 16#14A4 = 5284 | 16#2016/55 | 16#7B/01/55 = 123/01/85 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [AIV2 Channel Assign] (AIC2) | [Virtual AI2] (AV2) [PID controller] (PID)
AI1L | Analog input 1 range | 16#1182 = 4482 | 16#200E/53 | 16#77/01/53 = 119/01/83 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI1 range] (AI1L) | [AI1 configuration] (AI1)
AI2L | Analog input 2 range | 16#1183 = 4483 | 16#200E/54 | 16#77/01/54 = 119/01/84 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI2 range] (AI2L) | [AI2 configuration] (AI2)
AI3L | Analog input 3 range | 16#1184 = 4484 | 16#200E/55 | 16#77/01/55 = 119/01/85 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI3 range] (AI3L) | [AI3 configuration] (AI3)
APH | Power consumption | 16#0C9E = 3230 | 16#2002/1F | 16#71/01/1F = 113/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Consumption] (APH) | [Power-On time] (PET)
BNS | Program size | 16#3A90 = 14992 | 16#2077/5D | 16#AB/01/C1 = 171/01/193 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Program size] (BNS) | [FB Identification] (FBI) [FB Identification] (FBI)
BNV | Program format version | 16#3A8E = 14990 | 16#2077/5B | 16#AB/01/BF = 171/01/191 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Prg. format version] (BNV) | [FB Identification] (FBI) [FB Identification] (FBI)
BTPI | PIN code | 16#1A11 = 6673 | 16#2024/4A | 16#82/01/4A = 130/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [PIN code] (BTPI) | [Bluetooth] (BTH)
BTUA | Bluetooth Activation | 16#1A0E = 6670 | 16#2024/47 | 16#82/01/47 = 130/01/71 | ONOFF | Configuration and settings | R/WS | WORD (Enumeration) | - | [OFF] OFF |  | [Bluetooth Activation] (BTUA) | [Bluetooth] (BTH)
BTUC | Bluetooth Visibility | 16#1A0F = 6671 | 16#2024/48 | 16#82/01/48 = 130/01/72 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Bluetooth Visibility] (BTUC) | [Bluetooth] (BTH)
BVER | Program version | 16#3A91 = 14993 | 16#2077/5E | 16#AB/01/C2 = 171/01/194 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 255 | [Program version] (BVER) | [FB Identification] (FBI) [FB Identification] (FBI)
CCFG | Customized macro | 16#0BED = 3053 | 16#2000/36 | 16#70/01/36 = 112/01/54 | N_Y | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Customized macro] (CCFG) | [Simply start] (SIM)
CFG | Macro configuration | 16#0BEC = 3052 | 16#2000/35 | 16#70/01/35 = 112/01/53 | CFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Solar application] SUN |  | [Macro Config] (CFG) | [Configuration] (CONF) [Simply start] (SIM)
CIO2 | Configured assembly | 16#1A0C = 6668 | 16#2024/45 | 16#82/01/45 = 130/01/69 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] 21 |  | [Conf. Assembly] (CIO2) | [Communication module] (CBD)
CP1 | Ext weight point 1Y | 16#2758 = 10072 | 16#2046/49 | 16#93/01/49 = 147/01/73 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 A | Refer to programming manual | -3276.7 A ... 3276.7 A | [Point 1Y] (CP1) | [External weight meas.] (ELM)
CP2 | Ext weight point 2Y | 16#275A = 10074 | 16#2046/4B | 16#93/01/4B = 147/01/75 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 A | 0.0 A | -3276.7 A ... 3276.7 A | [Point 2Y] (CP2) | [External weight meas.] (ELM)
CTV | Catalogue version | 16#3A8F = 14991 | 16#2077/5C | 16#AB/01/C0 = 171/01/192 |  | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Catalogue version] (CTV) | [FB Identification] (FBI) [FB Identification] (FBI)
DAL | Slowdown limit config. | 16#30DD = 12509 | 16#205F/A | 16#9F/01/6E = 159/01/110 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active low] LO |  | [Slowdown limit cfg.] (DAL) | [Positioning by sensors] (LPO)
DANF | Available ANF detection direction | 16#160B = 5643 | 16#201A/2C | 16#7D/01/2C = 125/01/44 | DANF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Trip in case of overspeed] OVER |  | [ANF Direction check] (DANF) | [Encoder configuration] (IEN) [Encoder monitoring] (SDD)
DAS | Delay to open contactor | 16#332E = 13102 | 16#2065/3 | 16#A2/01/67 = 162/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 5.00 s | [Delay to open cont.] (DAS) | [Output contactor cmd] (OCC)
DBS | Delay to close o/p cont. | 16#332D = 13101 | 16#2065/2 | 16#A2/01/66 = 162/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.15 s | 0.05 s ... 60.00 s | [Delay to motor run] (DBS) | [Output contactor cmd] (OCC)
DCCC | DC Bus compatibility | 16#361B = 13851 | 16#206C/34 | 16#A6/01/34 = 166/01/52 | DCCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Altivar compatibility] ATV |  | [DC Bus compat.] (DCCC) | [DC bus] (DCC)
DCCM | DC Bus chaining mode | 16#361A = 13850 | 16#206C/33 | 16#A6/01/33 = 166/01/51 | DCCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [DC Bus chaining] (DCCM) | [DC bus] (DCC)
DTF | Decrease ref frequency | 16#2FB3 = 12211 | 16#205C/C | 16#9E/01/0C = 158/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Decrease Ref Freq] (DTF) | [Traverse control] (TR0)
EBHT | Encoder board hardware type | 16#0DE9 = 3561 | 16#2005/3E | 16#72/01/A2 = 114/01/162 | EBHT | Configuration and settings | R | WORD (Enumeration) | - | [Not configured] NO
EBO | End of reel | 16#2FB5 = 12213 | 16#205C/E | 16#9E/01/0E = 158/01/14 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [End reel] (EBO) | [Traverse control] (TR0)
ETHM | Ethernet protocol | 16#FAF1 = 64241 |  |  | ETHM | Configuration and settings | R/W | WORD (Enumeration) | - | [ModbusTCP] MBTP |  | [Ethernet protocol] (ETHM) | [Communication module] (CBD)
FANF | ANF error detection frequency | 16#160A = 5642 | 16#201A/2B | 16#7D/01/2B = 125/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 5.0 Hz | 0.1 Hz ... 50.0 Hz | [ANF Frequency Thd] (FANF) | [Encoder configuration] (IEN) [Encoder monitoring] (SDD)
FBCD | FunctionBlock activation | 16#3A72 = 14962 | 16#2077/3F | 16#AB/01/A3 = 171/01/163 | SPST | Function blocks | R/W | WORD (Enumeration) | - |  |  | [FB Activation] (FBCD) | [Function Blocks] (FBM)
FBDF | FunctionBlock response to drive error | 16#3A75 = 14965 | 16#2077/42 | 16#AB/01/A6 = 171/01/166 | SPIG | Function blocks | R/WS | WORD (Enumeration) | - | [Stop] STOP |  | [FB DriveError Resp] (FBDF) | [Function Blocks] (FBM)
FBFT | FunctionBlock error | 16#3A71 = 14961 | 16#2077/3E | 16#AB/01/A2 = 171/01/162 | FBFT | Function blocks | R | WORD (Enumeration) | - |  |  | [FB Error] (FBFT) | [Monit. Fun. Blocks] (MFB) [Monit. Fun. Blocks] (MFB)
FBRM | FunctionBlock start mode | 16#3A73 = 14963 | 16#2077/40 | 16#AB/01/A4 = 171/01/164 | PSLIN | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [FB Start Mode] (FBRM) | [Function Blocks] (FBM)
FBSM | Motor stop type on FunctionBlock stop | 16#3A74 = 14964 | 16#2077/41 | 16#AB/01/A5 = 171/01/165 | ECFG | Function blocks | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [FB Motor Stop Type] (FBSM) | [Function Blocks] (FBM)
FBST | FunctionBlock status | 16#3A70 = 14960 | 16#2077/3D | 16#AB/01/A1 = 171/01/161 | FBST | Function blocks | R | WORD (Enumeration) | - |  |  | [FB Status] (FBST) | [Monit. Fun. Blocks] (MFB) [Monit. Fun. Blocks] (MFB)
FDRD | FDR file error code | 16#FAE9 = 64233 |  |  |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [FDR Error Code] (FDRD) | [Communication module] (CBD)
GDLA | Guard Door Locking assignment | 16#3C1E = 15390 | 16#207B/5B | 16#AD/01/BF = 173/01/191 | SMSA | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
GDLS | GDL Status | 16#3C21 = 15393 | 16#207B/5E | 16#AD/01/C2 = 173/01/194 | GDLS | Safety function | R | WORD (Enumeration) | - |  |  | [GDL Status] (GDLS) | [MONIT. SAFETY] (SAF)
GLB | Global transmit | 16#19CF = 6607 | 16#2024/8 | 16#82/01/08 = 130/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 32
GLLD | GDL Long delay | 16#3C1F = 15391 | 16#207B/5C | 16#AD/01/C0 = 173/01/192 |  | Safety function | R/WS | UINT (Unsigned16) | 1 s | 1 s | 1 s ... 3600 s
GLSD | GDL Short delay | 16#3C20 = 15392 | 16#207B/5D | 16#AD/01/C1 = 173/01/193 |  | Safety function | R/WS | UINT (Unsigned16) | 1 s | 1 s | 1 s ... 3600 s
HRFC | Extended fault reset activation | 16#1BEE = 7150 | 16#2029/33 | 16#84/01/97 = 132/01/151 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Extended Fault Reset] (HRFC) | [Fault reset] (RST)
I2TA | I²t model activation for current limitation | 16#259F = 9631 | 16#2042/20 | 16#91/01/20 = 145/01/32 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [I²t model activation] (I2TA) | [Current Limit Dyn] (I2T)
I2TI | Maximum current of I2t model | 16#25A0 = 9632 | 16#2042/21 | 16#91/01/21 = 145/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 6553.5 A | [Max Current of I2t] (I2TI) | [Current Limit Dyn] (I2T)
I2TM | Monitoring of I2t overload level | 16#25A2 = 9634 | 16#2042/23 | 16#91/01/23 = 145/01/35 |  | Configuration and settings | R | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [I2t overload level] (I2TM) | [MONIT. MOTOR] (MMO)
I2TT | Maximum time of I2t model | 16#25A1 = 9633 | 16#2042/22 | 16#91/01/22 = 145/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 655.35 s | [Max Time of I2t] (I2TT) | [Current Limit Dyn] (I2T)
IA01 | FB : Analog Input XX assignment | 16#3A34 = 14900 | 16#2077/1 | 16#AB/01/65 = 171/01/101 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA01) | [Input Assignments] (FBA)
IA02 | FB : Analog Input XX assignment | 16#3A35 = 14901 | 16#2077/2 | 16#AB/01/66 = 171/01/102 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA02) | [Input Assignments] (FBA)
IA03 | FB : Analog Input XX assignment | 16#3A36 = 14902 | 16#2077/3 | 16#AB/01/67 = 171/01/103 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA03) | [Input Assignments] (FBA)
IA04 | FB : Analog Input XX assignment | 16#3A37 = 14903 | 16#2077/4 | 16#AB/01/68 = 171/01/104 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA04) | [Input Assignments] (FBA)
IA05 | FB : Analog Input XX assignment | 16#3A38 = 14904 | 16#2077/5 | 16#AB/01/69 = 171/01/105 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA05) | [Input Assignments] (FBA)
IA06 | FB : Analog Input XX assignment | 16#3A39 = 14905 | 16#2077/6 | 16#AB/01/6A = 171/01/106 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA06) | [Input Assignments] (FBA)
IA07 | FB : Analog Input XX assignment | 16#3A3A = 14906 | 16#2077/7 | 16#AB/01/6B = 171/01/107 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA07) | [Input Assignments] (FBA)
IA08 | FB : Analog Input XX assignment | 16#3A3B = 14907 | 16#2077/8 | 16#AB/01/6C = 171/01/108 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA08) | [Input Assignments] (FBA)
IA09 | FB : Analog Input XX assignment | 16#3A3C = 14908 | 16#2077/9 | 16#AB/01/6D = 171/01/109 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA09) | [Input Assignments] (FBA)
IA10 | FB : Analog Input XX assignment | 16#3A3D = 14909 | 16#2077/A | 16#AB/01/6E = 171/01/110 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [None] (IA10) | [Input Assignments] (FBA)
IBRA | IBR when weight loss | 16#275B = 10075 | 16#2046/4C | 16#93/01/4C = 147/01/76 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Ibr 4-20 mA loss] (IBRA) | [External weight meas.] (ELM)
ICFG | iPAR local configuration | 16#FB14 = 64276 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Local Conf] (ICFG) | [Communication module] (CBD)
IL01 | FB : Logical Input XX assignment | 16#3A48 = 14920 | 16#2077/15 | 16#AB/01/79 = 171/01/121 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL01) | [Input Assignments] (FBA)
IL02 | FB : Logical Input XX assignment | 16#3A49 = 14921 | 16#2077/16 | 16#AB/01/7A = 171/01/122 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL02) | [Input Assignments] (FBA)
IL03 | FB : Logical Input XX assignment | 16#3A4A = 14922 | 16#2077/17 | 16#AB/01/7B = 171/01/123 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL03) | [Input Assignments] (FBA)
IL04 | FB : Logical Input XX assignment | 16#3A4B = 14923 | 16#2077/18 | 16#AB/01/7C = 171/01/124 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL04) | [Input Assignments] (FBA)
IL05 | FB : Logical Input XX assignment | 16#3A4C = 14924 | 16#2077/19 | 16#AB/01/7D = 171/01/125 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL05) | [Input Assignments] (FBA)
IL06 | FB : Logical Input XX assignment | 16#3A4D = 14925 | 16#2077/1A | 16#AB/01/7E = 171/01/126 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL06) | [Input Assignments] (FBA)
IL07 | FB : Logical Input XX assignment | 16#3A4E = 14926 | 16#2077/1B | 16#AB/01/7F = 171/01/127 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL07) | [Input Assignments] (FBA)
IL08 | FB : Logical Input XX assignment | 16#3A4F = 14927 | 16#2077/1C | 16#AB/01/80 = 171/01/128 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL08) | [Input Assignments] (FBA)
IL09 | FB : Logical Input XX assignment | 16#3A50 = 14928 | 16#2077/1D | 16#AB/01/81 = 171/01/129 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL09) | [Input Assignments] (FBA)
IL10 | FB : Logical Input XX assignment | 16#3A51 = 14929 | 16#2077/1E | 16#AB/01/82 = 171/01/130 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [None] (IL10) | [Input Assignments] (FBA)
IPAE | iPar service status | 16#FB17 = 64279 |  |  | IPAE | Configuration and settings | R/W | WORD (Enumeration) | - | [Idle State] IDLE |  | [iPar Status] (IPAE) | [Communication module] (CBD)
IPAF | iPar response to detected error | 16#FB15 = 64277 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [iPar Error Response] (IPAF) | [Communication module] (CBD)
IPAS | iPar autosave activation | 16#FB13 = 64275 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Autosave Act] (IPAS) | [Communication module] (CBD)
IPAT | iPar autosave timer | 16#FB16 = 64278 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 0 ... 9999 | [iPar Autosave Timer] (IPAT) | [Communication module] (CBD)
IPAV | iPar service activation | 16#FB12 = 64274 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Activation] (IPAV) | [Communication module] (CBD)
IPM | IP mode | 16#FAFA = 64250 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [IP mode] (IPM) | [Communication module] (CBD)
LA01 | FB : ADL Container XX | 16#3A5C = 14940 | 16#2077/29 | 16#AB/01/8D = 171/01/141 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA02 | FB : ADL Container XX | 16#3A5D = 14941 | 16#2077/2A | 16#AB/01/8E = 171/01/142 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA03 | FB : ADL Container XX | 16#3A5E = 14942 | 16#2077/2B | 16#AB/01/8F = 171/01/143 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA04 | FB : ADL Container XX | 16#3A5F = 14943 | 16#2077/2C | 16#AB/01/90 = 171/01/144 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA05 | FB : ADL Container XX | 16#3A60 = 14944 | 16#2077/2D | 16#AB/01/91 = 171/01/145 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA06 | FB : ADL Container XX | 16#3A61 = 14945 | 16#2077/2E | 16#AB/01/92 = 171/01/146 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA07 | FB : ADL Container XX | 16#3A62 = 14946 | 16#2077/2F | 16#AB/01/93 = 171/01/147 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA08 | FB : ADL Container XX | 16#3A63 = 14947 | 16#2077/30 | 16#AB/01/94 = 171/01/148 |  | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
LA1D | DA1 On delay | 16#0FB5 = 4021 | 16#200A/16 | 16#75/01/16 = 117/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [DA1 On Delay] (LA1D) | [DA1 assignment] (LA1A) [DA1 Configuration] (LA1)
LA2D | DA2 On delay | 16#0FB6 = 4022 | 16#200A/17 | 16#75/01/17 = 117/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [DA2 On Delay] (LA2D) | [DA2 assignment] (LA2A) [DA2 Configuration] (LA2)
LANF | ANF error detection level | 16#1608 = 5640 | 16#201A/29 | 16#7D/01/29 = 125/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [ANF Detection level] (LANF) | [Encoder configuration] (IEN) [Encoder monitoring] (SDD)
LET | External error condition | 16#1BB2 = 7090 | 16#2028/5B | 16#84/01/5B = 132/01/91 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active high] HIG |  | [Ext Error Condition] (LET) | [External error] (ETF)
LIDT | DI Debounce time | 16#3BE2 = 15330 | 16#207B/1F | 16#AD/01/83 = 173/01/131 |  | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 50 ms | 0 ms ... 2000 ms
LIRT | DI Response time | 16#3BE3 = 15331 | 16#207B/20 | 16#AD/01/84 = 173/01/132 |  | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 50 ms
LO1 | LO1 assignment | 16#1391 = 5009 | 16#2014/A | 16#7A/01/0A = 122/01/10 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [LO1 assignment] (LO1) | [LO1 CONFIGURATION] (LO1)
LO1D | LO1 delay time | 16#1099 = 4249 | 16#200C/32 | 16#76/01/32 = 118/01/50 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [LO1 delay time] (LO1D) | [LO1 CONFIGURATION] (LO1)
LO1H | LO1 holding time | 16#1085 = 4229 | 16#200C/1E | 16#76/01/1E = 118/01/30 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [LO1 holding time] (LO1H) | [LO1 CONFIGURATION] (LO1)
LO1S | LO1 active level | 16#1071 = 4209 | 16#200C/A | 16#76/01/0A = 118/01/10 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [LO1 active at] (LO1S) | [LO1 CONFIGURATION] (LO1)
LO1F | Enable LO1 fallback | 16#10C4 = 4292 | 16#200C/5D | 16#76/01/5D = 118/01/93 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable LO1 fallback] (LO1F) | [LO1 CONFIGURATION] (LO1)
LP1 | Ext weight point 1 X | 16#2757 = 10071 | 16#2046/48 | 16#93/01/48 = 147/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 0.00 % | 0.00 % ... 99.99 % | [Point 1 X] (LP1) | [External weight meas.] (ELM)
LP2 | Ext weight point 2 X | 16#2759 = 10073 | 16#2046/4A | 16#93/01/4A = 147/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 50.00 % | 0.01 % ... 100.00 % | [Point 2 X] (LP2) | [External weight meas.] (ELM)
LRS1 | Logic result status 1 (PSL 000-015) | 16#0CB2 = 3250 | 16#2002/33 | 16#71/01/33 = 113/01/51 |  | Status parameters | R | WORD (BitString16) | -
LRS2 | Logic result status 2 (PSL 016-031) | 16#0CB3 = 3251 | 16#2002/34 | 16#71/01/34 = 113/01/52 |  | Status parameters | R | WORD (BitString16) | -
LRS3 | Logic result status 3 (PSL 032-047) | 16#0CB4 = 3252 | 16#2002/35 | 16#71/01/35 = 113/01/53 |  | Status parameters | R | WORD (BitString16) | -
LRS4 | Logic result status 4 (PSL 048-063) | 16#0CB5 = 3253 | 16#2002/36 | 16#71/01/36 = 113/01/54 |  | Status parameters | R | WORD (BitString16) | -
LRS5 | Logic result status 5 (PSL 064-079) | 16#0CB6 = 3254 | 16#2002/37 | 16#71/01/37 = 113/01/55 |  | Status parameters | R | WORD (BitString16) | -
LRS6 | Logic result status 6 (PSL 080-095) | 16#0CB7 = 3255 | 16#2002/38 | 16#71/01/38 = 113/01/56 |  | Status parameters | R | WORD (BitString16) | -
LRS7 | Logic result status 7 (PSL 096-111) | 16#0CB8 = 3256 | 16#2002/39 | 16#71/01/39 = 113/01/57 |  | Status parameters | R | WORD (BitString16) | -
LRS8 | Logic result status 8 (PSL 112-127) | 16#0CB9 = 3257 | 16#2002/3A | 16#71/01/3A = 113/01/58 |  | Status parameters | R | WORD (BitString16) | -
M001 | FB : M0XX parameter | 16#3A7A = 14970 | 16#2077/47 | 16#AB/01/AB = 171/01/171 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M001) | [FB Parameters] (FBP)
M002 | FB : M0XX parameter | 16#3A7B = 14971 | 16#2077/48 | 16#AB/01/AC = 171/01/172 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M002) | [FB Parameters] (FBP)
M003 | FB : M0XX parameter | 16#3A7C = 14972 | 16#2077/49 | 16#AB/01/AD = 171/01/173 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M003) | [FB Parameters] (FBP)
M004 | FB : M0XX parameter | 16#3A7D = 14973 | 16#2077/4A | 16#AB/01/AE = 171/01/174 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M004) | [FB Parameters] (FBP)
M005 | FB : M0XX parameter | 16#3A7E = 14974 | 16#2077/4B | 16#AB/01/AF = 171/01/175 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M005) | [FB Parameters] (FBP)
M006 | FB : M0XX parameter | 16#3A7F = 14975 | 16#2077/4C | 16#AB/01/B0 = 171/01/176 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M006) | [FB Parameters] (FBP)
M007 | FB : M0XX parameter | 16#3A80 = 14976 | 16#2077/4D | 16#AB/01/B1 = 171/01/177 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M007) | [FB Parameters] (FBP)
M008 | FB : M0XX parameter | 16#3A81 = 14977 | 16#2077/4E | 16#AB/01/B2 = 171/01/178 |  | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [None] (M008) | [FB Parameters] (FBP)
NTJ | Number of IGBT warnings | 16#0CA9 = 3241 | 16#2002/2A | 16#71/01/2A = 113/01/42 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [IGBT Warning Nb] (NTJ) | [Diagnostics] (DGT)
OCC | Output contactor control assignment | 16#3330 = 13104 | 16#2065/5 | 16#A2/01/69 = 162/01/105 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Out. Contactor Assign] (OCC) | [Output contactor cmd] (OCC)
PES | Weight sensor assignment | 16#2756 = 10070 | 16#2046/47 | 16#93/01/47 = 147/01/71 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Weight Sensor Assign] (PES) | [External weight meas.] (ELM)
PFI | RP filter | 16#33F8 = 13304 | 16#2067/5 | 16#A3/01/69 = 163/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [RP filter] (PFI) | [RP input] (PFRC) [DI5 configuration] (L5)
PFR | RP maximum value | 16#33F7 = 13303 | 16#2067/4 | 16#A3/01/68 = 163/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 20.00 kHz | 0.00 kHz ... 20.00 kHz | [RP max value] (PFR) | [RP input] (PFRC) [DI5 configuration] (L5)
PIL | Minimum pulse input | 16#33F6 = 13302 | 16#2067/3 | 16#A3/01/67 = 163/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 0.00 kHz | 0.00 kHz ... 20.00 kHz | [RP min value] (PIL) | [RP input] (PFRC) [DI5 configuration] (L5)
PRC | Peer Cop node | 16#19CE = 6606 | 16#2024/7 | 16#82/01/07 = 130/01/07 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO
PTCL | PTC probe feedback handling | 16#3393 = 13203 | 16#2066/4 | 16#A3/01/04 = 163/01/04 | PTCX | Configuration and settings | R/WS | WORD (Enumeration) | - | [No management] NO |  | [PTC Fdbk Handling] (PTCL) | [PTC management] (PTC)
PWRM | PWRM assignment | 16#3BD9 = 15321 | 16#207B/16 | 16#AD/01/7A = 173/01/122 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] PWRM
QSH | Quick step high | 16#2FAC = 12204 | 16#205C/5 | 16#9E/01/05 = 158/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [Quick step High] (QSH) | [Settings] (SET) [Traverse control] (TR0)
QSL | Quick step low | 16#2FAD = 12205 | 16#205C/6 | 16#9E/01/06 = 158/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [Quick step Low] (QSL) | [Settings] (SET) [Traverse control] (TR0)
R1F | Enable relay 1 fallback | 16#10C2 = 4290 | 16#200C/5B | 16#76/01/5B = 118/01/91 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R1 fallback] (R1F) | [R1 configuration] (R1)
R2F | Enable relay 2 fallback | 16#10C3 = 4291 | 16#200C/5C | 16#76/01/5C = 118/01/92 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R2 fallback] (R2F) | [R2 configuration] (R2)
RCA | Output contactor fdbk | 16#332F = 13103 | 16#2065/4 | 16#A2/01/68 = 162/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Output contact fdbk] (RCA) | [Output contactor cmd] (OCC)
RSL | PID wake up threshold | 16#2EB8 = 11960 | 16#2059/3D | 16#9C/01/A1 = 156/01/161 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 | 0.0 | 0.0 ... 100.0 | [PID wake up thresh.] (RSL) | [PID controller] (PID)
RTR | Traverse control disabled | 16#2FB2 = 12210 | 16#205C/B | 16#9E/01/0B = 158/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Traverse Ctrl OFF] (RTR) | [Traverse control] (TR0)
S001 | FB system word 01 | 16#3A84 = 14980 | 16#2077/51 | 16#AB/01/B5 = 171/01/181 |  | Function blocks | R | WORD (BitString16) | -
S002 | FB system word 02 | 16#3A85 = 14981 | 16#2077/52 | 16#AB/01/B6 = 171/01/182 |  | Function blocks | R | WORD (BitString16) | -
S006 | FB system word 06 | 16#3A89 = 14985 | 16#2077/56 | 16#AB/01/BA = 171/01/186 |  | Function blocks | R | WORD (BitString16) | -
SAF1 | Safety error register 1 | 16#3BF6 = 15350 | 16#207B/33 | 16#AD/01/97 = 173/01/151 |  | Safety function | R | WORD (BitString16) | - |  |  | [Safety Error Reg1] (SAF1) | [More error info] (AFI)
SAF2 | Safety error register 2 | 16#3BFF = 15359 | 16#207B/3C | 16#AD/01/A0 = 173/01/160 |  | Safety function | R | WORD (BitString16) | - |  |  | [Safety Error Reg2] (SAF2) | [More error info] (AFI)
SAL | Stop limit configuration | 16#30DC = 12508 | 16#205F/9 | 16#9F/01/6D = 159/01/109 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active low] LO |  | [Stop limit config.] (SAL) | [Positioning by sensors] (LPO)
SAT | Thermal warning stop | 16#2B0D = 11021 | 16#2050/16 | 16#98/01/16 = 152/01/22 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Thermal Warn stop] (SAT) | [Thermal warning stop] (SAT)
SCL3 | Ground short circuit detection | 16#1B6A = 7018 | 16#2028/13 | 16#84/01/13 = 132/01/19 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ground short circuit] (SCL3) | [DC bus] (DCC)
SDS | Customer scale factor | 16#2EE1 = 12001 | 16#205A/2 | 16#9D/01/02 = 157/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 30.0 | 0.1 ... 200.0 | [Scale factor display] (SDS) | [Settings] (SET)
SF00 | SAFF subcode 0 | 16#3BF7 = 15351 | 16#207B/34 | 16#AD/01/98 = 173/01/152 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 0] (SF00) | [More error info] (AFI)
SF01 | SAFF subcode 1 | 16#3BF8 = 15352 | 16#207B/35 | 16#AD/01/99 = 173/01/153 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 1] (SF01) | [More error info] (AFI)
SF02 | SAFF subcode 2 | 16#3BF9 = 15353 | 16#207B/36 | 16#AD/01/9A = 173/01/154 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 2] (SF02) | [More error info] (AFI)
SF03 | SAFF subcode 3 | 16#3BFA = 15354 | 16#207B/37 | 16#AD/01/9B = 173/01/155 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 3] (SF03) | [More error info] (AFI)
SF04 | SAFF subcode 4 | 16#3BFB = 15355 | 16#207B/38 | 16#AD/01/9C = 173/01/156 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 4] (SF04) | [More error info] (AFI)
SF05 | SAFF subcode 5 | 16#3BFC = 15356 | 16#207B/39 | 16#AD/01/9D = 173/01/157 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 5] (SF05) | [More error info] (AFI)
SF06 | SAFF subcode 6 | 16#3BFD = 15357 | 16#207B/3A | 16#AD/01/9E = 173/01/158 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 6] (SF06) | [More error info] (AFI)
SF07 | SAFF subcode 7 | 16#3BFE = 15358 | 16#207B/3B | 16#AD/01/9F = 173/01/159 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 7] (SF07) | [More error info] (AFI)
SF08 | SAFF subcode 8 | 16#3C00 = 15360 | 16#207B/3D | 16#AD/01/A1 = 173/01/161 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 8] (SF08) | [More error info] (AFI)
SF09 | SAFF subcode 9 | 16#3C01 = 15361 | 16#207B/3E | 16#AD/01/A2 = 173/01/162 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 9] (SF09) | [More error info] (AFI)
SF10 | SAFF subcode 10 | 16#3C02 = 15362 | 16#207B/3F | 16#AD/01/A3 = 173/01/163 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 10] (SF10) | [More error info] (AFI)
SF11 | SAFF subcode 11 | 16#3C03 = 15363 | 16#207B/40 | 16#AD/01/A4 = 173/01/164 |  | Safety function | R | WORD (BitString16) | - |  |  | [SAFF Subcode 11] (SF11) | [More error info] (AFI)
SFTY | Drive Safety status | 16#3BF0 = 15344 | 16#207B/2D | 16#AD/01/91 = 173/01/145 | SFTY | Safety function | R | WORD (Enumeration) | -
SLSA | SLS assignment | 16#3BC4 = 15300 | 16#207B/1 | 16#AD/01/65 = 173/01/101 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SLSP | SLS Set point | 16#3BC6 = 15302 | 16#207B/3 | 16#AD/01/67 = 173/01/103 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
SLSS | Safe limited speed status | 16#3BC8 = 15304 | 16#207B/5 | 16#AD/01/69 = 173/01/105 | SLSS | Safety function | R | WORD (Enumeration) | - |  |  | [SLS status] (SLSS) | [MONIT. SAFETY] (SAF)
SLT | SLS Type | 16#3BC5 = 15301 | 16#207B/2 | 16#AD/01/66 = 173/01/102 | SLT | Safety function | R/WS | WORD (Enumeration) | - | [None] TYP1
SLTT | SLS Tolerance threshold | 16#3BC7 = 15303 | 16#207B/4 | 16#AD/01/68 = 173/01/104 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
SLWT | SLS wait time | 16#3BC9 = 15305 | 16#207B/6 | 16#AD/01/6A = 173/01/106 |  | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 5000 ms
SMLH | SMS Speed High Limit | 16#3C16 = 15382 | 16#207B/53 | 16#AD/01/B7 = 173/01/183 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 6553.5 Hz
SMLL | SMS Speed Low Limit | 16#3C15 = 15381 | 16#207B/52 | 16#AD/01/B6 = 173/01/182 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 6553.5 Hz
SMLS | SMS Speed Selection | 16#3C17 = 15383 | 16#207B/54 | 16#AD/01/B8 = 173/01/184 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SMSA | Safely speed limiteed assignment | 16#3C14 = 15380 | 16#207B/51 | 16#AD/01/B5 = 173/01/181 | SMSA | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SMSS | SMS Status | 16#3C18 = 15384 | 16#207B/55 | 16#AD/01/B9 = 173/01/185 | SMSS | Safety function | R | WORD (Enumeration) | - |  |  | [SMS Status] (SMSS) | [MONIT. SAFETY] (SAF)
SNC | Counter wobble synchronization | 16#2FB4 = 12212 | 16#205C/D | 16#9E/01/0D = 158/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Counter wobble] (SNC) | [Traverse control] (TR0)
SPD2 | Output value customer | 16#2EE9 = 12009 | 16#205A/A | 16#9D/01/0A = 157/01/10 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 |  | 0.0 ... 6553.5 | [Cust. output value] (SPD2) | [MONITORING] (MON)
SPD3 | Output value customer | 16#2EEA = 12010 | 16#205A/B | 16#9D/01/0B = 157/01/11 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cust. output value] (SPD3) | [MONITORING] (MON)
SPDT | DRIVECOM : Deceleration - Time delta | 16#21A8 = 8616 | 16#2038/11 | 16#8C/01/11 = 140/01/17 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s
SR11 | Saf1 Reg n-1 | 16#1CE9 = 7401 | 16#202C/2 | 16#86/01/02 = 134/01/02 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-1] (SR11) | [None] (DP1)
SR12 | Saf1 Reg n-2 | 16#1CEA = 7402 | 16#202C/3 | 16#86/01/03 = 134/01/03 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-2] (SR12) | [None] (DP2)
SR13 | Saf1 Reg n-3 | 16#1CEB = 7403 | 16#202C/4 | 16#86/01/04 = 134/01/04 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-3] (SR13) | [None] (DP3)
SR14 | Saf1 Reg n-4 | 16#1CEC = 7404 | 16#202C/5 | 16#86/01/05 = 134/01/05 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-4] (SR14) | [None] (DP4)
SR15 | Saf1 Reg n-5 | 16#1CED = 7405 | 16#202C/6 | 16#86/01/06 = 134/01/06 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-5] (SR15) | [None] (DP5)
SR16 | Saf1 Reg n-6 | 16#1CEE = 7406 | 16#202C/7 | 16#86/01/07 = 134/01/07 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-6] (SR16) | [None] (DP6)
SR17 | Saf1 Reg n-7 | 16#1CEF = 7407 | 16#202C/8 | 16#86/01/08 = 134/01/08 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-7] (SR17) | [None] (DP7)
SR18 | Saf1 Reg n-8 | 16#1CF0 = 7408 | 16#202C/9 | 16#86/01/09 = 134/01/09 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf1 Reg n-8] (SR18) | [None] (DP8)
SR21 | Saf2 Reg n-1 | 16#1CF3 = 7411 | 16#202C/C | 16#86/01/0C = 134/01/12 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-1] (SR21) | [None] (DP1)
SR22 | Saf2 Reg n-2 | 16#1CF4 = 7412 | 16#202C/D | 16#86/01/0D = 134/01/13 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-2] (SR22) | [None] (DP2)
SR23 | Saf2 Reg n-3 | 16#1CF5 = 7413 | 16#202C/E | 16#86/01/0E = 134/01/14 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-3] (SR23) | [None] (DP3)
SR24 | Saf2 Reg n-4 | 16#1CF6 = 7414 | 16#202C/F | 16#86/01/0F = 134/01/15 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-4] (SR24) | [None] (DP4)
SR25 | Saf2 Reg n-5 | 16#1CF7 = 7415 | 16#202C/10 | 16#86/01/10 = 134/01/16 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-5] (SR25) | [None] (DP5)
SR26 | Saf2 Reg n-6 | 16#1CF8 = 7416 | 16#202C/11 | 16#86/01/11 = 134/01/17 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-6] (SR26) | [None] (DP6)
SR27 | Saf2 Reg n-7 | 16#1CF9 = 7417 | 16#202C/12 | 16#86/01/12 = 134/01/18 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-7] (SR27) | [None] (DP7)
SR28 | Saf2 Reg n-8 | 16#1CFA = 7418 | 16#202C/13 | 16#86/01/13 = 134/01/19 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Saf2 Reg n-8] (SR28) | [None] (DP8)
SRA1 | SF00 Reg n-1 | 16#1CFD = 7421 | 16#202C/16 | 16#86/01/16 = 134/01/22 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-1] (SRA1) | [None] (DP1)
SRA2 | SF00 Reg n-2 | 16#1CFE = 7422 | 16#202C/17 | 16#86/01/17 = 134/01/23 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-2] (SRA2) | [None] (DP2)
SRA3 | SF00 Reg n-3 | 16#1CFF = 7423 | 16#202C/18 | 16#86/01/18 = 134/01/24 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-3] (SRA3) | [None] (DP3)
SRA4 | SF00 Reg n-4 | 16#1D00 = 7424 | 16#202C/19 | 16#86/01/19 = 134/01/25 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-4] (SRA4) | [None] (DP4)
SRA5 | SF00 Reg n-5 | 16#1D01 = 7425 | 16#202C/1A | 16#86/01/1A = 134/01/26 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-5] (SRA5) | [None] (DP5)
SRA6 | SF00 Reg n-6 | 16#1D02 = 7426 | 16#202C/1B | 16#86/01/1B = 134/01/27 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-6] (SRA6) | [None] (DP6)
SRA7 | SF00 Reg n-7 | 16#1D03 = 7427 | 16#202C/1C | 16#86/01/1C = 134/01/28 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-7] (SRA7) | [None] (DP7)
SRA8 | SF00 Reg n-8 | 16#1D04 = 7428 | 16#202C/1D | 16#86/01/1D = 134/01/29 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF00 Reg n-8] (SRA8) | [None] (DP8)
SRB1 | SF01 Reg n-1 | 16#1D07 = 7431 | 16#202C/20 | 16#86/01/20 = 134/01/32 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-1] (SRB1) | [None] (DP1)
SRB2 | SF01 Reg n-2 | 16#1D08 = 7432 | 16#202C/21 | 16#86/01/21 = 134/01/33 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-2] (SRB2) | [None] (DP2)
SRB3 | SF01 Reg n-3 | 16#1D09 = 7433 | 16#202C/22 | 16#86/01/22 = 134/01/34 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-3] (SRB3) | [None] (DP3)
SRB4 | SF01 Reg n-4 | 16#1D0A = 7434 | 16#202C/23 | 16#86/01/23 = 134/01/35 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-4] (SRB4) | [None] (DP4)
SRB5 | SF01 Reg n-5 | 16#1D0B = 7435 | 16#202C/24 | 16#86/01/24 = 134/01/36 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-5] (SRB5) | [None] (DP5)
SRB6 | SF01 Reg n-6 | 16#1D0C = 7436 | 16#202C/25 | 16#86/01/25 = 134/01/37 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-6] (SRB6) | [None] (DP6)
SRB7 | SF01 Reg n-7 | 16#1D0D = 7437 | 16#202C/26 | 16#86/01/26 = 134/01/38 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-7] (SRB7) | [None] (DP7)
SRB8 | SF01 Reg n-8 | 16#1D0E = 7438 | 16#202C/27 | 16#86/01/27 = 134/01/39 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF01 Reg n-8] (SRB8) | [None] (DP8)
SRC1 | SF02 Reg n-1 | 16#1D11 = 7441 | 16#202C/2A | 16#86/01/2A = 134/01/42 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-1] (SRC1) | [None] (DP1)
SRC2 | SF02 Reg n-2 | 16#1D12 = 7442 | 16#202C/2B | 16#86/01/2B = 134/01/43 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-2] (SRC2) | [None] (DP2)
SRC3 | SF02 Reg n-3 | 16#1D13 = 7443 | 16#202C/2C | 16#86/01/2C = 134/01/44 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-3] (SRC3) | [None] (DP3)
SRC4 | SF02 Reg n-4 | 16#1D14 = 7444 | 16#202C/2D | 16#86/01/2D = 134/01/45 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-4] (SRC4) | [None] (DP4)
SRC5 | SF02 Reg n-5 | 16#1D15 = 7445 | 16#202C/2E | 16#86/01/2E = 134/01/46 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-5] (SRC5) | [None] (DP5)
SRC6 | SF02 Reg n-6 | 16#1D16 = 7446 | 16#202C/2F | 16#86/01/2F = 134/01/47 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-6] (SRC6) | [None] (DP6)
SRC7 | SF02 Reg n-7 | 16#1D17 = 7447 | 16#202C/30 | 16#86/01/30 = 134/01/48 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-7] (SRC7) | [None] (DP7)
SRC8 | SF02 Reg n-8 | 16#1D18 = 7448 | 16#202C/31 | 16#86/01/31 = 134/01/49 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF02 Reg n-8] (SRC8) | [None] (DP8)
SRD1 | SF03 Reg n-1 | 16#1D1B = 7451 | 16#202C/34 | 16#86/01/34 = 134/01/52 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-1] (SRD1) | [None] (DP1)
SRD2 | SF03 Reg n-2 | 16#1D1C = 7452 | 16#202C/35 | 16#86/01/35 = 134/01/53 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-2] (SRD2) | [None] (DP2)
SRD3 | SF03 Reg n-3 | 16#1D1D = 7453 | 16#202C/36 | 16#86/01/36 = 134/01/54 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-3] (SRD3) | [None] (DP3)
SRD4 | SF03 Reg n-4 | 16#1D1E = 7454 | 16#202C/37 | 16#86/01/37 = 134/01/55 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-4] (SRD4) | [None] (DP4)
SRD5 | SF03 Reg n-5 | 16#1D1F = 7455 | 16#202C/38 | 16#86/01/38 = 134/01/56 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-5] (SRD5) | [None] (DP5)
SRD6 | SF03 Reg n-6 | 16#1D20 = 7456 | 16#202C/39 | 16#86/01/39 = 134/01/57 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-6] (SRD6) | [None] (DP6)
SRD7 | SF03 Reg n-7 | 16#1D21 = 7457 | 16#202C/3A | 16#86/01/3A = 134/01/58 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-7] (SRD7) | [None] (DP7)
SRD8 | SF03 Reg n-8 | 16#1D22 = 7458 | 16#202C/3B | 16#86/01/3B = 134/01/59 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF03 Reg n-8] (SRD8) | [None] (DP8)
SRE1 | SF04 Reg n-1 | 16#1D25 = 7461 | 16#202C/3E | 16#86/01/3E = 134/01/62 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-1] (SRE1) | [None] (DP1)
SRE2 | SF04 Reg n-2 | 16#1D26 = 7462 | 16#202C/3F | 16#86/01/3F = 134/01/63 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-2] (SRE2) | [None] (DP2)
SRE3 | SF04 Reg n-3 | 16#1D27 = 7463 | 16#202C/40 | 16#86/01/40 = 134/01/64 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-3] (SRE3) | [None] (DP3)
SRE4 | SF04 Reg n-4 | 16#1D28 = 7464 | 16#202C/41 | 16#86/01/41 = 134/01/65 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-4] (SRE4) | [None] (DP4)
SRE5 | SF04 Reg n-5 | 16#1D29 = 7465 | 16#202C/42 | 16#86/01/42 = 134/01/66 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-5] (SRE5) | [None] (DP5)
SRE6 | SF04 Reg n-6 | 16#1D2A = 7466 | 16#202C/43 | 16#86/01/43 = 134/01/67 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-6] (SRE6) | [None] (DP6)
SRE7 | SF04 Reg n-7 | 16#1D2B = 7467 | 16#202C/44 | 16#86/01/44 = 134/01/68 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-7] (SRE7) | [None] (DP7)
SRE8 | SF04 Reg n-8 | 16#1D2C = 7468 | 16#202C/45 | 16#86/01/45 = 134/01/69 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF04 Reg n-8] (SRE8) | [None] (DP8)
SRF1 | SF05 Reg n-1 | 16#1D2F = 7471 | 16#202C/48 | 16#86/01/48 = 134/01/72 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-1] (SRF1) | [None] (DP1)
SRF2 | SF05 Reg n-2 | 16#1D30 = 7472 | 16#202C/49 | 16#86/01/49 = 134/01/73 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-2] (SRF2) | [None] (DP2)
SRF3 | SF05 Reg n-3 | 16#1D31 = 7473 | 16#202C/4A | 16#86/01/4A = 134/01/74 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-3] (SRF3) | [None] (DP3)
SRF4 | SF05 Reg n-4 | 16#1D32 = 7474 | 16#202C/4B | 16#86/01/4B = 134/01/75 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-4] (SRF4) | [None] (DP4)
SRF5 | SF05 Reg n-5 | 16#1D33 = 7475 | 16#202C/4C | 16#86/01/4C = 134/01/76 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-5] (SRF5) | [None] (DP5)
SRF6 | SF05 Reg n-6 | 16#1D34 = 7476 | 16#202C/4D | 16#86/01/4D = 134/01/77 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-6] (SRF6) | [None] (DP6)
SRF7 | SF05 Reg n-7 | 16#1D35 = 7477 | 16#202C/4E | 16#86/01/4E = 134/01/78 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-7] (SRF7) | [None] (DP7)
SRF8 | SF05 Reg n-8 | 16#1D36 = 7478 | 16#202C/4F | 16#86/01/4F = 134/01/79 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF05 Reg n-8] (SRF8) | [None] (DP8)
SRG1 | SF06 Reg n-1 | 16#1D39 = 7481 | 16#202C/52 | 16#86/01/52 = 134/01/82 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-1] (SRG1) | [None] (DP1)
SRG2 | SF06 Reg n-2 | 16#1D3A = 7482 | 16#202C/53 | 16#86/01/53 = 134/01/83 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-2] (SRG2) | [None] (DP2)
SRG3 | SF06 Reg n-3 | 16#1D3B = 7483 | 16#202C/54 | 16#86/01/54 = 134/01/84 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-3] (SRG3) | [None] (DP3)
SRG4 | SF06 Reg n-4 | 16#1D3C = 7484 | 16#202C/55 | 16#86/01/55 = 134/01/85 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-4] (SRG4) | [None] (DP4)
SRG5 | SF06 Reg n-5 | 16#1D3D = 7485 | 16#202C/56 | 16#86/01/56 = 134/01/86 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-5] (SRG5) | [None] (DP5)
SRG6 | SF06 Reg n-6 | 16#1D3E = 7486 | 16#202C/57 | 16#86/01/57 = 134/01/87 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-6] (SRG6) | [None] (DP6)
SRG7 | SF06 Reg n-7 | 16#1D3F = 7487 | 16#202C/58 | 16#86/01/58 = 134/01/88 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-7] (SRG7) | [None] (DP7)
SRG8 | SF06 Reg n-8 | 16#1D40 = 7488 | 16#202C/59 | 16#86/01/59 = 134/01/89 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF06 Reg n-8] (SRG8) | [None] (DP8)
SRH1 | SF07 Reg n-1 | 16#1D43 = 7491 | 16#202C/5C | 16#86/01/5C = 134/01/92 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-1] (SRH1) | [None] (DP1)
SRH2 | SF07 Reg n-2 | 16#1D44 = 7492 | 16#202C/5D | 16#86/01/5D = 134/01/93 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-2] (SRH2) | [None] (DP2)
SRH3 | SF07 Reg n-3 | 16#1D45 = 7493 | 16#202C/5E | 16#86/01/5E = 134/01/94 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-3] (SRH3) | [None] (DP3)
SRH4 | SF07 Reg n-4 | 16#1D46 = 7494 | 16#202C/5F | 16#86/01/5F = 134/01/95 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-4] (SRH4) | [None] (DP4)
SRH5 | SF07 Reg n-5 | 16#1D47 = 7495 | 16#202C/60 | 16#86/01/60 = 134/01/96 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-5] (SRH5) | [None] (DP5)
SRH6 | SF07 Reg n-6 | 16#1D48 = 7496 | 16#202C/61 | 16#86/01/61 = 134/01/97 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-6] (SRH6) | [None] (DP6)
SRH7 | SF07 Reg n-7 | 16#1D49 = 7497 | 16#202C/62 | 16#86/01/62 = 134/01/98 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-7] (SRH7) | [None] (DP7)
SRH8 | SF07 Reg n-8 | 16#1D4A = 7498 | 16#202C/63 | 16#86/01/63 = 134/01/99 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF07 Reg n-8] (SRH8) | [None] (DP8)
SRI1 | SF08 Reg n-1 | 16#1D4D = 7501 | 16#202D/2 | 16#86/01/66 = 134/01/102 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-1] (SRI1) | [None] (DP1)
SRI2 | SF08 Reg n-2 | 16#1D4E = 7502 | 16#202D/3 | 16#86/01/67 = 134/01/103 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-2] (SRI2) | [None] (DP2)
SRI3 | SF08 Reg n-3 | 16#1D4F = 7503 | 16#202D/4 | 16#86/01/68 = 134/01/104 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-3] (SRI3) | [None] (DP3)
SRI4 | SF08 Reg n-4 | 16#1D50 = 7504 | 16#202D/5 | 16#86/01/69 = 134/01/105 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-4] (SRI4) | [None] (DP4)
SRI5 | SF08 Reg n-5 | 16#1D51 = 7505 | 16#202D/6 | 16#86/01/6A = 134/01/106 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-5] (SRI5) | [None] (DP5)
SRI6 | SF08 Reg n-6 | 16#1D52 = 7506 | 16#202D/7 | 16#86/01/6B = 134/01/107 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-6] (SRI6) | [None] (DP6)
SRI7 | SF08 Reg n-7 | 16#1D53 = 7507 | 16#202D/8 | 16#86/01/6C = 134/01/108 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-7] (SRI7) | [None] (DP7)
SRI8 | SF08 Reg n-8 | 16#1D54 = 7508 | 16#202D/9 | 16#86/01/6D = 134/01/109 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF08 Reg n-8] (SRI8) | [None] (DP8)
SRJ1 | SF09 Reg n-1 | 16#1D57 = 7511 | 16#202D/C | 16#86/01/70 = 134/01/112 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-1] (SRJ1) | [None] (DP1)
SRJ2 | SF09 Reg n-2 | 16#1D58 = 7512 | 16#202D/D | 16#86/01/71 = 134/01/113 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-2] (SRJ2) | [None] (DP2)
SRJ3 | SF09 Reg n-3 | 16#1D59 = 7513 | 16#202D/E | 16#86/01/72 = 134/01/114 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-3] (SRJ3) | [None] (DP3)
SRJ4 | SF09 Reg n-4 | 16#1D5A = 7514 | 16#202D/F | 16#86/01/73 = 134/01/115 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-4] (SRJ4) | [None] (DP4)
SRJ5 | SF09 Reg n-5 | 16#1D5B = 7515 | 16#202D/10 | 16#86/01/74 = 134/01/116 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-5] (SRJ5) | [None] (DP5)
SRJ6 | SF09 Reg n-6 | 16#1D5C = 7516 | 16#202D/11 | 16#86/01/75 = 134/01/117 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-6] (SRJ6) | [None] (DP6)
SRJ7 | SF09 Reg n-7 | 16#1D5D = 7517 | 16#202D/12 | 16#86/01/76 = 134/01/118 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-7] (SRJ7) | [None] (DP7)
SRJ8 | SF09 Reg n-8 | 16#1D5E = 7518 | 16#202D/13 | 16#86/01/77 = 134/01/119 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF09 Reg n-8] (SRJ8) | [None] (DP8)
SRK1 | SF10 Reg n-1 | 16#1D61 = 7521 | 16#202D/16 | 16#86/01/7A = 134/01/122 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-1] (SRK1) | [None] (DP1)
SRK2 | SF10 Reg n-2 | 16#1D62 = 7522 | 16#202D/17 | 16#86/01/7B = 134/01/123 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-2] (SRK2) | [None] (DP2)
SRK3 | SF10 Reg n-3 | 16#1D63 = 7523 | 16#202D/18 | 16#86/01/7C = 134/01/124 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-3] (SRK3) | [None] (DP3)
SRK4 | SF10 Reg n-4 | 16#1D64 = 7524 | 16#202D/19 | 16#86/01/7D = 134/01/125 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-4] (SRK4) | [None] (DP4)
SRK5 | SF10 Reg n-5 | 16#1D65 = 7525 | 16#202D/1A | 16#86/01/7E = 134/01/126 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-5] (SRK5) | [None] (DP5)
SRK6 | SF10 Reg n-6 | 16#1D66 = 7526 | 16#202D/1B | 16#86/01/7F = 134/01/127 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-6] (SRK6) | [None] (DP6)
SRK7 | SF10 Reg n-7 | 16#1D67 = 7527 | 16#202D/1C | 16#86/01/80 = 134/01/128 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-7] (SRK7) | [None] (DP7)
SRK8 | SF10 Reg n-8 | 16#1D68 = 7528 | 16#202D/1D | 16#86/01/81 = 134/01/129 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF10 Reg n-8] (SRK8) | [None] (DP8)
SRL1 | SF11 Reg n-1 | 16#1D6B = 7531 | 16#202D/20 | 16#86/01/84 = 134/01/132 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-1] (SRL1) | [None] (DP1)
SRL2 | SF11 Reg n-2 | 16#1D6C = 7532 | 16#202D/21 | 16#86/01/85 = 134/01/133 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-2] (SRL2) | [None] (DP2)
SRL3 | SF11 Reg n-3 | 16#1D6D = 7533 | 16#202D/22 | 16#86/01/86 = 134/01/134 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-3] (SRL3) | [None] (DP3)
SRL4 | SF11 Reg n-4 | 16#1D6E = 7534 | 16#202D/23 | 16#86/01/87 = 134/01/135 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-4] (SRL4) | [None] (DP4)
SRL5 | SF11 Reg n-5 | 16#1D6F = 7535 | 16#202D/24 | 16#86/01/88 = 134/01/136 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-5] (SRL5) | [None] (DP5)
SRL6 | SF11 Reg n-6 | 16#1D70 = 7536 | 16#202D/25 | 16#86/01/89 = 134/01/137 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-6] (SRL6) | [None] (DP6)
SRL7 | SF11 Reg n-7 | 16#1D71 = 7537 | 16#202D/26 | 16#86/01/8A = 134/01/138 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-7] (SRL7) | [None] (DP7)
SRL8 | SF11 Reg n-8 | 16#1D72 = 7538 | 16#202D/27 | 16#86/01/8B = 134/01/139 |  | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [SF11 Reg n-8] (SRL8) | [None] (DP8)
SS1A | Safe Stop 1 Assigment | 16#3BCE = 15310 | 16#207B/B | 16#AD/01/6F = 173/01/111 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
SS1S | Safe stop 1 status | 16#3BD3 = 15315 | 16#207B/10 | 16#AD/01/74 = 173/01/116 | SS1S | Safety function | R | WORD (Enumeration) | - |  |  | [SS1 status] (SS1S) | [MONIT. SAFETY] (SAF)
SSRT | SS1 ramp value | 16#3BCF = 15311 | 16#207B/C | 16#AD/01/70 = 173/01/112 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 | 0.1 | 0.1 ... 599.0
SSRU | SS1 ramp unit | 16#3BD0 = 15312 | 16#207B/D | 16#AD/01/71 = 173/01/113 | SSRU | Safety function | R/WS | WORD (Enumeration) | - | [None] 1H
SSSL | SS1&SLS Standstill level | 16#3BD1 = 15313 | 16#207B/E | 16#AD/01/72 = 173/01/114 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
SSTT | SS1 Trip threshold | 16#3BD2 = 15314 | 16#207B/F | 16#AD/01/73 = 173/01/115 |  | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz
STFR | Stator frequency | 16#0CD1 = 3281 | 16#2002/52 | 16#71/01/52 = 113/01/82 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Stator frequency] (STFR) | [MONITORING] (MON)
STOA | STO assignment | 16#3BD8 = 15320 | 16#207B/15 | 16#AD/01/79 = 173/01/121 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | [None] NO
TAC | IGBT warning counter | 16#0CA3 = 3235 | 16#2002/24 | 16#71/01/24 = 113/01/36 |  | Measurement parameters | R | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s | [IGBT Warning Counter] (TAC) | [Diagnostics] (DGT)
TAC2 | Min IGBT frequency time | 16#0CAA = 3242 | 16#2002/2B | 16#71/01/2B = 113/01/43 |  | Measurement parameters | R | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s | [Min. freq time] (TAC2) | [Diagnostics] (DGT)
TANF | Detection time of ANF detected fault | 16#1609 = 5641 | 16#201A/2A | 16#7D/01/2A = 125/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 10.00 s | [ANF Time Thd.] (TANF) | [Encoder configuration] (IEN) [Encoder monitoring] (SDD)
TBO | Time to make a reel | 16#2FB0 = 12208 | 16#205C/9 | 16#9E/01/09 = 158/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 9999 min | [Reel time] (TBO) | [Traverse control] (TR0)
TDN | Traverse ctrl decel time | 16#2FAF = 12207 | 16#205C/8 | 16#9E/01/08 = 158/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 4.0 s | 0.1 s ... 999.9 s | [Traverse ctrl. decel] (TDN) | [Traverse control] (TR0)
TRC | Yarn control input | 16#2FA9 = 12201 | 16#205C/2 | 16#9E/01/02 = 158/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Yarn control] (TRC) | [Traverse control] (TR0)
TRH | Traverse frequency high | 16#2FAA = 12202 | 16#205C/3 | 16#9E/01/03 = 158/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 4.0 Hz | 0.0 Hz ... 10.0 Hz | [Traverse freq. high] (TRH) | [Settings] (SET) [Traverse control] (TR0)
TRL | Traverse frequency low | 16#2FAB = 12203 | 16#205C/4 | 16#9E/01/04 = 158/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 4.0 Hz | 0.0 Hz ... 10.0 Hz | [Traverse freq. Low] (TRL) | [Settings] (SET) [Traverse control] (TR0)
TSY | Sync. wobble output | 16#2FB6 = 12214 | 16#205C/F | 16#9E/01/0F = 158/01/15 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Sync. wobble] (TSY) | [Traverse control] (TR0)
TUP | Traverse control acceleration | 16#2FAE = 12206 | 16#205C/7 | 16#9E/01/07 = 158/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 4.0 s | 0.1 s ... 999.9 s | [TraverseCtrl Acc] (TUP) | [Traverse control] (TR0)
IPC1 | Ethernet : IP Card | 16#FAD4 = 64212 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPC2 | Ethernet : IP Card | 16#FAD5 = 64213 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPC3 | Ethernet : IP Card | 16#FAD6 = 64214 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPC4 | Ethernet : IP Card | 16#FAD7 = 64215 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM1 | Ethernet : Subnetwork Mask | 16#FAD8 = 64216 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM2 | Ethernet : Subnetwork Mask | 16#FAD9 = 64217 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM3 | Ethernet : Subnetwork Mask | 16#FADA = 64218 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPM4 | Ethernet : Subnetwork Mask | 16#FADB = 64219 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG1 | Ethernet : Gateway address | 16#FADC = 64220 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG2 | Ethernet : Gateway address | 16#FADD = 64221 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG3 | Ethernet : Gateway address | 16#FADE = 64222 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPG4 | Ethernet : Gateway address | 16#FADF = 64223 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA1 | Ethernet IP: Current IP Card | 16#FAFC = 64252 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA2 | Ethernet IP: Current IP Card | 16#FAFD = 64253 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA3 | Ethernet IP: Current IP Card | 16#FAFE = 64254 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPA4 | Ethernet IP: Current IP Card | 16#FAFF = 64255 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS1 | Ethernet IP: Current IP Mask | 16#FB00 = 64256 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS2 | Ethernet IP: Current IP Mask | 16#FB01 = 64257 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS3 | Ethernet IP: Current IP Mask | 16#FB02 = 64258 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPS4 | Ethernet IP: Current IP Mask | 16#FB03 = 64259 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT1 | Ethernet IP: Current IP Gateway | 16#FB04 = 64260 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT2 | Ethernet IP: Current IP Gateway | 16#FB05 = 64261 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT3 | Ethernet IP: Current IP Gateway | 16#FB06 = 64262 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
IPT4 | Ethernet IP: Current IP Gateway | 16#FB07 = 64263 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 255
UNT | APH, PTH, RTH, RTHI and VOL units | 16#0CA2 = 3234 | 16#2002/23 | 16#71/01/23 = 113/01/35 |  | Configuration and settings | R | WORD (BitString16) | -
NTID | Fieldbus identifier selection | 16#1A26 = 6694 | 16#2024/5F | 16#82/01/5F = 130/01/95 | NTID | Configuration and settings | R/WS | WORD (Enumeration) | - | [ATV320 identifier] ATV320 |  | [Fieldbus Identifier Sel] (NTID) | [Communication] (COM)
JAMS | Anti-Jam status | 16#3E3F = 15935 | 16#2081/24 | 16#B0/01/88 = 176/01/136 | JAMS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Anti-Jam Status] (JAMS) | [MONITORING] (MON) [Anti-Jam] (AJM) [Anti-Jam] (AJM)
LPA | Liquid probe assignment | 16#A0F0 = 41200 |  |  | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Liquid Probe Assign] (LPA) | [Tank Liquid Probe] (LPM) [Tank Liquid Probe] (LPM)
LPT | Liquid detection threshold | 16#A0F1 = 41201 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 25 % | 0 % ... 100 % | [Liquid Threshold] (LPT) | [Tank Liquid Probe] (LPM) [Tank Liquid Probe] (LPM)
LPTF | Tank full delay | 16#A0F2 = 41202 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 1 min | 0 min ... 60 min | [Tank Full Delay] (LPTF) | [Tank Liquid Probe] (LPM) [Tank Liquid Probe] (LPM)
LPTE | Tank empty delay | 16#A0F3 = 41203 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 10 min | 0 min ... 60 min | [Tank Empty Delay] (LPTE) | [Tank Liquid Probe] (LPM) [Tank Liquid Probe] (LPM)
LPTP | Tank probe presence threshold | 16#A0F4 = 41204 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Probe Threshold] (LPTP) | [Tank Liquid Probe] (LPM) [Tank Liquid Probe] (LPM)
LDCA | Low voltage assignment | 16#A105 = 41221 |  |  | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Low Voltage Assign] (LDCA) | [Sun] (SUN)
PVSA | PV supply assignment | 16#A104 = 41220 |  |  | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PV Supply Assign] (PVSA) | [Sun] (SUN)
LITR | Low light duration | 16#A0FA = 41210 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | Refer to programming manual | 0 s ... 3600 s | [Low Light Duration] (LITR) | [Sun] (SUN)

## Enumerations
List ID | Value | Display | Description
ACT | 0 | [Not Done] (TAB) | Not done
| 1 | [Pending] (PEND) | Test is pending
| 2 | [In Progress] (PROG) | Test in progress
| 3 | [Error] (FAIL) | Error detected
| 4 | [Autotuning Done] (DONE) | Autotuning Done
ACTION | 0 | [No Action] (NO) | No action
| 1 | [Apply Autotuning] (YES) | Apply autotuning
| 2 | [Erase Autotuning] (CLR) | Erase autotuning
ADC | 0 | [No] (NO) | No DC injection
| 1 | [Yes] (YES) | DC injection
| 2 | [Continuous] (CT) | Continuous DC injection
AIOL | 0 | [0 - 100%] (POS) | Positive only
| 1 | [+/- 100%] (POSNEG) | Positive and negative
AIOT | 1 | [Voltage] (10U) | Voltage
| 2 | [Current] (0A) | Current
| 5 | [Voltage +/-] (N10U) | AI bipolar volts selected
AST | 3 | [IPM align.] (IPMA) | IPM alignment
| 4 | [SPM align.] (SPMA) | SPM alignment
| 5 | [PSI align.] (PSI) | Pulse Signal injection
| 6 | [PSIO align.] (PSIO) | Pulse Signal injection - Optimized
| 254 | [No align.] (NO) | NO alignment
AUT | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [One] (ONE) | At first run order
BDCO | 38 | [50 kbps] (50K) | Baud rate 50kbps
| 52 | [125 kbps] (125K) | Baud rate 125kbps
| 60 | [250 kbps] (250K) | Baud rate 250kbps
| 68 | [500 kbps] (500K) | Baud rate 500kbps
| 76 | [1 Mbps] (1M) | Baud rate 1Mbps
BFR | 0 | [50 Hz] (50Hz) | 50Hz motor frequency
| 1 | [60 Hz] (60Hz) | 60Hz motor frequency
BIP | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Brake impulse Fwd
| 2 | [2 IBR] (2IBR) | Brake impulse Fwd/Rev
BLC | 0 | [No] (NO) | No
| 2 | [R2] (R2) | Relay R2
| 17 | [LO1] (LO1) | Logic output 1
| 64 | [DQ1 Digital Output] (DO1) | DQ1 digital output
BMP | 0 | [Stop On Switching] (STOP) | Stop on switching
| 1 | [Bumpless] (BUMP) | Bumpless
BOA | 0 | [Inactive] (NO) | Inactive
| 1 | [Dynamic] (DYNA) | Dynamic
| 2 | [Static] (STAT) | Static
BRA | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [High Torque] (DYNA) | High torque
BSP | 0 | [Standard] (BSD) | Standard ref template
| 1 | [Pedestal] (BLS) | Pedestal at LSP
| 2 | [Deadband] (BNS) | Deadband at LSP
| 4 | [Deadband at 0%] (BNS0) | Deadband at 0 speed
BST | 0 | [Traveling] (HOR) | Cross traverse motion
| 1 | [Hoisting] (VER) | Hoisting motion
CDX | 1 | [Terminals] (TER) | Terminal block
| 2 | [Local] (LOC) | Local control
| 3 | [HMI] (LCC) | Local HMI
| 10 | [Modbus] (MDB) | Modbus communication
| 20 | [CANopen] (CAN) | CANopen communication
| 30 | [Com. Module] (NET) | Ext. communication module
CFG | 0 | [Start/Stop] (STS) | Standard Start/Stop
| 1 | [M. handling] (HDG) | Material handling
| 2 | [Hoisting] (HST) | Hoisting
| 3 | [Gen. Use] (GEN) | General use
| 4 | [PID regul.] (PID) | PID regulation
| 5 | [Network C.] (NET) | Network communications
| 8 | [Solar Application] (SUN) | Solar application
CFPS | 0 | [None] (NO) | Not Assigned
| 1 | [Set No.1] (CFP1) | Parameter set 1
| 2 | [Set No.2] (CFP2) | Parameter set 2
| 3 | [Set No.3] (CFP3) | Parameter set 3
CHCF | 1 | [Not separ.] (SIM) | Combined channel mode
| 2 | [Separate] (SEP) | Separated channel mode
| 3 | [I/O profile] (IO) | I/O mode
CIOA | 0 | [20/70] (20) | 20/70
| 1 | [21/71] (21) | 21/71
| 2 | [100/101] (100) | 100/101
| 3 | [Unconfig.] (UNCG) | Unconfigured
CNFS | 0 | [In progress] (NO) | In progress
| 1 | [Config. No.0] (CNF0) | Configuration 0 active
| 2 | [Config. No.1] (CNF1) | Configuration 1 active
| 3 | [Config. No.2] (CNF2) | Configuration 2 active
CNL | 0 | [Terminals] (TER) | Terminal block
| 1 | [Local] (LOC) | Local
| 2 | [HMI] (LCC) | Local HMI
| 3 | [Modbus] (MDB) | Modbus communication 1
| 6 | [CANopen] (CAN) | CANopen communication
| 7 | [+/- speed] (TUD) | Increase/Decrease speed
| 8 | [LUD->NotDef] (LUD) | LUD->NotDef
| 9 | [Com. Module] (NET) | Ext. communication module
| 14 | [Mfg] (IND) | Indus
| 15 | [PC tool] (PWS) | PC tool
COP | 0 | [No] (NO) | No copy
| 1 | [Reference Frequency] (SP) | Copy reference frequency
| 2 | [Command] (CD) | Copy command
| 3 | [Cmd + Ref Frequency] (ALL) | Copy command & reference frequency
CSLFN | 0 | [No] (NO) | No
| 180 | [Jog] (FNJOG) | Jog
| 181 | [Preset Speed 1] (FNPS1) | Preset speed 1
| 182 | [Preset Speed 2] (FNPS2) | Preset speed 2
| 183 | [PID Ref Freq 1] (FNPR1) | PID reference frequency 1
| 184 | [PID Ref Freq 2] (FNPR2) | PID reference frequency 2
| 185 | [+speed] (FNUSP) | Increase speed
| 186 | [-speed] (FNDSP) | Decrease speed
| 187 | [T/K] (FNTK) | Terminal keypad
| 172 | [Forward / Reverse] (FNFR) | Forward / Reverse
CSLOUT | 0 | [No] (NO) | No
| 146 | [R2] (R2) | Relay R2
| 129 | [LO1] (LO1) | Logical output LO1
| 161 | [DQ1] (DO1) | Digital ouptut DQ1
CTT | 0 | [SVC V] (VVC) | Sensorless flux vector V
| 3 | [U/F VC Standard] (STD) | U/F VC Standard motor law
| 4 | [U/F VC 5pts] (UF5) | U/F VC 5 point voltage/frequency
| 5 | [Sync. mot.] (SYN) | Synchronous motor
| 6 | [U/F VC Quad.] (UFQ) | U/F VC Quadratic
| 7 | [Energy Sav.] (NLD) | Energy Saving
DANF | 0 | [Over] (OVER) | Trip in case of overspeed
| 1 | [Both] (BOTH) | Trip in case of overspeed or underspeed
DCCC | 0 | [Altivar] (ATV) | Altivar compatibility
| 1 | [Lexium] (LHM) | Lexium compatibility
DCCM | 0 | [No] (NO) | No
| 1 | [Bus & Mains] (MAIN) | Bus and Mains
| 2 | [Only Bus] (BUS) | Only Bus
DOTD | 0 | [Freewheel Stop] (NST) | Drive freewheel stop
| 1 | [Ramp Stop] (RMP) | Ramp stop
DPMA | 1 | [Master 1] (1) | Master 1
| 2 | [Master 2] (2) | Master 2
DSF | 0 | [Standard] (STD) | Standard
| 1 | [Optimized] (OPT) | Optimized
DUR | 0 | [5 minutes] (5) | 5 minutes
| 1 | [10 minutes] (10) | 10 minutes
| 2 | [30 minutes] (30) | 30 minutes
| 3 | [1 hour] (1H) | 1 hour
| 4 | [2 hours] (2H) | 2 hours
| 5 | [3 hours] (3H) | 3 hours
| 6 | [Unlimited] (CT) | Unlimited
EBHT | 0 | [No] (NO) | Not configured
| 1 | [RS422 5V] (RS05) | RS422 5V
| 2 | [Push Pull 24V] (PP24) | Push Pull 24V
| 3 | [Open collector 15V] (OC15) | Open collector 15V
| 4 | [Open collector 12V] (OC12) | Open collector 12V
| 5 | [RS422 15V] (RS15) | RS422 15V
| 6 | [Push Pull 15V] (PP15) | Push Pull 15V
| 7 | [Push Pull 12V] (PP12) | Push Pull 12V
ECFG | 0 | [Ignore] (NO) | Ignore
| 1 | [Freewheel Stop] (YES) | Freewheel stop
| 2 | [Per STT] (STT) | Per STT
| 4 | [Fallback Speed] (LFF) | Fallback speed
| 5 | [Speed maintained] (RLS) | Speed maintained
| 6 | [Ramp stop] (RMP) | Ramp stop
| 7 | [Fast stop] (FST) | Fast stop
| 8 | [DC injection] (DCI) | DC injection
ENS | 1 | [AABB] (AABB) | For signals A/A-/B/B-
| 2 | [AB] (AB) | For signals A/B
ENU | 0 | [No] (NO) | Inactive
| 1 | [Speed Monitoring] (SEC) | Speed feedback monitoring
ERRD | 16#0000 | [No Error] (NOF) | No error detected
| 16#1000 | [Precharge Capacitor] (CRF1) | Precharge capacitor
| 16#1000 | [Motor Overload] (OLF) | Motor overload
| 16#1000 | [Motor Overspeed] (SOF) | Motor overspeed
| 16#1000 | [IGBT desaturation] (HDF) | IGBT desaturation
| 16#1000 | [Internal Error 14] (INFE) | Internal error 14 (CPU)
| 16#1000 | [Channel Switch Error] (CSF) | Channel switching detected error
| 16#1000 | [Angle error] (ASF) | Angle error
| 16#2230 | [IGBT Short Circuit] (SCF4) | IGBT short circuit
| 16#2310 | [Overcurrent] (OCF) | Overcurrent
| 16#2311 | [Process Overload] (OLC) | Process overload
| 16#2320 | [Motor short circuit] (SCF1) | Motor short circuit
| 16#2320 | [Motor Short Circuit] (SCF5) | Motor short circuit
| 16#2330 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 16#3110 | [Supply Mains Overvoltage] (OSF) | Supply mains overvoltage
| 16#3120 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 16#3130 | [Input Phase Loss] (PHF) | Input phase loss
| 16#3310 | [DC Bus Overvoltage] (OBF) | DC bus overvoltage
| 16#3310 | [Single output phase loss] (OPF1) | Single output phase loss
| 16#3310 | [Output Phase Loss] (OPF2) | Output phase loss
| 16#4210 | [Device Overheating] (OHF) | Device overheating
| 16#4210 | [IGBT Overheating] (TJF) | IGBT overheating
| 16#4310 | [DI6=PTC Overheat] (OTFL) | DI6=PTC overheat
| 16#5000 | [Out Contact Closed Error] (FCF1) | Output contactor closed error
| 16#5000 | [Out Contact Opened Error] (FCF2) | Output contactor opened error
| 16#5000 | [Input Contactor] (LCF) | input contactor
| 16#5210 | [Internal Error 9] (INF9) | Internal error 9 (Measure)
| 16#5210 | [Internal Error 10] (INFA) | Internal error 10 (Mains)
| 16#5210 | [Internal Error 11] (INFB) | Internal error 11 (Temperature)
| 16#5530 | [Control Memory Error] (EEF1) | Control memory error
| 16#5530 | [Power Memory Error] (EEF2) | Power memory error
| 16#6100 | [Internal Error 1] (INF1) | Internal error 1 (Rating)
| 16#6100 | [Internal Error 2] (INF2) | Internal error 2 (Soft)
| 16#6100 | [Internal Error 3] (INF3) | Internal error 3 (Intern Comm)
| 16#6100 | [Internal Error 4] (INF4) | Internal error 4 (Manufacturing)
| 16#6100 | [Boards Compatibility] (HCF) | Boards compatibility
| 16#6300 | [Incorrect Config] (CFF) | Incorrect configuration
| 16#6300 | [Invalid Configuration] (CFI) | Invalid configuration
| 16#6300 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 16#7000 | [Internal Error 6] (INF6) | Internal error 6 (Option)
| 16#7110 | [Brake Feedback] (BRF) | Brake feedback
| 16#7300 | [Load slipping] (ANF) | Load slipping
| 16#7300 | [DI6=PTC Probe Error] (PTFL) | DI6=PTC probe detected error
| 16#7300 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 16#7300 | [Tank Probe Error] (TSF) | Tank probe error
| 16#7310 | [Encoder Feedback Loss] (SPF) | Encoder feedback loss
| 16#7400 | [Function Block Error] (FBE) | Function Block error
| 16#7400 | [Function Block Stop Error] (FBES) | Function Block stop error
| 16#7510 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 16#7510 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 16#7520 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 16#7520 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 16#7530 | [PC Com Interruption] (SLF2) | PC communication interruption
| 16#8100 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 16#9000 | [External Error] (EPF1) | External detected error
| 16#9000 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 16#FF00 | [Autotuning Error] (TNF) | Autotuning detected error
| 16#FF01 | [Brake Control] (BLF) | Brake control
| 16#FF02 | [Torque Limitation Error] (SSF) | Torque limitation error
| 16#FF03 | [Process Underload] (ULF) | Process underload
| 16#FF03 | [Safety Function Error] (SAFF) | Safety function detected error
| 16#FF80 | [Dynamic Load Error] (DLF) | Dynamic load detected error
ETHM | 0 | [ModbusTCP] (MBTP) | ModbusTCP
| 1 | [EthernetIP] (ETIP) | EthernetIP
ETST | 1 | [Init] (INIT) | Init
| 2 | [PreOp] (PROP) | PreOp
| 3 | [Boot] (BOOT) | Boot
| 4 | [SafeOp] (SFOP) | SafeOp
| 8 | [Op] (OP) | Op
FBFT | 0 | [No] (NO) | No
| 1 | [Internal] (INT) | Internal
| 2 | [Binary file] (BIN) | Binary file
| 3 | [Intern para.] (INP) | Internal parameters
| 4 | [Para. RW] (PAR) | Parameter access on read or write
| 5 | [Calculation] (CAL) | Calculation
| 6 | [AUX TO] (TOAU) | TimeOut AUX task
| 7 | [Synch TO] (TOPP) | TimeOut in synchronous tasks
| 8 | [Bad ADLC] (ADL) | ADLC with bad parameter
| 9 | [Input assig.] (IN) | Inputs assignment
FBST | 0 | [Not Active] (IDLE) | Not active
| 1 | [Check prog.] (CHEC) | Check program
| 2 | [Stop] (STOP) | Stop
| 3 | [Init] (INIT) | Init
| 4 | [Run] (RUN) | Run
| 5 | [Error] (ERR) | Error
FCS | 0 | [No] (NO) | No
| 2 | [Recall customer parameter set 1] (REC1) | Recall customer parameter set 1
| 3 | [Recall customer parameter set 2] (REC2) | Recall customer parameter set 2
| 64 | [Recall default parameter set] (INI) | Recall default parameter set
| 71 | [Recall OEM default parameter set] (INI1) | Recall OEM default parameter set
FEM | 0 | [No] (NO) | Pump characteristics disabled
| 2 | [PQ] (PQ) | Activate power vs flow curve
FFM | 0 | [Standard] (STD) | Standard
| 1 | [Always] (RUN) | Always
| 2 | [Never] (STP) | Never
FLU | 0 | [Not continuous] (FNC) | Not continuous
| 1 | [Continuous] (FCT) | Continuous
| 2 | [No] (FNO) | No
FOR | 0 | [No] (NO) | Not configured
| 1 | [AUTO] (AUTO) | Automatic format
| 2 | [8-O-1] (8O1) | 8bit odd parity 1stop bit
| 3 | [8-E-1] (8E1) | 8 bits even parity 1 stop bit
| 4 | [8-N-1] (8N1) | 8bit no parity 1stop bit
| 5 | [8-N-2] (8N2) | 8bit no parity 2stop bits
| 6 | [7-O-1] (7O1) | 7bit odd parity 1stop bit
| 7 | [7-E-1] (7E1) | 7 bits even parity 1 stop bit
| 8 | [7-O-2] (7O2) | 7bit odd parity 2stop bits
| 9 | [7-E-2] (7E2) | 7 bits even parity 2 stop bits
GDLS | 0 | [Not Set] (NO) | Not Set
| 1 | [Inactive] (OFF) | Inactive
| 2 | [Short Delay] (STD) | Short delay In Progress
| 3 | [Long Delay] (LGD) | Long delay In Progress
| 4 | [Active] (ON) | Active
| 5 | [Internal Error] (FLT) | Internal error
HMIS | 0 | [Autotuning] (TUN) | Drive automatic tuning
| 1 | [In DC inject.] (DCB) | DC injection
| 2 | [Ready] (RDY) | Ready
| 3 | [Freewheel] (NST) | Freewheel stop
| 4 | [Running] (RUN) | Running
| 5 | [Accelerating] (ACC) | Accelerating
| 6 | [Decelerating] (DEC) | Decelerating
| 7 | [Current Limitation] (CLI) | In current limitation
| 8 | [Fast stop] (FST) | Fast stop
| 9 | [Mot. fluxing] (FLU) | Motor fluxing
| 11 | [No Mains Voltage] (NLP) | No mains voltage
| 12 | [Active PWR] (PRA) | Drive in power removal
| 13 | [control.stop] (CTL) | Control stopping
| 14 | [Dec. adapt.] (OBR) | Dec ramp adaptation
| 15 | [Output cut] (SOC) | Output cut
| 17 | [Undervoltage Warning] (USA) | Undervoltage warning
| 18 | [TC Mode Active] (TC) | TC mode active
| 19 | [In autotest] (ST) | In autotest
| 20 | [Autotest error] (FA) | Autotest error
| 21 | [Autotest OK] (OK) | Autotest OK
| 22 | [EEprom test] (EP) | EEprom test
| 23 | [Operating State "Fault"] (FLT) | Operating state "Fault"
| 25 | [DCP Flashing Mode] (DCP) | DCP Flashing mode
| 28 | [SS1 Active] (SS1) | SS1 active
| 29 | [SLS Active] (SLS) | SLS active
| 30 | [STO active] (STO) | STO active
| 31 | [SMS Active] (SMS) | SMS active
| 32 | [GDL Active] (GDL) | GDL active
| 33 | [Tank Full] (TF) | Tank full
| 34 | [Low Light] (LL) | Low light
| 75 | [Global MPPT] (GPPT) | Global MPPT
HSO | 0 | [No] (NO) | Inactive
| 1 | [Reference Frequency] (SSO) | Reference frequency
| 2 | [Current Limit] (CSO) | Current limit
INCPER | 0 | [0.01%] (001) | 0.01%
| 1 | [0.1%] (01) | 0.1%
| 2 | [1%] (1) | 1%
INR | 0 | [0.01] (001) | hundredths of seconds
| 1 | [0.1] (01) | Tenths of seconds
| 2 | [1] (1) | seconds
IPAE | 0 | [Idle State] (IDLE) | Idle State
| 1 | [Init] (INIT) | Init
| 2 | [Configuration] (CONF) | Configuration
| 3 | [Ready] (RDY) | Ready
| 4 | [Operational] (OPE) | Operational
| 5 | [Not Configured] (UCFG) | Not Configured
| 6 | [Unrecoverable Error] (UREC) | Unrecoverable error
IPM | 0 | [Fixed] (MANU) | Fixed address
| 1 | [BOOTP] (BOOTP) | BOOTP
| 2 | [DHCP] (DHCP) | DHCP
| 3 | [DCP] (DCP) | DCP
JAMS | 0 | [Not Configured] (NONE) | Not configured
| 1 | [Inactive] (NACT) | Inactive
| 2 | [Pending] (PEND) | Pending
| 3 | [Running] (RUN) | Running
LFT | 0 | [No Error] (NOF) | No error detected
| 2 | [Control Memory Error] (EEF1) | Control memory error
| 3 | [Incorrect Config] (CFF) | Incorrect configuration
| 4 | [Invalid Configuration] (CFI) | Invalid configuration
| 5 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 6 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 7 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 8 | [External Error] (EPF1) | External detected error
| 9 | [Overcurrent] (OCF) | Overcurrent
| 10 | [Precharge Capacitor] (CRF1) | Precharge capacitor
| 11 | [Encoder Feedback Loss] (SPF) | Encoder feedback loss
| 12 | [Load slipping] (ANF) | Load slipping
| 16 | [Device Overheating] (OHF) | Device overheating
| 17 | [Motor Overload] (OLF) | Motor overload
| 18 | [DC Bus Overvoltage] (OBF) | DC bus overvoltage
| 19 | [Supply Mains Overvoltage] (OSF) | Supply mains overvoltage
| 20 | [Single output phase loss] (OPF1) | Single output phase loss
| 21 | [Input Phase Loss] (PHF) | Input phase loss
| 22 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 23 | [Motor short circuit] (SCF1) | Motor short circuit
| 24 | [Motor Overspeed] (SOF) | Motor overspeed
| 25 | [Autotuning Error] (TNF) | Autotuning detected error
| 26 | [Internal Error 1] (INF1) | Internal error 1 (Rating)
| 27 | [Internal Error 2] (INF2) | Internal error 2 (Soft)
| 28 | [Internal Error 3] (INF3) | Internal error 3 (Intern Comm)
| 29 | [Internal Error 4] (INF4) | Internal error 4 (Manufacturing)
| 30 | [Power Memory Error] (EEF2) | Power memory error
| 32 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 33 | [Output Phase Loss] (OPF2) | Output phase loss
| 34 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 35 | [Brake Control] (BLF) | Brake control
| 38 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 41 | [Brake Feedback] (BRF) | Brake feedback
| 42 | [PC Com Interruption] (SLF2) | PC communication interruption
| 44 | [Torque Limitation Error] (SSF) | Torque limitation error
| 45 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 49 | [DI6=PTC Probe Error] (PTFL) | DI6=PTC probe detected error
| 50 | [DI6=PTC Overheat] (OTFL) | DI6=PTC overheat
| 51 | [Internal Error 9] (INF9) | Internal error 9 (Measure)
| 52 | [Internal Error 10] (INFA) | Internal error 10 (Mains)
| 53 | [Internal Error 11] (INFB) | Internal error 11 (Temperature)
| 54 | [IGBT Overheating] (TJF) | IGBT overheating
| 55 | [IGBT Short Circuit] (SCF4) | IGBT short circuit
| 56 | [Motor Short Circuit] (SCF5) | Motor short circuit
| 58 | [Out Contact Closed Error] (FCF1) | Output contactor closed error
| 59 | [Out Contact Opened Error] (FCF2) | Output contactor opened error
| 64 | [Input Contactor] (LCF) | input contactor
| 67 | [IGBT desaturation] (HDF) | IGBT desaturation
| 68 | [Internal Error 6] (INF6) | Internal error 6 (Option)
| 69 | [Internal Error 14] (INFE) | Internal error 14 (CPU)
| 71 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 73 | [Boards Compatibility] (HCF) | Boards compatibility
| 76 | [Dynamic Load Error] (DLF) | Dynamic load detected error
| 77 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 99 | [Channel Switch Error] (CSF) | Channel switching detected error
| 100 | [Process Underload] (ULF) | Process underload
| 101 | [Process Overload] (OLC) | Process overload
| 105 | [Angle error] (ASF) | Angle error
| 107 | [Safety Function Error] (SAFF) | Safety function detected error
| 108 | [Function Block Error] (FBE) | Function Block error
| 109 | [Function Block Stop Error] (FBES) | Function Block stop error
| 110 | [Tank Probe Error] (TSF) | Tank probe error
L_H | 0 | [Active low] (LO) | Active low
| 1 | [Active high] (HIG) | Active high
MPC | 0 | [Mot Power] (NPR) | Nominal motor power
| 1 | [Mot Cosinus] (COS) | Nominal motor cosinus Phi
NCV | 0 | [Unknown rating] (NO) | Unknown rating
| 1 | [0.12kW] (U010) | 0.10kW - 0.2HP
| 2 | [0.18kW / 0.25Hp] (U018) | 0.18 kW / 0.25 Hp
| 3 | [0.25kW] (U025) | 0.25kW - 0.37HP
| 4 | [0.37 kW / 0.5 Hp] (U037) | 0.37 kW / 0.5 Hp
| 5 | [0.55 kW /0.75 Hp] (U055) | 0.55 kW / 0.75 Hp
| 6 | [0.75 kW / 1 Hp] (U075) | 0.75 kW / 1 Hp
| 7 | [5.5kW / 7.5HP] (U090) | 5.5kW - 7.5HP
| 8 | [1.1 kW / 1.5 Hp] (U110) | 1.1 kW / 1.5 Hp
| 9 | [1.5 kW / 2 Hp] (U150) | 1.5 kW / 2 Hp
| 10 | [1.85kW] (U185) | 1.85kW - 3HP
| 11 | [2.2 kW / 3 Hp] (U220) | 2.2 kW / 3 Hp
| 12 | [3 kW / 4HP] (U300) | 3 kW / 4HP
| 13 | [4kW / 5HP] (U370) | 3.7kW - 5HP
| 14 | [4kW / 5HP] (U400) | 4kW - 5HP
| 15 | [5.5 kW / 7.5 Hp] (U550) | 5.5 kW / 7.5 Hp
| 16 | [7.5 kW / 10 Hp] (U750) | 7.5 kW / 10 Hp
| 17 | [9kW] (U900) | 9kW - 11HP
| 18 | [11 kW / 15 Hp] (D110) | 11 kW / 15 HP
| 19 | [15 kW / 20 Hp] (D150) | 15 kW / 20 HP
| 20 | [18,5kW / 25HP] (D185) | 18.5kW - 25HP
| 21 | [22kW / 30HP] (D220) | 22kW - 30HP
| 22 | [30kW / 40HP] (D300) | 30kW - 40HP
NPL | 0 | [High Level] (POS) | High level
| 1 | [Low Level] (NEG) | Low level
NTID | 0 | [ATV320] (ATV320) | ATV320 identifier
| 1 | [ATV32] (ATV32) | ATV32 identifier
N_Y | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
ONOFF | 0 | [OFF] (OFF) | OFF
| 1 | [ON] (ON) | ON
OPL | 0 | [Function Inactive] (NO) | Function inactive
| 1 | [OPF Error Triggered] (YES) | OPF error Triggered
| 2 | [No Error Triggered] (OAC) | No error triggered
PRFL | 0 | [Not Configured] (UNCG) | Not configured
| 1 | [1] (1) | 1
| 2 | [None] (2)
| 7 | [None] (7)
| 9 | [None] (9)
| 100 | [100] (100) | 100
| 101 | [101] (101) | 101
| 102 | [102] (102) | 102
PSA | 0 | [Not Configured] (NO) | Not configured
| 1 | [AI1] (AI1) | AI1 Analog input
| 2 | [AI2] (AI2) | AI2 Analog input
| 3 | [AI3] (AI3) | AI3 Analog input
| 129 | [Motor Current] (OCR) | Motor current
| 130 | [Motor Frequency] (OFR) | Motor frequency
| 131 | [Ramp Out.] (ORP) | Ramp output
| 132 | [Motor Torq.] (TRQ) | Motor torque
| 133 | [Sign. Torque] (STQ) | Signed torque
| 134 | [sign Ramp] (ORS) | Signed ramp
| 135 | [PID Ref.] (OPS) | PID reference
| 136 | [PID Feedbk] (OPF) | PID feedback
| 137 | [PID Error] (OPE) | PID error
| 138 | [PID Output] (OPI) | PID output
| 139 | [Mot Mech Power in %] (OPR) | Motor power in %
| 140 | [Mot Thermal] (THR) | Motor thermal state
| 141 | [Drv Thermal] (THD) | Drive thermal state
| 142 | [Torque 4Q] (TQMS) | Master / slave torque
| 144 | [Drive State] (DST) | Drive state
| 160 | [Ref Frequency via DI] (UPDT) | Reference frequency via DI
| 161 | [+/-Spd HMI] (UPDH) | INC/DEC speed via HMI
| 163 | [HMI] (LCC) | Local HMI
| 164 | [Ref. Freq-Modbus] (MDB) | Reference frequency via Modbus
| 167 | [Ref. Freq-CANopen] (CAN) | Reference frequency via CANopen
| 169 | [Ref. Freq-Com. Module] (NET) | Reference frequency via Com module
| 173 | [Sig. O/P Frq.] (OFS) | Signed output frequency
| 174 | [Mot Therm2] (THR2) | Motor thermal 2 state
| 175 | [Mot Therm3] (THR3) | Motor thermal 3 state
| 179 | [Torque Lim.] (TQL) | Torque limit
| 180 | [Motor volt.] (UOP) | Motor voltage
| 181 | [RP] (PI) | Pulse input
| 183 | [AI Virtual 1] (AIV1) | AI Virtual 1
| 184 | [DQ1] (DO1) | Digital output 1
| 185 | [AI Virtual 2] (AIV2) | AI Virtual 2
| 240 | [OA01] (OA01) | OA01
| 241 | [OA02] (OA02) | OA02
| 242 | [OA03] (OA03) | OA03
| 243 | [OA04] (OA04) | OA04
| 244 | [OA05] (OA05) | OA05
| 245 | [OA06] (OA06) | OA06
| 246 | [OA07] (OA07) | OA07
| 247 | [OA08] (OA08) | OA08
| 248 | [OA09] (OA09) | OA09
| 249 | [OA10] (OA10) | OA10
PSL | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Device in operating state "Fault"
| 2 | [Device Running] (RUN) | Device running
| 3 | [Output cont] (OCC) | Ouput contactor control
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 5 | [High Speed Reached] (FLA) | High speed reached
| 6 | [Current Thd Reached] (CTA) | Current threshold reached
| 7 | [Ref Freq Reached] (SRA) | Reference frequency reached
| 8 | [Motor Therm Thd reached] (TSA) | Motor thermal threshold reached
| 9 | [Brake Sequence] (BLC) | Brake sequence
| 10 | [PID error Warning] (PEE) | PID error warning
| 11 | [PID Feedback Warn] (PFA) | PID feedback warning
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 14 | [Dev Thermal reached] (TAD) | Device thermal threshold reached
| 21 | [Process Undld Warn] (ULA) | Process underload warning
| 22 | [Process Overload Warning] (OLA) | Process overload warning
| 27 | [Slack Rope Warning] (RSDA) | Slack rope warning
| 28 | [High Torque Warning] (TTHA) | High torque warning
| 29 | [Low Torque Warning] (TTLA) | Low torque warning
| 30 | [Run Forward] (MFRD) | Run forward
| 31 | [Run Reverse] (MRRS) | Run reverse
| 37 | [Mot2 Therm Thd reached] (TS2) | Motor 2 thermal threshold reached
| 38 | [Mot3 Therm Thd reached] (TS3) | Motor 3 thermal threshold reached
| 47 | [Neg Torque] (ATS) | Negative torque
| 48 | [Cnfg.0 act.] (CNF0) | Configuration 0 active
| 49 | [Cnfg.1 act.] (CNF1) | Configuration 1 active
| 50 | [Cnfg.2 act.] (CNF2) | Configuration 2 active
| 52 | [set 1 active] (CFP1) | Parameter set 1 active
| 53 | [set 2 active] (CFP2) | Parameter set 2 active
| 54 | [set 3 active] (CFP3) | Parameter set 3 active
| 64 | [DC charged] (DBL) | DC bus charged
| 65 | [In braking] (BRS) | In braking sequence
| 66 | [Power Removal State] (PRM) | Power Removal state
| 67 | [Power Switch Disable] (PSDI) | Power switch disable
| 72 | [Pulse Warn Thd Reached] (FQLA) | Pulse warning threshold reached
| 73 | [Mains Contactor] (LLC) | Mains contactor control
| 77 | [I present] (MCP) | I present
| 78 | [Limit Switch Reached] (LSA) | Limit switch reached
| 79 | [Dynamic Load Warning] (DLDA) | Dynamic load warning
| 80 | [Warning Grp 1] (AG1) | Warning group 1
| 81 | [Warning Grp 2] (AG2) | Warning group 2
| 82 | [Warning Grp 3] (AG3) | Warning group 3
| 85 | [DI6=PTC Warning] (PLA) | DI6=PTC warning
| 87 | [External Error Warning] (EFA) | External error warning
| 88 | [Undervoltage Warning] (USA) | Undervoltage warning
| 89 | [Preventive UnderV Active] (UPA) | Preventive undervoltage active
| 91 | [Device Therm Warn] (THA) | Device thermal state warning
| 95 | [Lim T/I Reached] (SSA) | Limit torque / I reached
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 2
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 101 | [Spool end] (EBO) | Spool end
| 102 | [Sync wobble] (TSY) | Sync wobble
| 104 | [Therm Junction Warn] (TJA) | Thermal junction warning
| 107 | [AI3 4-20 Warning] (AP3) | AI3 4-20 Loss warning
| 116 | [Function key 1] (FN1) | Graphic display terminal function key 1
| 117 | [Function key 2] (FN2) | Graphic display terminal function key 2
| 118 | [Function key 3] (FN3) | Graphic display terminal function key 3
| 119 | [Function key 4] (FN4) | Graphic display terminal function key 4
| 127 | [Ready] (RDY) | Ready
| 128 | [Yes] (YES) | Yes
| 129 | [DI1] (LI1) | Digital input 1
| 130 | [DI2] (LI2) | Digital input 2
| 131 | [DI3] (LI3) | Digital input 3
| 132 | [DI4] (LI4) | Digital input 4
| 133 | [DI5] (LI5) | Digital input 5
| 134 | [DI6] (LI6) | Digital input 6
| 143 | [DAI1] (LAI1) | Digital input AI1
| 144 | [DAI2] (LAI2) | Digital input AI2
| 158 | [Time Delay Control] (TDC) | Time delay control
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 176 | [C100] (C100) | Bit 0 Modbus ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 192 | [C200] (C200) | Bit 0 CANopen ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 208 | [C300] (C300) | Bit 0 Com module ctrl word
| 209 | [C301] (C301) | Bit 1 Com module ctrl word
| 210 | [C302] (C302) | Bit 2 Com module ctrl word
| 211 | [C303] (C303) | Bit 3 Com module ctrl word
| 212 | [C304] (C304) | Bit 4 Com module ctrl word
| 213 | [C305] (C305) | Bit 5 Com module ctrl word
| 214 | [C306] (C306) | Bit 6 Com module ctrl word
| 215 | [C307] (C307) | Bit 7 Com module ctrl word
| 216 | [C308] (C308) | Bit 8 Com module ctrl word
| 217 | [C309] (C309) | Bit 9 Com module ctrl word
| 218 | [C310] (C310) | Bit 10 Com module ctrl word
| 219 | [C311] (C311) | Bit 11 Com module ctrl word
| 220 | [C312] (C312) | Bit 12 Com module ctrl word
| 221 | [C313] (C313) | Bit 13 Com module ctrl word
| 222 | [C314] (C314) | Bit 14 Com module ctrl word
| 223 | [C315] (C315) | Bit 15 Com module ctrl word
| 240 | [OL01] (OL01) | OL01
| 241 | [OL02] (OL02) | OL02
| 242 | [OL03] (OL03) | OL03
| 243 | [OL04] (OL04) | OL04
| 244 | [OL05] (OL05) | OL05
| 245 | [OL06] (OL06) | OL06
| 246 | [OL07] (OL07) | OL07
| 247 | [OL08] (OL08) | OL08
| 248 | [OL09] (OL09) | OL09
| 249 | [OL10] (OL10) | OL10
| 250 | [GDL] (GDL) | GDL
PSLIN | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Device in operating state "Fault"
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 2
| 128 | [Yes] (YES) | Yes
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 129 | [DI1] (LI1) | Digital input 1
| 130 | [DI2] (LI2) | Digital input 2
| 131 | [DI3] (LI3) | Digital input 3
| 132 | [DI4] (LI4) | Digital input 4
| 133 | [DI5] (LI5) | Digital input 5
| 134 | [DI6] (LI6) | Digital input 6
| 143 | [DAI1] (LAI1) | Digital input AI1
| 144 | [DAI2] (LAI2) | Digital input AI2
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 209 | [C301] (C301) | Bit 1 Com module ctrl word
| 210 | [C302] (C302) | Bit 2 Com module ctrl word
| 211 | [C303] (C303) | Bit 3 Com module ctrl word
| 212 | [C304] (C304) | Bit 4 Com module ctrl word
| 213 | [C305] (C305) | Bit 5 Com module ctrl word
| 214 | [C306] (C306) | Bit 6 Com module ctrl word
| 215 | [C307] (C307) | Bit 7 Com module ctrl word
| 216 | [C308] (C308) | Bit 8 Com module ctrl word
| 217 | [C309] (C309) | Bit 9 Com module ctrl word
| 218 | [C310] (C310) | Bit 10 Com module ctrl word
| 219 | [C311] (C311) | Bit 11 Com module ctrl word
| 220 | [C312] (C312) | Bit 12 Com module ctrl word
| 221 | [C313] (C313) | Bit 13 Com module ctrl word
| 222 | [C314] (C314) | Bit 14 Com module ctrl word
| 223 | [C315] (C315) | Bit 15 Com module ctrl word
| 240 | [OL01] (OL01) | OL01
| 241 | [OL02] (OL02) | OL02
| 242 | [OL03] (OL03) | OL03
| 243 | [OL04] (OL04) | OL04
| 244 | [OL05] (OL05) | OL05
| 245 | [OL06] (OL06) | OL06
| 246 | [OL07] (OL07) | OL07
| 247 | [OL08] (OL08) | OL08
| 248 | [OL09] (OL09) | OL09
| 249 | [OL10] (OL10) | OL10
PTCX | 0 | [No] (NO) | No management
| 1 | [Always] (AS) | Always
| 2 | [Power ON] (RDS) | Power ON
| 3 | [Motor ON] (RS) | Motor ON
QSTD | 2 | [Fast stop then disable voltage] (FST2) | Fast stop then disable voltage
| 6 | [Fast stop then stay in quick stop state] (FST6) | Fast stop then stay in quick stop state
RDS | 0 | [Auto] (AUTO) | Auto detected
| 1 | [10M. full] (10F) | 10Mbps full duplex
| 2 | [10M. half] (10H) | 10Mbps half duplex
| 3 | [100M. full] (100F) | 100Mbps full duplex
| 4 | [100M. half] (100H) | 100Mbps half duplex
RPR | 0 | [No] (NO) | No
| 1 | [Reset Consumption] (APH) | Reset consumption counters
| 2 | [Reset Run Time] (RTH) | Reset run time
| 3 | [Reset Tot Run Time] (RTHI) | Reset total run time
| 4 | [Reset Power On Time] (PTH) | Reset power ON time
| 5 | [Volume Counters] (VOL) | Volume counters
| 64 | [Reset All (Service)] (ALL) | Reset all counters including service
RPT | 0 | [Linear] (LIN) | Linear ramp
| 1 | [S-Ramp] (S) | S-Ramp
| 2 | [U-Ramp] (U) | U-Ramp
| 3 | [Customized] (CUS) | Ramp customized
RSD | 0 | [No] (NO) | No
| 1 | [Weight Estimation] (DRI) | Weight estimation
| 2 | [Ext Weight Sensor] (PES) | External weight sensor
SCS | 0 | [No] (NO) | No
| 1 | [Config 0] (STR0) | Save configuration 0
| 2 | [Config 1] (STR1) | Save configuration 1
| 3 | [Config 2] (STR2) | Save configuration 2
SFT | 1 | [SFR type 1] (HF1) | Switch.frequency type 1
| 2 | [SFR type 2] (HF2) | Switch.frequency type 2
SFTY | 0 | [Standard] (STD) | Standard drive
| 1 | [Safe] (SAFE) | Safe drive
SLSS | 0 | [Not configured] (NO) | Not configured
| 1 | [Idle] (IDLE) | No activated
| 2 | [Safe ramp] (SS1) | Safe ramp
| 3 | [Spd limited] (SLS) | Speed limited
| 4 | [Safe stop] (STO) | Safe stop
| 5 | [Error] (FLT) | Error
| 6 | [SLS wait] (WAIT) | SLS wait
| 7 | [SLS Start] (STRT) | SLS Start
SLT | 0 | [None] (TYP1)
| 1 | [None] (TYP2)
| 2 | [None] (TYP3)
| 3 | [None] (TYP4)
| 4 | [None] (TYP5)
| 5 | [None] (TYP6)
SMOT | 0 | [No info.] (NO) | No information
| 1 | [Low salient] (LLS) | Low saliency
| 2 | [Med salient] (MLS) | Medium saliency
| 3 | [High salient] (HLS) | High saliency
SMSA | 0 | [None] (NO)
| 1 | [None] (YES)
SMSS | 0 | [Not Set] (NO) | Not Set
| 1 | [Active] (SMS) | Active
| 2 | [Internal Error] (FTI) | Internal error
| 3 | [Max Speed] (FTO) | Maximum speed reached
SOP | 6 | [6 µs] (6) | 6 µs
| 8 | [8 µs] (8) | 8 µs
| 10 | [10 µs] (10) | 10 µs
SPIG | 0 | [Stop] (STOP) | Stop
| 1 | [Ignore] (IGN) | Ignore
SPSL | 0 | [None] (NO)
| 1 | [None] (L34)
| 2 | [None] (L56)
| 3 | [None] (L3PW)
| 4 | [None] (PWRM)
SPST | 0 | [Stop] (STOP) | Stop
| 1 | [Start] (STRT) | Start
SS1S | 0 | [Not configured] (NO) | Not configured
| 1 | [Idle] (IDLE) | No activated
| 2 | [Safe ramp] (SS1) | Safe ramp
| 3 | [Safe stop] (STO) | Safe stop
| 4 | [Error] (FLT) | Error
SSRU | 0 | [None] (1H)
| 1 | [None] (10H)
| 2 | [None] (100H)
STOS | 0 | [Not active] (IDLE) | Not active
| 1 | [Active] (STO) | Active
| 2 | [Error] (FLT) | Error
STP | 0 | [Inactive] (NO) | Inactive
| 1 | [Maintain DC Bus] (MMS) | Maintain DC Bus
| 2 | [Ramp Stop] (RMP) | Ramp Stop
| 4 | [Freewheel Stop] (LNF) | Locked in freewheel stop without error
STR | 0 | [No Save] (NO) | No save
| 1 | [Save to RAM] (RAM) | Save to RAM
| 2 | [Save to EEPROM] (EEP) | Save to EEPROM
STT | 0 | [On Ramp] (RMP) | On ramp
| 1 | [Fast stop] (FST) | Fast stop
| 2 | [Freewheel Stop] (NST) | Freewheel stop
| 3 | [DC injection] (DCI) | DC injection
STUN | 0 | [Default] (TAB) | Default
| 1 | [Measure] (MEAS) | Measure
| 2 | [Custom] (CUS) | Custom
TBR | 0 | [Not config.] (NO) | Not configured
| 4 | [Automatic] (AUTO) | Automatic
| 8 | [300 bps] (300) | 300 bps
| 12 | [600 bps] (600) | 600 bps
| 16 | [1.2 Kbps] (1200) | 1.2 Kbps
| 20 | [2.4 Kbps] (2400) | 2.4 Kbps
| 24 | [4800 bps] (4800) | 4800 bps
| 28 | [9600 bps] (9600) | 9600 bps
| 30 | [10 Kbps] (10000) | 10 Kbps
| 32 | [19200 bps] (19200) | 19200 bps
| 34 | [20 Kbps] (20000) | 20 Kbps
| 35 | [28.8 Kbps] (28800) | 28.8 Kbps
| 36 | [38.4 Kbps] (38400) | 38.4 Kbps
| 37 | [45.45 Kbps] (45450) | 45.45 Kbps
| 38 | [50 Kbps] (50000) | 50 Kbps
| 40 | [57.6 Kbps] (57600) | 57.6 Kbps
| 42 | [93.75 Kbps] (93750) | 93.75 Kbps
| 44 | [100 Kbps] (100K) | 100 Kbps
| 48 | [115.2 Kbps] (115K2) | 115.2 Kbps
| 52 | [125 Kbps] (125K) | 125 Kbps
| 53 | [156 Kbps] (156K) | 156 Kbps
| 54 | [187.5 Kbps] (187K5) | 187.5 Kbps
| 56 | [230.4 Kbps] (230K4) | 230.4 Kbps
| 60 | [250 Kbps] (250K) | 250 Kbps
| 64 | [460.8 Kbps] (460K8) | 460.8 Kbps
| 68 | [500 Kbps] (500K) | 500 Kbps
| 69 | [625 Kbps] (625K) | 625 Kbps
| 70 | [800 Kbps] (800K) | 800 Kbps
| 72 | [921.6 Kbps] (921K6) | 921.6 Kbps
| 76 | [1 Mbps] (1M) | 1 Mbps
| 80 | [1.5 Mbps] (1M5) | 1.5 Mbps
| 81 | [2.5 Mbps] (2M5) | 2.5 Mbps
| 82 | [3 Mbps] (3M) | 3 Mbps
| 83 | [6 Mbps] (6M) | 6 Mbps
| 84 | [10 Mbps] (10M) | 10 Mbps
| 86 | [5 Mbps] (5M) | 5 Mbps
| 88 | [12 Mbps] (12M) | 12 Mbps
| 92 | [100 Mbps] (100M) | 100 Mbps
TCC | 0 | [2-Wire Control] (2C) | 2-wire control
| 1 | [3-Wire Control] (3C) | 3-wire control
TCT | 0 | [Level] (LEL) | Level
| 1 | [Transition] (TRN) | Transition
| 2 | [Level With Fwd Priority] (PFO) | Level with forward priority
THT | 0 | [No] (NO) | No thermal monitoring
| 1 | [Self cooled] (ACL) | Self cooled motor
| 2 | [Force-cool] (FCL) | Force cooled motor
TUNU | 0 | [No] (NO) | No
| 1 | [Therm mot] (TM) | Use the motor thermal evolution
| 2 | [Cold tun] (CT) | Use the cold tune values
URES | 20 | [200 Vac] (200) | 200 Vac
| 22 | [220 Vac] (220) | 220 Vac
| 23 | [230 Vac] (230) | 230 Vac
| 24 | [240 Vac] (240) | 240 Vac
| 38 | [380 Vac] (380) | 380 Vac
| 40 | [400 Vac] (400) | 400 Vac
| 44 | [440 Vac] (440) | 440 Vac
| 46 | [460 Vac] (460) | 460 Vac
| 50 | [500Vac] (500) | 500Vac
| 53 | [525 Vac] (525) | 525 Vac
| 60 | [600 Vac] (600) | 600 Vac
| 254 | [Lexium] (LHM) | Lexium compatibility level
USB | 0 | [Error Triggered] (0) | Error triggered
| 1 | [Error Triggered w/o Relay] (1) | Error triggered w/o relay
| 2 | [Warning Triggered] (2) | Warning Triggered
VCAL | 0 | [Unknown Voltage] (NO) | Unkown voltage
| 1 | [100-120(1)] (110M) | 100-120 V single phase
| 2 | [100-120(3)] (110T) | 100-120 V three phase
| 3 | [200-240 V single] (220M) | 200-240 V single
| 4 | [200-240 V Three] (220T) | 200-240 V three phase
| 5 | [380-500(1)] (480M) | 380-500 V single phase
| 6 | [380-500 V Three] (480T) | 380-500 V three phase
| 7 | [500-690(1)] (690M) | 500-690 V single phase
| 8 | [500-690 V Three] (690T) | 500-690 V three phase
| 9 | [600(1)] (600M) | 600 V single phase
| 10 | [600 V Three] (600T) | 600 V three phase

## Registers
CMI |  | Bit 0 | Factory setting command (active at 1).
|  | Bit 1 | Save configuration to EEPROM non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | Bit 2 | Reserved (= 0).
|  | Bit 3 | Reserved (= 0).
|  | Bit 4 | Reserved (= 0).
|  | Bit 5 | Reserved (= 0).
|  | Bit 6 | Reserved (= 0).
|  | Bit 7 | Reserved (= 0).
|  | Bit 8 | Reserved (= 0).
|  | Bit 9 | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
= 0: 0.1 Hz
= 1: Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz.
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | Bit 10 | Reserved (= 0).
|  | Bit 11 | Reserved (= 0).
|  | Bit 12 | Reserved (= 0).
|  | Bit 13 | Reserved (= 0).
|  | Bit 14 | Reserved (= 0).
|  | Bit 15 | Parameter consistency check
= 0: The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr).
= 1: The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
CMD | Possible values in CiA402 profile, separate or not separate mode:
CMP0 |  | Bit 0 | Switch on/Contactor command.
CMP1 |  | Bit 1 | Disable voltage/Authorization to supply AC power.
CMP2 |  | Bit 2 | Quick stop.
CMP3 |  | Bit 3 | Enable operation/Run command.
CMP4 |  | Bit 4 | Reserved (set to 0).
CMP5 |  | Bit 5 | Reserved (set to 0).
CMP6 |  | Bit 6 | Reserved (set to 0).
CMP7 |  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
CMP8 |  | Bit 8 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
|  | Bit 9 | Reserved (set to 0).
|  | Bit 10 | Reserved (set to 0).
|  | Bit 11 to 15 | Can be assigned to commands.
Possible values in the IO profile on state command [2 wire] (2C).
|  | Bit 0 | Forward (on state) command
= 0: No forward command
= 1: Forward command
The assignment of Bit 0 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bit 0 (Cd00) is only active if the channel of this control word is active.
|  | Bit 1 to 15 | Can be assigned to commands.
Possible values in the IO profile on edge command [3 wire] (3C).
|  | Bit 0 | Stop (run authorization).
= 0: Stop
= 1: Run is authorized on a forward or reverse command
|  | Bit 1 | Forward (on 0 to 1 rising edge) command.
The assignment of Bits 0 and 1 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bits 0 (Cd00) and 1 (Cd01) are only active if the channel of this control word is active.
|  | Bit 2 to 15 | can be assigned to commands.
ETA | Possible values in CiA402 profile, separate or not separate mode:
EP0 |  | Bit 0 | = 1: "Ready to switch on", awaiting power section line supply
EP1 |  | Bit 1 | = 1: "Switched on", ready
EP2 |  | Bit 2 | = 1: "Operation enabled", running
EP3 |  | Bit 3 | = 1: Fault detection
EP4 |  | Bit 4 | "Voltage enabled", power part connected to supply mains
EP5 |  |  | = 0: Power part not connected to supply mains
EP6 |  |  | = 1: Power part connected to supply mains
EP7 |  |  | When the drive is powered by the power section only, this bit is always at 1.
EP8 |  | Bit 5 | Bit 5: = 0: Quick stop
ETAD |  | Bit 6 | Bit 6: = 1: "Switched on disabled", power section line supply locked
|  | Bit 7 | Bit 7: Warning
= 0: No warning
= 1: Warning active
|  | Bit 8 | Bit 8: Reserved (= 0)
|  | Bit 9 | Bit 9: Remote: command or reference via fieldbus
= 0: Command or reference given via the graphic display terminal or remote display terminal
= 1: Command or reference via fieldbus
|  | Bit 10 | Bit 10: Target reference reached
= 0: The reference is not reached
= 1: The reference has been reached
When the drive is in speed mode, this is the reference frequency.
|  | Bit 11 | Bit 11: "Internal limit active", reference outside limits
= 0: The reference is within the limits
= 1: The reference is not within the limits
When the drive is in speed mode, the limits are defined by the [Low speed] (LSP) and [High speed] (HSP) parameters.
|  | Bit 12 | Bit 12: Reserved (= 0)
|  | Bit 13 | Bit 13: Reserved (= 0)
|  | Bit 14 | Bit 14: "Stop key", STOP via stop key
= 0: STOP key not active
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15 | Bit 15: "Direction", direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (refer to fieldbus manuals).
ETI |  | Bit 0 | = 1: Access to the EEPROM non-volatile memory in progress
IP0 |  | Bit 1 | = 0: No parameter consistency check
IP1 |  |  | = 1: Parameter consistency check
IP2 |  | Bit 2 | = 0: The drive is not in operating state "Fault" or in operating state "Fault" and the error is active
IP3 |  |  | = 1: The drive is in operating state "Fault" and the error is no longer active (not reset))
IP4 |  | Bit 3 | Bit 3: Reserved (= 0).
IP5 |  | Bit 4 | = 1: The drive is in speed mode
IP6 |  | Bit 5 | = 1: DC injection active
IP7 |  | Bit 6 | = 0: Drive in steady state
IP8 |  |  | = 1: Drive in transient state
|  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
|  | Bit 8 | = 1: DC bus overvoltage
|  | Bit 9 | = 1: Acceleration active
|  | Bit 10 | = 1: Deceleration active
|  | Bit 11 | = 1: Current limit active
|  | Bit 12 | = 1: Fast stop active
|  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: Drive controled by terminal
bit 13 = 1 and bit 14 = 0: Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1: Drive controled by Modbus
bit 13 = 1 and bit 14 = 1: Drive controled by CANopen or the network card
|  | Bit 15 | = 0: Forward operation applied before the ramp
= 1: Reverse operation applied before the ramp
CRC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | = 1 : APP option board
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
CCC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | = 1 : APP option board
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
IL1R |  | Bit 0 | "LI1" logic inputs real image
|  | Bit 1 | "LI2" logic inputs real image
|  | Bit 2 | "LI3" logic inputs real image
|  | Bit 3 | "LI4" logic inputs real image
|  | Bit 4 | "LI5" logic inputs real image
|  | Bit 5 | "LI6" logic inputs real image
|  | Bit 6 | "AI1" as logic input real image
|  | Bit 7 | "AI2" as logic input real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OL1R |  | Bit 0 | "R1" relay real image
|  | Bit 1 | "R2" relay real image
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | "L01" logic outputs real image
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CIC |  | Bit 0 | = 1: Change of rating.
|  | Bit 1 | = 1: The fielbus module has been added.
|  | Bit 2 | = 1: The fielbus module has been removed.
|  | Bit 3 | = 1: Loaded config invalid.
|  | Bit 4 | = 1: The fielbus module has been changed.
|  | Bit 5 | Reserved (=0).
|  | Bit 6 | Reserved (=0).
|  | Bit 7 | Reserved (=0).
|  | Bit 8 | = 1: The IO module has been added.
|  | Bit 9 | = 1: The IO module has been removed.
|  | Bit 10 | = 1: The IO module has been changed.
|  | Bit 11 | = 1: The encoder module has been added.
|  | Bit 12 | = 1: The encoder module has been removed.
|  | Bit 13 | = 1: The encoder module has been changed.
|  | Bit 14 | = 1: The control board has been changed.
If one of these events occurs, the drive will trigger an error [Invalid configiguration] (CFI) and then automatically restore the factory settings.
CRP0 | Bit 0 to Bit 7: Active command channels
CRP1 |  |  | =0 : The terminal board is the active channel.
CRP2 |  |  | =1 : The local keypad is the active channel.
CRP3 |  |  | =2 : The remote keypad is the active channel.
CRP4 |  |  | =3 : Modbus is the active channel.
CRP5 |  |  | =4 : Reserved
CRP6 |  |  | =5 : Reserved
CRP7 |  |  | =6 : CANopen is the active channel.
CRP8 |  |  | =7 : The terminals are the active channel in the +/- speed reference.
=8 : The remote keypad is the active channel (up-down speed)
=9 : The fieldbus module is the active channel.
=10 : Reserved
=11 : Reserved
=12 : Reserved
=13 : Reserved
=14 : Reserved
=15 : SoMove software is the active channel.
Bit 8 to Bit 15: Active reference channels
=0 : The terminals are the active channel via an analog input.
=1 : The local keypad is the active channel.
=2 : The remote keypad is the active channel.
=3 : Modbus is the active channel.
=4 : Reserved
=5 : Reserved
=6 : CANopen is the active channel.
=7 : The terminals are the active channel in the +/- speed reference.
=8 : The remote keypad is the active channel (up-down speed)
=9 : The fieldbus module is the active channel.
=10 : Reserved
=11 : Reserved
=12 : Reserved
=13 : Reserved
=14 : Reserved
=15 : SoMove software is the active channel.
FRY |  | Bit 0 | = 1 : All parameters
|  | Bit 1 | = 1 : Drive configuration
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : Motor parameters
|  | Bit 4 | = 1 : Communication menu
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Display menu
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved (Bit15 = 1 : Communication option parameters)
EWE |  | Bit 0 | = 1 : Enable Web
|  | Bit 1 | = 1 : Enable Email
IL1I |  | Bit 0 | "LI1" logic inputs physical image
|  | Bit 1 | "LI2" logic inputs physical image
|  | Bit 2 | "LI3" logic inputs physical image
|  | Bit 3 | "LI4" logic inputs physical image
|  | Bit 4 | "LI5" logic inputs physical image
|  | Bit 5 | "LI6" logic inputs physical image
|  | Bit 6 | "AI1" as logic inputs physical image
|  | Bit 7 | "AI2" as logic inputs physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
LRS1 |  |  | _(000_NO) Bit0 : Reserved
_(001_FLT) Bit1 = 1 : Drive fault
_(002_RUN) Bit2 = 1 : Drive running
_(003_OCC) Bit3 = 1 : Downstreamcontactor running
_(004_FTA) Bit4 = 1 : Motor frequency threshold (FTD) reached
_(005_FLA) Bit5 = 1 : High Speed (HSP) reached
_(006_CTA) Bit6 = 1 : Motor current threshold (CTD) reached
_(007_SRA) Bit7 = 1 : Frequency reference reached
_(008_TSA) Bit8 = 1 : Motor thermal threshold (TTD) reached
_(009_BLC) Bit9 = 1 : Braking sequence active
_(010_PEE) Bit10 = 1 : PID error
_(011_PFA) Bit11 = 1 : PID feedback alarm
_(012) Bit12 : Reserved
_(013_F2A) Bit13 = 1 : Second frequency threshold (F2D) reached
_(014_TAD) Bit14 = 1 : Drive thermal threshold reached
_(015_TRC) Bit15 = 1 : Traverse control running
LRS2 |  |  | _(016) Bit0 : Reserved
_(017) Bit1 : Reserved
_(018) Bit2 : Reserved
_(019) Bit3 : Reserved
_(020) Bit4 : Reserved
_(021_ULA) Bit5 = 1 : Undeload alarm
_(022_OLA) Bit6 = 1 : Overload alarm
_(023) Bit7 : Reserved
_(024) Bit8 : Reserved
_(025) Bit9 : Reserved
_(026) Bit10 : Reserved
_(027_RSDA) Bit11 : TBD
_(028_TTHA) Bit12 = 1 : High torque threshold
_(029_TTLA) Bit13 = 1 : Low torque threshold
_(030_MFRD) Bit14 = 1 : Run Forward
_(031_MRRS) Bit15 = 1 : Run Reverse
LRS3 |  |  | _(032_RFC) Bit0 = 0 : Reference channel 1, 1 : Reference channel 2
_(033_CCS) Bit1 = 0 : Command channel 1, 1 : Command channel 2
_(034_RP2) Bit2 = 1 : Ramp switching active
_(035_CL2) Bit3 = 1 : Current limitation switching active
_(036) Bit4 : Reserved
_(037_TS2) Bit5 = 1 : Motor 2 thermal threshold (TTD2) reached
_(038_TS3) Bit6 = 1 : Motor 3 thermal threshold (TTD3) reached
_(039) Bit7 : Reserved
_(040_EPR) Bit8 = 1 : External Power Present
_(041_SLM) Bit9 = 1 : Sleeping Mode active
_(042) Bit10 : Reserved
_(043) Bit11 : Reserved
_(044) Bit12 : Reserved
_(045) Bit13 : Reserved
_(046) Bit14 : Reserved
_(047_ATS) Bit15 = 1 : Actual torque sign
LRS4 |  |  | _(048_CNF0) Bit0 = 1 : Configuration 0 active
_(049_CNF1) Bit1 = 1 : Configuration 1 active
_(050_CNF2) Bit2 = 1 : Configuration 2 active
_(051) Bit3 : Reserved
_(052_CFP1) Bit4 = 1 : Parameter set 1 active
_(053_CFP2) Bit5 = 1 : Parameter set 2 active
_(054_CFP3) Bit6 = 1 : Parameter set 3 active
_(055) Bit7 : Reserved
_(056_PWR) Bit8 = 1 : Power removed
_(057_FLU) Bit9 = 1 : Fluxing in progress
_(058_FLX) Bit10 = 1 : Motor fluxed
_(059_IDC) Bit11 = 1 : DC injection running
_(060_CLI) Bit12 = 1 : Current limitation running
_(061_ACC) Bit13 = 1 : Product in acceleration
_(062_DEC) Bit14 = 1 : Product in deceleration
_(063_FST) Bit15 = 1 : Fast stop in progress
LRS5 |  |  | _(064_DBL) Bit0 = 1 : DC bus loaded
_(065_BRS) Bit1 = 1 : Braking activated
_(066_PRM) Bit2 = 1 : Power removed
_(067_AUTO) Bit3 = 1 : Automatic restart attempts in progress
_(068_TUN) Bit4 = 1 : Autotune in progress
_(069_CTL) Bit5 = 1 : Controlled stop in progress
_(070_OBR) Bit6 = 1 : Adapted deceleration in progress
_(071_SOC) Bit7 = 1 : Stand by output cut in progress
_(072_FQLA) Bit8 = 1 : Frequency level reached status
_(073_LLC) Bit9 = 1 : Line contactor activated
_(074_TUD) Bit10 = 1 : Autotune complete
_(075_EEP) Bit11 = 1 : Eeprom writing in progress
_(076_EED) Bit12 = 1 : Eeprom writing complete
_(077_MCP) Bit13 = 1 : Motor current present
_(078_LSA) Bit14 = 1 : Limit switch function activated
_(079_DLDA) Bit15 : TBD
LRS6 |  |  | _(080_AG1) Bit0 = 1 : Alarm Group 1
_(081_AG2) Bit1 = 1 : Alarm Group 2
_(082_AG3) Bit2 = 1 : Alarm Group 3
_(083) Bit3 : Reserved
_(084) Bit4 : Reserved
_(085_PLA) Bit5 = 1 : PTCL Alarm
_(086) Bit6 : Reserved
_(087_EFA) Bit7 = 1 : External fault alarm
_(088_USA) Bit8 = 1 : Undervoltage alarm
_(089_UPA) Bit9 = 1 : Undervoltage prevention Alarm
_(090) Bit10 : Reserved
_(091_THA) Bit11 = 1 : Transistor heating alarm
_(092) Bit12 : Reserved
_(093) Bit13 : Reserved
_(094) Bit14 : Reserved
_(095_SSA) Bit15 = 1 : Torque current limitation alarm
LRS7 |  |  | _(096_FR1) Bit0 = 1 : Reference channel = channel 1 (for RFC)
_(097_FR2) Bit1 = 1 : Reference channel = channel 2 (for RFC)
_(098_CD1) Bit2 = 1 : Command channel = channel 1 (for CCS)
_(099_CD2) Bit3 = 1 : Command channel = channel 2 (for CCS)
_(100_FR1B) Bit4 = 1 : Reference channel = channel 1B (for RFC)
_(101_EBO) Bit5 = 1 : End of bobbin
_(102_TSY) Bit6 = 1 : Traverse control synchronization counter wobble
_(103) Bit7 : Reserved
_(104_TJA) Bit8 = 1 : Thermal junction alarm
_(105) Bit9 : Reserved
_(106) Bit10 : Reserved
_(107_AP3) Bit11 = 1 : AI3 4-20 mA loss alarm
_(108) Bit12 : Reserved
_(109) Bit13 : Reserved
_(110) Bit14 : Reserved
_(111) Bit15 : Reserved
LRS8 |  |  | _(112_SAF) Bit0 = 1 : Stop Switch in Forward(SAF) activated
_(113_SAR) Bit1 = 1 : Stop Switch in Reverse(SAR) activated
_(114_NOFW) Bit2 = 1 : Forward impossible (Stop Switch in Forward(SAF) memorized or activated)
_(115_NORV) Bit3 = 1 : Reverse impossible (Stop Switch in Reverse(SAR) memorized or activated)
_(116_PSDI) Bit4 : Power Switch Disable
_(117 GPPT) Bit5 : Enable/Disable Global Maximum Power Point Tracking
_(118) Bit6 : Reserved
_(119) Bit7 : Reserved
_(120) Bit8 : Reserved
_(121_FLO) Bit9 = 1 : force local mode activated
_(122) Bit10 : Reserved
_(123) Bit11 : Reserved
_(124) Bit12 : Reserved
_(125) Bit13 : Reserved
_(126) Bit14 : Reserved
_(127_RDY) Bit15 = 1 : Product ready to start
S001 |  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | TB100MS : Clock bit : period 100ms, duty cycle 50%
|  | Bit 6 | TB1SEC : Clock bit : period 1s, duty cycle 50%
|  | Bit 7 | TB1MIN : Clock bit : period 1min, duty cycle 50%
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | 1RSTSCANRUN : FB is executing its 1rst cycle since last RUN.
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
S002 |  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | OPTION_OK
|  | Bit 12 | CANOPEN_OK
|  | Bit 13 | MODBUS_OK
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
S006 |  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | USRMWSAVE : Users variable save request (Save configuration)
|  | Bit 15 | Reserved
SAF1 |  |  | APP Safety fault register
|  | Bit 0 | = 1 : CoT : PWRM consistency fault
|  | Bit 1 | = 1 : DSP : Safe parameters fault
|  | Bit 2 | = 1 : ATAP : App auto test fault (details: SF00)
|  | Bit 3 | = 1 : DSFIP : Diagnostic check of safe function activation
|  | Bit 4 | = 1 : LICT : Logical inputs diagnostic fault (details: SF01)
|  | Bit 5 | = 1 : EXTEND: Extended fault (details: SF04)
|  | Bit 6 | = 1 : WDM1 : App watchdog management fault (details: SF02/SF07)
|  | Bit 7 | = 1 : MC : Motor control fault
|  | Bit 8 | = 1 : ISL : Internal Serial Link Core fault
|  | Bit 9 | = 1 : LIA : Logical Input activation fault (details: SF03)
|  | Bit 10 | = 1 : STO : Safe Torque Off fault (details: SF04)
|  | Bit 11 | = 1 : APPINT: App safety interface fault
|  | Bit 12 | = 1 : SS1 : Safe Stop 1 fault (details: SF05)
|  | Bit 13 | = 1 : SLS : Safely Limited Speed fault (details: SF06)
|  | Bit 14 | = 1 : MOTOR : Motor data fault
|  | Bit 15 | = 1 : CISL : Internal Serial Link Data Flow fault (partial details: SF11)
SAF2 |  |  | MC Safety fault register
|  | Bit 0 | = 1 : Consistency Stator Frequency check fault
|  | Bit 1 | = 1 : Stator Frequency Estimation fault
|  | Bit 2 | = 1 : Motor control watchdog management is active (details: SF08)
|  | Bit 3 | = 1 : Motor control hardware watchdog is active
|  | Bit 4 | = 1 : Motor control auto test has detected an error (details: SF09)
|  | Bit 5 | = 1 : Chain testing detected error
|  | Bit 6 | = 1 : Internal serial link core detected error
|  | Bit 7 | = 1 : Direct short-circuit detected error (details: SF10)
|  | Bit 8 | = 1 : PWM driver detected error
|  | Bit 9 | = 1 : GDL internal detected error
|  | Bit 10 | : Reserved
|  | Bit 11 | = 1 : Application interface has detected an error of the safety functions
|  | Bit 12 | : Reserved
|  | Bit 13 | : Reserved
|  | Bit 14 | = 1 : Motor data is corrupted
|  | Bit 15 | = 1 : Internal serial link data flow detected error (partial details: SF11)
SF00 |  |  | Safety App Auto Test fault register
|  | Bit 0 | Reserved
|  | Bit 1 | = 1 : Ram stack overflow
|  | Bit 2 | = 1 : Ram address integrity error
|  | Bit 3 | = 1 : Ram data access error
|  | Bit 4 | = 1 : Flash Checksum Error
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : Consistency check - ram address variables
|  | Bit 7 | = 1 : Consistency check - ram data access variables
|  | Bit 8 | = 1 : Consistency check - DMA channels variables
|  | Bit 9 | = 1 : Fast task overflow
|  | Bit 10 | = 1 : Slow task overflow
|  | Bit 11 | = 1 : App task overflow
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : PWRM line is not activated during initialization phase
|  | Bit 15 | = 1 : Hardware WD is not running after initialization
SF01 |  |  | Safety LI Diagnostic fault register
|  | Bit 0 | = 1 : Management - state machine error
|  | Bit 1 | = 1 : Data required for test management are corrupted
|  | Bit 2 | = 1 : Channel selection error
|  | Bit 3 | = 1 : Testing - state machine error
|  | Bit 4 | = 1 : Test request is corrupted
|  | Bit 5 | = 1 : Pointer to test method is corrupted
|  | Bit 6 | = 1 : Incorrect test action provided
|  | Bit 7 | = 1 : Error in results collecting
|  | Bit 8 | = 1 : LI3 is defective. Cannot activate safe function
|  | Bit 9 | = 1 : LI4 is defective. Cannot activate safe function
|  | Bit 10 | = 1 : LI5 is defective. Cannot activate safe function
|  | Bit 11 | = 1 : LI6 is defective. Cannot activate safe function
|  | Bit 12 | = 1 : Test sequence updated while a diagnostic is in progress
|  | Bit 13 | = 1 : Error in test pattern management
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF02 |  |  | Safety App Watchdog Management fault register
|  | Bit 0 | = 1 : Fast task fault
|  | Bit 1 | = 1 : Slow task fault
|  | Bit 2 | = 1 : App task fault
|  | Bit 3 | = 1 : Background task fault
|  | Bit 4 | = 1 : Safety fast task/input fault
|  | Bit 5 | = 1 : Safety slow task/input fault
|  | Bit 6 | = 1 : Safety app task/input fault
|  | Bit 7 | = 1 : Safety app task/treatment fault
|  | Bit 8 | = 1 : Safety background task fault
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF03 |  |  | Safety LI Activation fault register
|  | Bit 0 | = 1 : Debounce time out
|  | Bit 1 | = 1 : Input not consistent
|  | Bit 2 | = 1 : Consistency check - state machine error
|  | Bit 3 | = 1 : Consistency check - debounce timeout corrupted
|  | Bit 4 | = 1 : Response time data error
|  | Bit 5 | = 1 : Response time corrupted
|  | Bit 6 | = 1 : Undefined consumer queried
|  | Bit 7 | = 1 : Configuration error
|  | Bit 8 | = 1 : Inputs are not in nominal mode
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF04 |  |  | Safe Torque Off fault register
|  | Bit 0 | = 1 : No signal configured
|  | Bit 1 | = 1 : State machine error
|  | Bit 2 | = 1 : Internal data error
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | =1 : SMS SAFF Overspeed
|  | Bit 9 | =1 : SMS SAFF Internal
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | =1 : SFO SAFF Internal
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF05 |  |  | Safe Stop 1 fault register
|  | Bit 0 | = 1 : State machine error
|  | Bit 1 | = 1 : Motor speed sign changed during stop
|  | Bit 2 | = 1 : Motor speed reached trip area
|  | Bit 3 | = 1 : Theoretical motor speed corrupted
|  | Bit 4 | = 1 : Unauthorized configuration
|  | Bit 5 | = 1 : Theoretical motor speed computation error
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Speed sign check: consistency error
|  | Bit 8 | = 1 : Internal SS1 request corrupted
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF06 |  |  | Safely Limited Speed fault register
|  | Bit 0 | = 1 : State machine error
|  | Bit 1 | = 1 : Motor speed sign changed during limitation
|  | Bit 2 | = 1 : Motor speed reached trip area
|  | Bit 3 | = 1 : Data corruption
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF07 |  |  | Safety App Watchdog Management fault register
|  | Bit 0 | Reserved
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF08 |  |  | Safety Mc Watchdog Management fault register
|  | Bit 0 | = 1 : PWM task fault
|  | Bit 1 | = 1 : Fixed task fault
|  | Bit 2 | = 1 : ATMC watchdog fault
|  | Bit 3 | = 1 : DYNFCT watchdog fault
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF09 |  |  | Safety Mc Auto Test fault register
|  | Bit 0 | Reserved
|  | Bit 1 | = 1 : Ram stack overflow
|  | Bit 2 | = 1 : Ram address integrity error
|  | Bit 3 | = 1 : Ram data access error
|  | Bit 4 | = 1 : Flash Checksum Error
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | = 1 : 1ms task overflow
|  | Bit 10 | = 1 : PWM task overflow
|  | Bit 11 | = 1 : Fixed task overflow
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Unwanted interruption
|  | Bit 15 | = 1 : Hardware WD is not running after initialization
SF10 |  |  | Safety Mc Direct shortcircuit fault register
|  | Bit 0 | = 1 : Ground short circuit - Configuration error
|  | Bit 1 | = 1 : Phase to phase short circuit - Configuration error
|  | Bit 2 | = 1 : Ground short circuit detected
|  | Bit 3 | = 1 : Phase to phase short circuit detected
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SF11 |  |  | Safety Mc Dynamic check of activity fault register
|  | Bit 0 | = 1 : App requested safe diagnostic of direct short circuit
|  | Bit 1 | = 1 : App requested consistency check of stator frequency estimation (voltage + current)
|  | Bit 2 | = 1 : App requested diagnostic of SpdStat provided by Mc
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | = 1 : MC safe diagnostic of direct short circuit is enabled
|  | Bit 9 | = 1 : Mc consistency check of stator frequency estimation is enabled
|  | Bit 10 | = 1 : Mc diagnostic of SpdStat provided by Mc is enabled
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
UNT | *** UNT should be read after value parameter (APH, PTH, RTH) ***
|  | Bit 0 to 1 | : APH unit (0 : Wh, 1 : kWh, 2 : MWh)
|  | Bit 2 to 3 | : PTH unit (0 : s, 1 : mn, 2 : h)
|  | Bit 4 to 5 | : RTH unit (0 : s, 1 : mn, 2 : h)
|  | Bit 6 | : Reserved
|  | Bit 7 | : Reserved
|  | Bit 8 | : Reserved
|  | Bit 9 | : Reserved
|  | Bit 10 | : Reserved
|  | Bit 11 | : Reserved
|  | Bit 12 | : Reserved
|  | Bit 13 | : Reserved
|  | Bit 14 | : Reserved
|  | Bit 15 | : Reserved