## readme
How to use this document
This document outlines the Modbus map for the ION9000 device and includes the tags that can be used to reference quantities in custom web pages. There is both a high-level and a detailed view of the Modbus map in this document. For more information on the contents of fields in the detailed Modbus map, see the additional worksheets with the corresponding field names.
Document compatibility
FW version | 004.000.000

## High-Level Modbus Map
Modbus Map Section | Start Address | End Address | Comments
Generic data | 0 | 65535 | Excludes 52001-59999 inclusive for other sections described below
External Control | 52001 | 53000 | Includes external pulse, external boolean, and external numeric. The registers shown in the detailed Modbus Map are all of the possible registers for this section. At any given time these registers may or may not be active.
Enumerated Registers | 54001 | 56000 | The registers shown in the detailed Modbus Map are only a small subset of the registers contained in this section.
Numeric Registers | 56001 | 59999 | The registers shown in the detailed Modbus Map are only a small subset of the registers contained in this section.
Modbus Slave Modules | 0 | 65535 | Modbus addresses used through Modbus slave module cannot conflict with addresses in the generic data section but will automatically overwrite any data presented in the external control, data recorder, enumerated register and numeric register sections.

## Detailed Modbus Map
Quantity | Modbus Register | # of Modbus Registers | Modbus Data Type | Modbus Units | Modbus Permissions | Value Type | Enumerations | Web Page Tag | Display and Web Units | Data Mapping Module | Derived Source | Comments
Meter Name | 30 | 20 | UTF8 | --- | R/O | string | --- | DeviceName | NONE | Config | None
Serial Number | 117 | 12 | UTF8 | --- | R/O | string | --- | Serial Number | NONE | Config | None
Current Version | 1717 | 6 | UTF8 | --- | R/O | numeric | --- | Revision | NONE | Config | None
Year | 1837 | 1 | INT16U | year | R/O | numeric | --- | Year | NONE | Config | None
Month | 1838 | 1 | INT16U | month | R/O | numeric | --- | Month | NONE | Config | None
Day | 1839 | 1 | INT16U | days | R/O | numeric | --- | Day | NONE | Config | None
Hour | 1840 | 1 | INT16U | hours | R/O | numeric | --- | Hour | NONE | Config | None
Minute | 1841 | 1 | INT16U | minutes | R/O | numeric | --- | Minute | NONE | Config | None
Second | 1842 | 1 | INT16U | seconds | R/O | numeric | --- | Second | NONE | Config | None
Day of Week | 1844 | 1 | INT16U | --- | R/O | numeric | --- | Day Of Week | NONE | Config | None
UTC Time | 1845 | 4 | DATETIME | --- | R/O | numeric | --- | UTC Time | NONE | Config | None
Digital Input Status Validity - Base Unit | 2400 | 2 | BITMAP | --- | R/O | bitmap | --- | S States | NONE | IO | None
Digital Output Status Validity - Base Unit | 2402 | 2 | BITMAP | --- | R/O | bitmap | --- | D States | NONE | IO | None
Setpoint Status Validity | 2420 | 2 | BITMAP | --- | R/O | bitmap | --- | SPT States | NONE | IO | None
Digital Input Status Validity – Option Slot A | 2550 | 2 | BITMAP | --- | R/O | bitmap | --- | A S States | NONE | IO | None
Digital Input Status Validity – Option Slot B | 2552 | 2 | BITMAP | --- | R/O | bitmap | --- | B S States | NONE | IO | None
Digital Input Status Validity – Option Slot C | 2554 | 2 | BITMAP | --- | R/O | bitmap | --- | C S States | NONE | IO | None
Digital Input Status Validity – Option Slot D | 2556 | 2 | BITMAP | --- | R/O | bitmap | --- | D S States | NONE | IO | None
Digital Output Status Validity – Option Slot A | 2566 | 2 | BITMAP | --- | R/O | bitmap | --- | A D States | NONE | IO | None
Digital Output Status Validity – Option Slot B | 2568 | 2 | BITMAP | --- | R/O | bitmap | --- | B D States | NONE | IO | None
Digital Output Status Validity – Option Slot C | 2570 | 2 | BITMAP | --- | R/O | bitmap | --- | C D States | NONE | IO | None
Digital Output Status Validity – Option Slot D | 2572 | 2 | BITMAP | --- | R/O | bitmap | --- | D D States | NONE | IO | None
Active Energy Delivered (Into Load) | 2700 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del | KWH | ENM | None
Active Energy Received (Out of Load) | 2702 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh rec | KWH | ENM | None
Active Energy Delivered + Received | 2704 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del+rec | KWH | ENM | None
Active Energy Delivered- Received | 2706 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del-rec | KWH | ENM | None
Reactive Energy Delivered | 2708 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del | KVARH | ENM | None
Reactive Energy Received | 2710 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh rec | KVARH | ENM | None
Reactive Energy Delivered + Received | 2712 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del+rec | KVARH | ENM | None
Reactive Energy Delivered - Received | 2714 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del-rec | KVARH | ENM | None
Apparent Energy Delivered | 2716 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del | KVAH | ENM | None
Apparent Energy Received | 2718 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh rec | KVAH | ENM | None
Apparent Energy Delivered + Received | 2720 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del+rec | KVAH | ENM | None
Apparent Energy Delivered - Received | 2722 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del-rec | KVAH | ENM | None
Active Energy in Quadrant I | 2724 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh Q1 | KWH | ENM | None
Active Energy in Quadrant II | 2726 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh Q2 | KWH | ENM | None
Active Energy in Quadrant III | 2728 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh Q3 | KWH | ENM | None
Active Energy in Quadrant IV | 2730 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh Q4 | KWH | ENM | None
Reactive Energy in Quadrant I | 2732 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh Q1 | KVARH | ENM | None
Reactive Energy in Quadrant II | 2734 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh Q2 | KVARH | ENM | None
Reactive Energy in Quadrant III | 2736 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh Q3 | KVARH | ENM | None
Reactive Energy in Quadrant IV | 2738 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh Q4 | KVARH | ENM | None
Apparent Energy in Quadrant I | 2740 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh Q1 | KVAH | ENM | None
Apparent Energy in Quadrant II | 2742 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh Q2 | KVAH | ENM | None
Apparent Energy in Quadrant III | 2744 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh Q3 | KVAH | ENM | None
Apparent Energy in Quadrant IV | 2746 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh Q4 | KVAH | ENM | None
Conditional Active Energy Delivered (Into Load) | 2748 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Cnd kWh del | KWH | ENM | None
Conditional Active Energy Received (Out of Load) | 2750 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Cnd kWh rec | KWH | ENM | None
Active Energy Delivered - Received, Conditional | 2754 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Cnd kWh d-r | KWH | ENM | None
Conditional Reactive Energy In (Delivered) | 2756 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Cnd kVARh del | KVARH | ENM | None
Conditional Reactive Energy Out (Received) | 2758 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Cnd kVARh rec | KVARH | ENM | None
Reactive Energy Delivered - Received, Conditional | 2762 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Cnd kVARh d-r | KVARH | ENM | None
Apparent Energy Delivered + Received, Conditional | 2768 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | Cnd kVAh d+r | KVAH | ENM | None
Active Energy Delivered , Last Complete Interval | 2772 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Inc kWh del C | KWH | ENM | None
Active Energy Received , Last Complete Interval | 2774 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Inc kWh rec C | KWH | ENM | None
Active Energy Delivered - Received , Last Complete Interval | 2776 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Inc kWh d-r C | KWH | ENM | None
Reactive Energy Delivered , Last Complete Interval | 2778 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Inc kVARh del C | KVARH | ENM | None
Reactive Energy Received , Last Complete Interval | 2780 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Inc kVARh rec C | KVARH | ENM | None
Reactive Energy Delivered - Received , Last Complete Interval | 2782 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Inc kVARh d-r C | KVARH | ENM | None
Apparent Energy Delivered + Received , Last Complete Interval | 2784 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | Inc kVAh d+r C | KVAH | ENM | None
Active Energy Delivered , Present Interval | 2786 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Inc kWh del | KWH | ENM | None
Active Energy Received , Present Interval | 2788 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Inc kWh rec | KWH | ENM | None
Active Energy Delivered - Received , Present Interval | 2790 | 2 | FLOAT32 | kWh | R/O | numeric | --- | Inc kWh d-r | KWH | ENM | None
Reactive Energy Delivered , Present Interval | 2792 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Inc kVARh del | KVARH | ENM | None
Reactive Energy Received , Present Interval | 2794 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Inc kVARh rec | KVARH | ENM | None
Reactive Energy Delivered - Received , Present Interval | 2796 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | Inc kVARh d-r | KVARH | ENM | None
Apparent Energy Delivered + Received , Present Interval | 2798 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | Inc kVAh d+r | KVAH | ENM | None
Active Energy Delivered Interval | 2800 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del int | KWH | ENM | None
Active Energy Received Interval | 2802 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh rec int | KWH | ENM | None
Reactive Energy Delivered Interval | 2804 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del int | KVARH | ENM | None
Reactive Energy Received Interval | 2806 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh rec int | KVARH | ENM | None
Apparent Energy Delivered Interval | 2808 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del int | KVAH | ENM | None
Apparent Energy Received Interval | 2810 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh rec int | KVAH | ENM | None
Input Metering Accumulation Channel 01 | 2830 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM1 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 02 | 2832 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM2 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 03 | 2834 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM3 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 04 | 2836 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM4 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 05 | 2838 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM5 Consumption | NONE | IOM | None
Current A | 3000 | 2 | FLOAT32 | A | R/O | numeric | --- | I a | CT_A | MEM | None
Current B | 3002 | 2 | FLOAT32 | A | R/O | numeric | --- | I b | CT_A | MEM | None
Current C | 3004 | 2 | FLOAT32 | A | R/O | numeric | --- | I c | CT_A | MEM | None
Current N | 3006 | 2 | FLOAT32 | A | R/O | numeric | --- | I 4 | CT_A | MEM | None
Current G | 3008 | 2 | FLOAT32 | A | R/O | numeric | --- | I 5 | CT_A | MEM | None
Current Avg | 3010 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg | CT_A | MEM | None
Current Unbalance Worst | 3018 | 2 | FLOAT32 | --- | R/O | numeric | --- | I unbal | PERCENT | MEM | None
Voltage A-B | 3020 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ab | PT_V | MEM | None
Voltage B-C | 3022 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll bc | PT_V | MEM | None
Voltage C-A | 3024 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ca | PT_V | MEM | None
Voltage L-L Avg | 3026 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll avg | PT_V | MEM | None
Voltage A-N | 3028 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln a | PT_V | MEM | None
Voltage B-N | 3030 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln b | PT_V | MEM | None
Voltage C-N | 3032 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln c | PT_V | MEM | None
Voltage N-G | 3034 | 2 | FLOAT32 | V | R/O | numeric | --- | Vne | PT_V | MEM | None
Voltage L-N Avg | 3036 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln avg | PT_V | MEM | None
Voltage Unbalance L-N Worst | 3052 | 2 | FLOAT32 | --- | R/O | numeric | --- | V unbal | PERCENT | MEM | None
Active Power A | 3054 | 2 | FLOAT32 | W | R/O | numeric | --- | kW a | PT_CT_KW | MEM | None
Active Power B | 3056 | 2 | FLOAT32 | W | R/O | numeric | --- | kW b | PT_CT_KW | MEM | None
Active Power C | 3058 | 2 | FLOAT32 | W | R/O | numeric | --- | kW c | PT_CT_KW | MEM | None
Active Power Total | 3060 | 2 | FLOAT32 | W | R/O | numeric | --- | kW tot | PT_CT_KW | MEM | None
Reactive Power A | 3062 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR a | PT_CT_KVAR | MEM | None
Reactive Power B | 3064 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR b | PT_CT_KVAR | MEM | None
Reactive Power C | 3066 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR c | PT_CT_KVAR | MEM | None
Reactive Power Total | 3068 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR tot | PT_CT_KVAR | MEM | None
Apparent Power A | 3070 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA a | PT_CT_KVA | MEM | None
Apparent Power B | 3072 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA b | PT_CT_KVA | MEM | None
Apparent Power C | 3074 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA c | PT_CT_KVA | MEM | None
Apparent Power Total | 3076 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA tot | PT_CT_KVA | MEM | None
Residual current I0 sum | 3094 | 2 | FLOAT32 | A | R/O | numeric | --- | I calc res | CT_A | MEM | None
Voltage 4-N | 3096 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln 4 | PT_V | MEM | None
Voltage A-G | 3098 | 2 | FLOAT32 | V | R/O | numeric | --- | Vle a | PT_V | MEM | None
Voltage B-G | 3100 | 2 | FLOAT32 | V | R/O | numeric | --- | Vle b | PT_V | MEM | None
Voltage C-G | 3102 | 2 | FLOAT32 | V | R/O | numeric | --- | Vle c | PT_V | MEM | None
Voltage 4-G | 3104 | 2 | FLOAT32 | V | R/O | numeric | --- | Vle 4 | PT_V | MEM | None
Frequency | 3110 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Freq | HZ | MEM | None
Input Metering Rate Channel 01 | 3112 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM1 Rate | NONE | IOM | None
Input Metering Rate Channel 02 | 3114 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM2 Rate | NONE | IOM | None
Input Metering Rate Channel 03 | 3116 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM3 Rate | NONE | IOM | None
Input Metering Rate Channel 04 | 3118 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM4 Rate | NONE | IOM | None
Input Metering Rate Channel 05 | 3120 | 2 | FLOAT32 | --- | R/O | numeric | --- | IM5 Rate | NONE | IOM | None
Current Capacity A | 3136 | 2 | FLOAT32 | --- | R/O | numeric | --- | I a capacity | PERCENT | MEM | None
Current Capacity B | 3138 | 2 | FLOAT32 | --- | R/O | numeric | --- | I b capacity | PERCENT | MEM | None
Current Capacity C | 3140 | 2 | FLOAT32 | --- | R/O | numeric | --- | I c capacity | PERCENT | MEM | None
Current Capacity avg | 3142 | 2 | FLOAT32 | --- | R/O | numeric | --- | I avg capacity | PERCENT | MEM | None
Power Factor A | 3144 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF sign a | PF | MEM | None
Power Factor B | 3146 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF sign b | PF | MEM | None
Power Factor C | 3148 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF sign c | PF | MEM | None
Power Factor Total | 3150 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF sign tot | PF | MEM | None
Displacement Power Factor A | 3152 | 2 | FLOAT32 | --- | R/O | numeric | --- | Dsplcmnt PF 1 | PF | MEM | None
Displacement Power Factor B | 3154 | 2 | FLOAT32 | --- | R/O | numeric | --- | Dsplcmnt PF 2 | PF | MEM | None
Displacement Power Factor C | 3156 | 2 | FLOAT32 | --- | R/O | numeric | --- | Dsplcmnt PF 3 | PF | MEM | None
Displacement Power Factor Total | 3158 | 2 | FLOAT32 | --- | R/O | numeric | --- | Dsplcmnt PF tot | PF | MEM | None
Power Factor A Lagging | 3160 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag a | PF | MEM | None
Power Factor A Leading | 3162 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead a | PF | MEM | None
Power Factor B Lagging | 3164 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag b | PF | MEM | None
Power Factor B Leading | 3166 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead b | PF | MEM | None
Power Factor C Lagging | 3168 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag c | PF | MEM | None
Power Factor C Leading | 3170 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead c | PF | MEM | None
Power Factor Lagging | 3172 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag tot | PF | MEM | None
Power Factor Leading | 3174 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead tot | PF | MEM | None
Active Energy Delivered (Into Load) | 3204 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del | KWH | ENM | None
Active Energy Received (Out of Load) | 3208 | 4 | INT64 | Wh | R/O | numeric | --- | kWh rec | KWH | ENM | None
Active Energy Delivered + Received | 3212 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del+rec | KWH | ENM | None
Active Energy Delivered- Received | 3216 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del-rec | KWH | ENM | None
Reactive Energy Delivered | 3220 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del | KVARH | ENM | None
Reactive Energy Received | 3224 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh rec | KVARH | ENM | None
Reactive Energy Delivered + Received | 3228 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del+rec | KVARH | ENM | None
Reactive Energy Delivered - Received | 3232 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del-rec | KVARH | ENM | None
Apparent Energy Delivered | 3236 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del | KVAH | ENM | None
Apparent Energy Received | 3240 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh rec | KVAH | ENM | None
Apparent Energy Delivered + Received | 3244 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del+rec | KVAH | ENM | None
Apparent Energy Delivered - Received | 3248 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del-rec | KVAH | ENM | None
Active Energy in Quadrant I | 3256 | 4 | INT64 | Wh | R/O | numeric | --- | kWh Q1 | KWH | ENM | None
Active Energy in Quadrant II | 3260 | 4 | INT64 | Wh | R/O | numeric | --- | kWh Q2 | KWH | ENM | None
Active Energy in Quadrant III | 3264 | 4 | INT64 | Wh | R/O | numeric | --- | kWh Q3 | KWH | ENM | None
Active Energy in Quadrant IV | 3268 | 4 | INT64 | Wh | R/O | numeric | --- | kWh Q4 | KWH | ENM | None
Reactive Energy in Quadrant I | 3272 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh Q1 | KVARH | ENM | None
Reactive Energy in Quadrant II | 3276 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh Q2 | KVARH | ENM | None
Reactive Energy in Quadrant III | 3280 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh Q3 | KVARH | ENM | None
Reactive Energy in Quadrant IV | 3284 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh Q4 | KVARH | ENM | None
Apparent Energy in Quadrant I | 3288 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh Q1 | KVAH | ENM | None
Apparent Energy in Quadrant II | 3292 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh Q2 | KVAH | ENM | None
Apparent Energy in Quadrant III | 3296 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh Q3 | KVAH | ENM | None
Apparent Energy in Quadrant IV | 3300 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh Q4 | KVAH | ENM | None
Conditional Active Energy Delivered (Into Load) | 3358 | 4 | INT64 | Wh | R/O | numeric | --- | Cnd kWh del | KWH | ENM | None
Conditional Active Energy Received (Out of Load) | 3362 | 4 | INT64 | Wh | R/O | numeric | --- | Cnd kWh rec | KWH | ENM | None
Active Energy Delivered - Received, Conditional | 3370 | 4 | INT64 | Wh | R/O | numeric | --- | Cnd kWh d-r | KWH | ENM | None
Conditional Reactive Energy In (Delivered) | 3374 | 4 | INT64 | VARh | R/O | numeric | --- | Cnd kVARh del | KVARH | ENM | None
Conditional Reactive Energy Out (Received) | 3378 | 4 | INT64 | VARh | R/O | numeric | --- | Cnd kVARh rec | KVARH | ENM | None
Reactive Energy Delivered - Received, Conditional | 3386 | 4 | INT64 | VARh | R/O | numeric | --- | Cnd kVARh d-r | KVARH | ENM | None
Apparent Energy Delivered + Received, Conditional | 3398 | 4 | INT64 | VAh | R/O | numeric | --- | Cnd kVAh d+r | KVAH | ENM | None
Active Energy Delivered , Last Complete Interval | 3414 | 4 | INT64 | Wh | R/O | numeric | --- | Inc kWh del C | KWH | ENM | None
Active Energy Received , Last Complete Interval | 3418 | 4 | INT64 | Wh | R/O | numeric | --- | Inc kWh rec C | KWH | ENM | None
Active Energy Delivered - Received , Last Complete Interval | 3422 | 4 | INT64 | Wh | R/O | numeric | --- | Inc kWh d-r C | KWH | ENM | None
Reactive Energy Delivered , Last Complete Interval | 3426 | 4 | INT64 | VARh | R/O | numeric | --- | Inc kVARh del C | KVARH | ENM | None
Reactive Energy Received , Last Complete Interval | 3430 | 4 | INT64 | VARh | R/O | numeric | --- | Inc kVARh rec C | KVARH | ENM | None
Reactive Energy Delivered - Received , Last Complete Interval | 3434 | 4 | INT64 | VARh | R/O | numeric | --- | Inc kVARh d-r C | KVARH | ENM | None
Apparent Energy Delivered + Received , Last Complete Interval | 3438 | 4 | INT64 | VAh | R/O | numeric | --- | Inc kVAh d+r C | KVAH | ENM | None
Active Energy Delivered , Present Interval | 3442 | 4 | INT64 | Wh | R/O | numeric | --- | Inc kWh del | KWH | ENM | None
Active Energy Received , Present Interval | 3446 | 4 | INT64 | Wh | R/O | numeric | --- | Inc kWh rec | KWH | ENM | None
Active Energy Delivered - Received , Present Interval | 3450 | 4 | INT64 | Wh | R/O | numeric | --- | Inc kWh d-r | KWH | ENM | None
Reactive Energy Delivered , Present Interval | 3454 | 4 | INT64 | VARh | R/O | numeric | --- | Inc kVARh del | KVARH | ENM | None
Reactive Energy Received , Present Interval | 3458 | 4 | INT64 | VARh | R/O | numeric | --- | Inc kVARh rec | KVARH | ENM | None
Reactive Energy Delivered - Received , Present Interval | 3462 | 4 | INT64 | VARh | R/O | numeric | --- | Inc kVARh d-r | KVARH | ENM | None
Apparent Energy Delivered + Received , Present Interval | 3466 | 4 | INT64 | VAh | R/O | numeric | --- | Inc kVAh d+r | KVAH | ENM | None
Active Energy Delivered Interval | 3470 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del int | KWH | ENM | None
Active Energy Received Interval | 3474 | 4 | INT64 | Wh | R/O | numeric | --- | kWh rec int | KWH | ENM | None
Reactive Energy Delivered Interval | 3478 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del int | KVARH | ENM | None
Reactive Energy Received Interval | 3482 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh rec int | KVARH | ENM | None
Apparent Energy Delivered Interval | 3486 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del int | KVAH | ENM | None
Apparent Energy Received Interval | 3490 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh rec int | KVAH | ENM | None
Input Metering Accumulation Channel 01 | 3570 | 4 | INT64 | --- | R/O | numeric | --- | IM1 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 02 | 3574 | 4 | INT64 | --- | R/O | numeric | --- | IM2 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 03 | 3578 | 4 | INT64 | --- | R/O | numeric | --- | IM3 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 04 | 3582 | 4 | INT64 | --- | R/O | numeric | --- | IM4 Consumption | NONE | IOM | None
Input Metering Accumulation Channel 05 | 3602 | 4 | INT64 | --- | R/O | numeric | --- | IM5 Consumption | NONE | IOM | None
Current A Squared Hours | 3650 | 2 | FLOAT32 | A^2h | R/O | numeric | --- | MU Ia^2h | A_SQ_H | ENM | None
Current B Square Hours | 3652 | 2 | FLOAT32 | A^2h | R/O | numeric | --- | MU Ib^2h | A_SQ_H | ENM | None
Current C Square Hours | 3654 | 2 | FLOAT32 | A^2h | R/O | numeric | --- | MU Ic^2h | A_SQ_H | ENM | None
Voltage A-B Square Hours | 3656 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vll ab^2h | V_SQ_H | ENM | None
Voltage B-C Square Hours | 3658 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vll bc^2h | V_SQ_H | ENM | None
Voltage C-A Square Hours | 3660 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vll ca^2h | V_SQ_H | ENM | None
Current A Squared Hours | 3668 | 2 | FLOAT32 | A^2h | R/O | numeric | --- | MU Ia^2h int | A_SQ_H | ENM | None
Current B Square Hours | 3670 | 2 | FLOAT32 | A^2h | R/O | numeric | --- | MU Ib^2h int | A_SQ_H | ENM | None
Current C Square Hours | 3672 | 2 | FLOAT32 | A^2h | R/O | numeric | --- | MU Ic^2h int | A_SQ_H | ENM | None
Voltage A-B Square Hours | 3674 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vllab^2h int | V_SQ_H | ENM | None
Voltage B-C Square Hours | 3676 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vllbc^2h int | V_SQ_H | ENM | None
Voltage C-A Square Hours | 3678 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vllca^2h int | V_SQ_H | ENM | None
Voltage A-N Square Hours | 3680 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vlna^2h int | V_SQ_H | ENM | None
Voltage B-N Square Hours | 3682 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vlnb^2h int | V_SQ_H | ENM | None
Voltage C-N Square Hours | 3684 | 2 | FLOAT32 | V^2h | R/O | numeric | --- | MU Vlnc^2h int | V_SQ_H | ENM | None
Active Energy Delivered Rate 1 | 4196 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del A | KWH | TOM | None
Active Energy Delivered Rate 2 | 4200 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del B | KWH | TOM | None
Active Energy Delivered Rate 3 | 4204 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del C | KWH | TOM | None
Active Energy Delivered Rate 4 | 4208 | 4 | INT64 | Wh | R/O | numeric | --- | kWh del D | KWH | TOM | None
Active Energy Received Rate 1 | 4228 | 4 | INT64 | Wh | R/O | numeric | --- | kWh rec A | KWH | TOM | None
Active Energy Received Rate 2 | 4232 | 4 | INT64 | Wh | R/O | numeric | --- | kWh rec B | KWH | TOM | None
Active Energy Received Rate 3 | 4236 | 4 | INT64 | Wh | R/O | numeric | --- | kWh rec C | KWH | TOM | None
Active Energy Received Rate 4 | 4240 | 4 | INT64 | Wh | R/O | numeric | --- | kWh rec D | KWH | TOM | None
Reactive Energy Delivered Rate 1 | 4260 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del A | KVARH | TOM | None
Reactive Energy Delivered Rate 2 | 4264 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del B | KVARH | TOM | None
Reactive Energy Delivered Rate 3 | 4268 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del C | KVARH | TOM | None
Reactive Energy Delivered Rate 4 | 4272 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh del D | KVARH | TOM | None
Reactive Energy Received Rate 1 | 4292 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh rec A | KVARH | TOM | None
Reactive Energy Received Rate 2 | 4296 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh rec B | KVARH | TOM | None
Reactive Energy Received Rate 3 | 4300 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh rec C | KVARH | TOM | None
Reactive Energy Received Rate 4 | 4304 | 4 | INT64 | VARh | R/O | numeric | --- | kVARh rec D | KVARH | TOM | None
Apparent Energy Delivered Rate 1 | 4324 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del A | KVAH | TOM | None
Apparent Energy Delivered Rate 2 | 4328 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del B | KVAH | TOM | None
Apparent Energy Delivered Rate 3 | 4332 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del C | KVAH | TOM | None
Apparent Energy Delivered Rate 4 | 4336 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh del D | KVAH | TOM | None
Apparent Energy Received Rate 1 | 4356 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh rec A | KVAH | TOM | None
Apparent Energy Received Rate 2 | 4360 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh rec B | KVAH | TOM | None
Apparent Energy Received Rate 3 | 4364 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh rec C | KVAH | TOM | None
Apparent Energy Received Rate 4 | 4368 | 4 | INT64 | VAh | R/O | numeric | --- | kVAh rec D | KVAH | TOM | None
Active Energy Delivered Rate 1 | 4800 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del A | KWH | TOM | None
Active Energy Delivered Rate 2 | 4802 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del B | KWH | TOM | None
Active Energy Delivered Rate 3 | 4804 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del C | KWH | TOM | None
Active Energy Delivered Rate 4 | 4806 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh del D | KWH | TOM | None
Active Energy Received Rate 1 | 4816 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh rec A | KWH | TOM | None
Active Energy Received Rate 2 | 4818 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh rec B | KWH | TOM | None
Active Energy Received Rate 3 | 4820 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh rec C | KWH | TOM | None
Active Energy Received Rate 4 | 4822 | 2 | FLOAT32 | kWh | R/O | numeric | --- | kWh rec D | KWH | TOM | None
Reactive Energy Delivered Rate 1 | 4832 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del A | KVARH | TOM | None
Reactive Energy Delivered Rate 2 | 4834 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del B | KVARH | TOM | None
Reactive Energy Delivered Rate 3 | 4836 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del C | KVARH | TOM | None
Reactive Energy Delivered Rate 4 | 4838 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh del D | KVARH | TOM | None
Reactive Energy Received Rate 1 | 4848 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh rec A | KVARH | TOM | None
Reactive Energy Received Rate 2 | 4850 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh rec B | KVARH | TOM | None
Reactive Energy Received Rate 3 | 4852 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh rec C | KVARH | TOM | None
Reactive Energy Received Rate 4 | 4854 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | kVARh rec D | KVARH | TOM | None
Apparent Energy Delivered Rate 1 | 4864 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del A | KVAH | TOM | None
Apparent Energy Delivered Rate 2 | 4866 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del B | KVAH | TOM | None
Apparent Energy Delivered Rate 3 | 4868 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del C | KVAH | TOM | None
Apparent Energy Delivered Rate 4 | 4870 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh del D | KVAH | TOM | None
Apparent Energy Received Rate 1 | 4880 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh rec A | KVAH | TOM | None
Apparent Energy Received Rate 2 | 4882 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh rec B | KVAH | TOM | None
Apparent Energy Received Rate 3 | 4884 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh rec C | KVAH | TOM | None
Apparent Energy Received Rate 4 | 4886 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | kVAh rec D | KVAH | TOM | None
Digital Input S1 Count | 8915 | 2 | INT32U | --- | R/O | numeric | --- | S1 Count | NONE | IO | None
Digital Input S2 Count | 8919 | 2 | INT32U | --- | R/O | numeric | --- | S2 Count | NONE | IO | None
Digital Input S3 Count | 8923 | 2 | INT32U | --- | R/O | numeric | --- | S3 Count | NONE | IO | None
Digital Input S4 Count | 8925 | 2 | INT32U |  | R/O | numeric | --- | S4 Count | NONE | IO | None
Digital Input S5 Count | 8927 | 2 | INT32U |  | R/O | numeric | --- | S5 Count | NONE | IO | None
Digital Input S6 Count | 8929 | 2 | INT32U |  | R/O | numeric | --- | S6 Count | NONE | IO | None
Digital Input S7 Count | 8931 | 2 | INT32U |  | R/O | numeric | --- | S7 Count | NONE | IO | None
Digital Input S8 Count | 8933 | 2 | INT32U |  | R/O | numeric | --- | S8 Count | NONE | IO | None
Digital Input A S1 Count | 9027 | 2 | INT32U | --- | R/O | numeric | --- | A S1 Count | NONE | IO | None
Digital Input A S2 Count | 9029 | 2 | INT32U | --- | R/O | numeric | --- | A S2 Count | NONE | IO | None
Digital Input A S3 Count | 9031 | 2 | INT32U | --- | R/O | numeric | --- | A S3 Count | NONE | IO | None
Digital Input A S4 Count | 9033 | 2 | INT32U | --- | R/O | numeric | --- | A S4 Count | NONE | IO | None
Digital Input A S5 Count | 9035 | 2 | INT32U | --- | R/O | numeric | --- | A S5 Count | NONE | IO | None
Digital Input A S6 Count | 9037 | 2 | INT32U | --- | R/O | numeric | --- | A S6 Count | NONE | IO | None
Digital Input B S1 Count | 9039 | 2 | INT32U | --- | R/O | numeric | --- | B S1 Count | NONE | IO | None
Digital Input B S2 Count | 9041 | 2 | INT32U | --- | R/O | numeric | --- | B S2 Count | NONE | IO | None
Digital Input B S3 Count | 9043 | 2 | INT32U | --- | R/O | numeric | --- | B S3 Count | NONE | IO | None
Digital Input B S4 Count | 9045 | 2 | INT32U | --- | R/O | numeric | --- | B S4 Count | NONE | IO | None
Digital Input B S5 Count | 9047 | 2 | INT32U | --- | R/O | numeric | --- | B S5 Count | NONE | IO | None
Digital Input B S6 Count | 9049 | 2 | INT32U | --- | R/O | numeric | --- | B S6 Count | NONE | IO | None
Digital Input C S1 Count | 9051 | 2 | INT32U | --- | R/O | numeric | --- | C S1 Count | NONE | IO | None
Digital Input C S2 Count | 9053 | 2 | INT32U | --- | R/O | numeric | --- | C S2 Count | NONE | IO | None
Digital Input C S3 Count | 9055 | 2 | INT32U | --- | R/O | numeric | --- | C S3 Count | NONE | IO | None
Digital Input C S4 Count | 9057 | 2 | INT32U | --- | R/O | numeric | --- | C S4 Count | NONE | IO | None
Digital Input C S5 Count | 9059 | 2 | INT32U | --- | R/O | numeric | --- | C S5 Count | NONE | IO | None
Digital Input C S6 Count | 9061 | 2 | INT32U | --- | R/O | numeric | --- | C S6 Count | NONE | IO | None
Digital Input D S1 Count | 9063 | 2 | INT32U | --- | R/O | numeric | --- | D S1 Count | NONE | IO | None
Digital Input D S2 Count | 9065 | 2 | INT32U | --- | R/O | numeric | --- | D S2 Count | NONE | IO | None
Digital Input D S3 Count | 9067 | 2 | INT32U | --- | R/O | numeric | --- | D S3 Count | NONE | IO | None
Digital Input D S4 Count | 9069 | 2 | INT32U | --- | R/O | numeric | --- | D S4 Count | NONE | IO | None
Digital Input D S5 Count | 9071 | 2 | INT32U | --- | R/O | numeric | --- | D S5 Count | NONE | IO | None
Digital Input D S6 Count | 9073 | 2 | INT32U | --- | R/O | numeric | --- | D S6 Count | NONE | IO | None
Analog input 1 Scaled Value | 10016 | 2 | FLOAT32 | --- | R/O | numeric | --- | A A1 Scaled | NONE | IO | None
Analog input 2 Scaled Value | 10018 | 2 | FLOAT32 | --- | R/O | numeric | --- | A A2 Scaled | NONE | IO | None
Analog input 3 Scaled Value | 10020 | 2 | FLOAT32 | --- | R/O | numeric | --- | A A3 Scaled | NONE | IO | None
Analog input 4 Scaled Value | 10022 | 2 | FLOAT32 | --- | R/O | numeric | --- | A A4 Scaled | NONE | IO | None
Analog input 1 Scaled Value | 10032 | 2 | FLOAT32 | --- | R/O | numeric | --- | B A1 Scaled | NONE | IO | None
Analog input 2 Scaled Value | 10034 | 2 | FLOAT32 | --- | R/O | numeric | --- | B A2 Scaled | NONE | IO | None
Analog input 3 Scaled Value | 10036 | 2 | FLOAT32 | --- | R/O | numeric | --- | B A3 Scaled | NONE | IO | None
Analog input 4 Scaled Value | 10038 | 2 | FLOAT32 | --- | R/O | numeric | --- | B A4 Scaled | NONE | IO | None
Analog input 1 Scaled Value | 10048 | 2 | FLOAT32 | --- | R/O | numeric | --- | C A1 Scaled | NONE | IO | None
Analog input 2 Scaled Value | 10050 | 2 | FLOAT32 | --- | R/O | numeric | --- | C A2 Scaled | NONE | IO | None
Analog input 3 Scaled Value | 10052 | 2 | FLOAT32 | --- | R/O | numeric | --- | C A3 Scaled | NONE | IO | None
Analog input 4 Scaled Value | 10054 | 2 | FLOAT32 | --- | R/O | numeric | --- | C A4 Scaled | NONE | IO | None
Analog input 1 Scaled Value | 10064 | 2 | FLOAT32 | --- | R/O | numeric | --- | D A1 Scaled | NONE | IO | None
Analog input 2 Scaled Value | 10066 | 2 | FLOAT32 | --- | R/O | numeric | --- | D A2 Scaled | NONE | IO | None
Analog input 3 Scaled Value | 10068 | 2 | FLOAT32 | --- | R/O | numeric | --- | D A3 Scaled | NONE | IO | None
Analog input 4 Scaled Value | 10070 | 2 | FLOAT32 | --- | R/O | numeric | --- | D A4 Scaled | NONE | IO | None
Analog output 1 Normalized Value | 10216 | 2 | FLOAT32 | --- | R/O | numeric | --- | A Q1 Normalized | NONE | IO | None
Analog output 2 Normalized Value | 10218 | 2 | FLOAT32 | --- | R/O | numeric | --- | A Q2 Normalized | NONE | IO | None
Analog output 1 Normalized Value | 10232 | 2 | FLOAT32 | --- | R/O | numeric | --- | B Q1 Normalized | NONE | IO | None
Analog output 2 Normalized Value | 10234 | 2 | FLOAT32 | --- | R/O | numeric | --- | B Q2 Normalized | NONE | IO | None
Analog output 1 Normalized Value | 10248 | 2 | FLOAT32 | --- | R/O | numeric | --- | C Q1 Normalized | NONE | IO | None
Analog output 2 Normalized Value | 10250 | 2 | FLOAT32 | --- | R/O | numeric | --- | C Q2 Normalized | NONE | IO | None
Analog output 1 Normalized Value | 10264 | 2 | FLOAT32 | --- | R/O | numeric | --- | D Q1 Normalized | NONE | IO | None
Analog output 2 Normalized Value | 10266 | 2 | FLOAT32 | --- | R/O | numeric | --- | D Q2 Normalized | NONE | IO | None
Current Disturbance | 13598 | 2 | INT32U | --- | R/O | numeric | --- | I Sg/Sw Count | NONE | PQM | None
Voltage Disturbance | 13600 | 2 | INT32U | --- | R/O | numeric | --- | V Sg/Sw Count | NONE | PQM | None
Transient Count | 13613 | 2 | INT32U | --- | R/O | numeric | --- | V Transient Count | NONE | PQM | None
Over Current I4 | 14040 | 2 | INT32U | --- | R/O | numeric | --- | Over I 4 | NONE | IOM | BASE_PDMD_OVER_I_4
Pickup Setpoint | 14045 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I 4 High Limit | A | IOM | PDMD_OVER_I_4
Pickup Time Delay | 14047 | 2 | INT32U | seconds | R/O | numeric | --- | Over I 4 SusUntlON | S_3D | IOM | PDMD_OVER_I_4
Dropout Setpoint | 14049 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I 4 Low Limit | A | IOM | PDMD_OVER_I_4
Dropout Time Delay | 14051 | 2 | INT32U | seconds | R/O | numeric | --- | Over I 4 SusUntlOFF | S_3D | IOM | PDMD_OVER_I_4
Over Demand, Active Power, Last | 14320 | 2 | INT32U | --- | R/O | numeric | --- | Over kW sd | NONE | IOM | BASE_PDMD_OVER_KW_SD
Pickup Setpoint | 14325 | 2 | FLOAT32 | W | R/O | numeric | --- | Over kW sd High Limit | PT_CT_KW | IOM | PDMD_OVER_KW_SD
Pickup Time Delay | 14327 | 2 | INT32U | seconds | R/O | numeric | --- | Over kW sd SusUntlON | S_3D | IOM | PDMD_OVER_KW_SD
Dropout Setpoint | 14329 | 2 | FLOAT32 | W | R/O | numeric | --- | Over kW sd Low Limit | PT_CT_KW | IOM | PDMD_OVER_KW_SD
Dropout Time Delay | 14331 | 2 | INT32U | seconds | R/O | numeric | --- | Over kW sd SusUntlOFF | S_3D | IOM | PDMD_OVER_KW_SD
Over Voltage Unbalance | 14520 | 2 | INT32U | --- | R/O | numeric | --- | Over V unbal | NONE | IOM | BASE_PDMD_OVER_V_UNBAL
Pickup Setpoint | 14525 | 2 | FLOAT32 | --- | R/O | numeric | --- | Over V unbal High Limit | PERCENT | IOM | PDMD_OVER_V_UNBAL
Pickup Time Delay | 14527 | 2 | INT32U | seconds | R/O | numeric | --- | Over V unbal SusUntlON | S_3D | IOM | PDMD_OVER_V_UNBAL
Dropout Setpoint | 14529 | 2 | FLOAT32 | --- | R/O | numeric | --- | Over V unbal Low Limit | PERCENT | IOM | PDMD_OVER_V_UNBAL
Dropout Time Delay | 14531 | 2 | INT32U | seconds | R/O | numeric | --- | Over V unbal SusUntlOFF | S_3D | IOM | PDMD_OVER_V_UNBAL
Over Current A | 14580 | 2 | INT32U | --- | R/O | numeric | --- | Over I a | NONE | IOM | BASE_PDMD_OVER_I_A
Pickup Setpoint | 14585 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I a High Limit | A | IOM | PDMD_OVER_I_A
Pickup Time Delay | 14587 | 2 | INT32U | seconds | R/O | numeric | --- | Over I a SusUntlON | S_3D | IOM | PDMD_OVER_I_A
Dropout Setpoint | 14589 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I a Low Limit | A | IOM | PDMD_OVER_I_A
Dropout Time Delay | 14591 | 2 | INT32U | seconds | R/O | numeric | --- | Over I a SusUntlOFF | S_3D | IOM | PDMD_OVER_I_A
Over Current B | 14600 | 2 | INT32U | --- | R/O | numeric | --- | Over I b | NONE | IOM | BASE_PDMD_OVER_I_B
Pickup Setpoint | 14605 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I b High Limit | A | IOM | PDMD_OVER_I_B
Pickup Time Delay | 14607 | 2 | INT32U | seconds | R/O | numeric | --- | Over I b SusUntlON | S_3D | IOM | PDMD_OVER_I_B
Dropout Setpoint | 14609 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I b Low Limit | A | IOM | PDMD_OVER_I_B
Dropout Time Delay | 14611 | 2 | INT32U | seconds | R/O | numeric | --- | Over I b SusUntlOFF | S_3D | IOM | PDMD_OVER_I_B
Over Current C | 14620 | 2 | INT32U | --- | R/O | numeric | --- | Over I c | NONE | IOM | BASE_PDMD_OVER_I_C
Pickup Setpoint | 14625 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I c High Limit | A | IOM | PDMD_OVER_I_C
Pickup Time Delay | 14627 | 2 | INT32U | seconds | R/O | numeric | --- | Over I c SusUntlON | S_3D | IOM | PDMD_OVER_I_C
Dropout Setpoint | 14629 | 2 | FLOAT32 | A | R/O | numeric | --- | Over I c Low Limit | A | IOM | PDMD_OVER_I_C
Dropout Time Delay | 14631 | 2 | INT32U | seconds | R/O | numeric | --- | Over I c SusUntlOFF | S_3D | IOM | PDMD_OVER_I_C
HS Current A | 21000 | 2 | FLOAT32 | A | R/O | numeric | --- | HS I a | CT_A | MEM | None
HS Current B | 21002 | 2 | FLOAT32 | A | R/O | numeric | --- | HS I b | CT_A | MEM | None
HS Current C | 21004 | 2 | FLOAT32 | A | R/O | numeric | --- | HS I c | CT_A | MEM | None
HS Current N | 21006 | 2 | FLOAT32 | A | R/O | numeric | --- | HS I 4 | CT_A | MEM | None
HS Current G | 21008 | 2 | FLOAT32 | A | R/O | numeric | --- | HS I 5 | CT_A | MEM | None
HS Current Avg | 21010 | 2 | FLOAT32 | A | R/O | numeric | --- | HS I avg | CT_A | MEM | None
HS Frequency | 21016 | 2 | FLOAT32 | Hz | R/O | numeric | --- | HS Freq | HZ | MEM | None
HS Voltage, A-B | 21018 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vll ab | PT_V | MEM | None
HS Voltage, B-C | 21020 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vll bc | PT_V | MEM | None
HS Voltage, C-A | 21022 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vll ca | PT_V | MEM | None
HS Voltage, L-L Average | 21024 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vll avg | PT_V | MEM | None
HS Voltage, A-N | 21026 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vln a | PT_V | MEM | None
HS Voltage, B-N | 21028 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vln b | PT_V | MEM | None
HS Voltage, C-N | 21030 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vln c | PT_V | MEM | None
HS Voltage, N-G | 21032 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vne | PT_V | MEM | None
HS Voltage, L-N Average | 21034 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vln avg | PT_V | MEM | None
Current Unbalance Worst | 21036 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS I unbal | PERCENT | MEM | None
Voltage Unbalance Worst | 21038 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS V unbal | PERCENT | MEM | None
HS Active Power A | 21040 | 2 | FLOAT32 | W | R/O | numeric | --- | HS kW a | PT_CT_KW | MEM | None
HS Active Power B | 21042 | 2 | FLOAT32 | W | R/O | numeric | --- | HS kW b | PT_CT_KW | MEM | None
HS Active Power C | 21044 | 2 | FLOAT32 | W | R/O | numeric | --- | HS kW c | PT_CT_KW | MEM | None
HS Active Power Total | 21046 | 2 | FLOAT32 | W | R/O | numeric | --- | HS kW tot | PT_CT_KW | MEM | None
HS Reactive Power A | 21048 | 2 | FLOAT32 | VAR | R/O | numeric | --- | HS kVAR a | PT_CT_KVAR | MEM | None
HS Reactive Power B | 21050 | 2 | FLOAT32 | VAR | R/O | numeric | --- | HS kVAR b | PT_CT_KVAR | MEM | None
HS Reactive Power C | 21052 | 2 | FLOAT32 | VAR | R/O | numeric | --- | HS kVAR c | PT_CT_KVAR | MEM | None
HS Reactive Power Total | 21054 | 2 | FLOAT32 | VAR | R/O | numeric | --- | HS kVAR tot | PT_CT_KVAR | MEM | None
HS Apparent Power A | 21056 | 2 | FLOAT32 | VA | R/O | numeric | --- | HS kVA a | PT_CT_KVA | MEM | None
HS Apparent Power B | 21058 | 2 | FLOAT32 | VA | R/O | numeric | --- | HS kVA b | PT_CT_KVA | MEM | None
HS Apparent Power C | 21060 | 2 | FLOAT32 | VA | R/O | numeric | --- | HS kVA c | PT_CT_KVA | MEM | None
HS Apparent Power Total | 21062 | 2 | FLOAT32 | VA | R/O | numeric | --- | HS kVA tot | PT_CT_KVA | MEM | None
HS Power Factor A | 21064 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF sign a | PF | MEM | None
HS Power Factor B | 21066 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF sign b | PF | MEM | None
HS Power Factor C | 21068 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF sign c | PF | MEM | None
HS Power Factor Total | 21070 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF sign tot | PF | MEM | None
HS Power Factor A Lagging | 21072 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lag a | PF | MEM | None
HS Power Factor A Leading | 21074 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lead a | PF | MEM | None
HS Power Factor B Lagging | 21076 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lag b | PF | MEM | None
HS Power Factor B Leading | 21078 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lead b | PF | MEM | None
HS Power Factor C Lagging | 21080 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lag c | PF | MEM | None
HS Power Factor C Leading | 21082 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lead c | PF | MEM | None
HS Power Factor Lagging | 21084 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lag tot | PF | MEM | None
HS Power Factor Leading | 21086 | 2 | FLOAT32 | --- | R/O | numeric | --- | HS PF lead tot | PF | MEM | None
HS Residual current I0 sum | 21088 | 2 | FLOAT32 | A | R/O | numeric | --- | HS I calc res | CT_A | MEM | None
HS Voltage 4-N | 21090 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vln 4 | PT_V | MEM | None
HS Voltage A-G | 21092 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vle a | PT_V | MEM | None
HS Voltage B-G | 21094 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vle b | PT_V | MEM | None
HS Voltage C-G | 21096 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vle c | PT_V | MEM | None
HS Voltage 4-G | 21098 | 2 | FLOAT32 | V | R/O | numeric | --- | HS Vle 4 | PT_V | MEM | None
THD Current A | 21300 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 THD 3s | PERCENT | PQM | None
THD Current B | 21302 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 THD 3s | PERCENT | PQM | None
THD Current C | 21304 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 THD 3s | PERCENT | PQM | None
THD Current N | 21306 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 THD 3s | PERCENT | PQM | None
THD Current G | 21308 | 2 | FLOAT32 | --- | R/O | numeric | --- | I5 THD 3s | PERCENT | PQM | None
THD Voltage A-N | 21330 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 THD 3s | PERCENT | PQM | None
THD Voltage B-N | 21332 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 THD 3s | PERCENT | PQM | None
THD Voltage C-N | 21334 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 THD 3s | PERCENT | PQM | None
THD Voltage 4-N | 21336 | 2 | FLOAT32 | --- | R/O | numeric | --- | V4 THD 3s | PERCENT | PQM | None
K-Factor A | 21358 | 2 | FLOAT32 |  | R/O | numeric | --- | I1 K Factor | NONE | PQM | None
K-Factor B | 21360 | 2 | FLOAT32 |  | R/O | numeric | --- | I2 K Factor | NONE | PQM | None
K-Factor C | 21362 | 2 | FLOAT32 |  | R/O | numeric | --- | I3 K Factor | NONE | PQM | None
Crest Factor A | 21364 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 Crest Factor | NONE | PQM | None
Crest Factor B | 21366 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 Crest Factor | NONE | PQM | None
Crest Factor C | 21368 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 Crest Factor | NONE | PQM | None
Crest Factor N | 21370 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 Crest Factor | NONE | PQM | None
Total Cap HD Current A | 21432 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Current A | 21434 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 Total Ind HD 3s | PERCENT | PQM | None
Total Cap HD Current B | 21436 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Current B | 21438 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 Total Ind HD 3s | PERCENT | PQM | None
Total Cap HD Current C | 21440 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Current C | 21442 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 Total Ind HD 3s | PERCENT | PQM | None
Total Cap HD Current N | 21444 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Current N | 21446 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 Total Ind HD 3s | PERCENT | PQM | None
Total Cap HD Current G | 21448 | 2 | FLOAT32 | --- | R/O | numeric | --- | I5 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Current G | 21450 | 2 | FLOAT32 | --- | R/O | numeric | --- | I5 Total Ind HD 3s | PERCENT | PQM | None
Total Cap HD Voltage A | 21452 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Voltage A | 21454 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 Total Ind HD 3s | PERCENT | PQM | None
Total Cap HD Voltage B | 21456 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Voltage B | 21458 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 Total Ind HD 3s | PERCENT | PQM | None
Total Cap HD Voltage C | 21460 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Voltage C | 21462 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 Total Ind HD 3s | PERCENT | PQM | None
Total Even HD Current A | 21464 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Current A | 21466 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 Total Odd HD 3s | PERCENT | PQM | None
Total Even HD Current B | 21468 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Current B | 21470 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 Total Odd HD 3s | PERCENT | PQM | None
Total Even HD Current C | 21472 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Current C | 21474 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 Total Odd HD 3s | PERCENT | PQM | None
Total Even HD Current N | 21476 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Current N | 21478 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 Total Odd HD 3s | PERCENT | PQM | None
Total Even HD Current G | 21480 | 2 | FLOAT32 | --- | R/O | numeric | --- | I5 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Current G | 21482 | 2 | FLOAT32 | --- | R/O | numeric | --- | I5 Total Odd HD 3s | PERCENT | PQM | None
Total Even HD Voltage A | 21484 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Voltage A | 21486 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 Total Odd HD 3s | PERCENT | PQM | None
Total Even HD Voltage B | 21488 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Voltage B | 21490 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 Total Odd HD 3s | PERCENT | PQM | None
Total Even HD Voltage C | 21492 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Voltage C | 21494 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 Total Odd HD 3s | PERCENT | PQM | None
Fundamental Active Power A | 21496 | 2 | FLOAT32 | W | R/O | numeric | --- | Fundamental kW A | PT_CT_KW | MEM | None
Fundamental Active Power B | 21498 | 2 | FLOAT32 | W | R/O | numeric | --- | Fundamental kW B | PT_CT_KW | MEM | None
Fundamental Active Power C | 21500 | 2 | FLOAT32 | W | R/O | numeric | --- | Fundamental kW C | PT_CT_KW | MEM | None
Fundamental Active Power Total | 21502 | 2 | FLOAT32 | W | R/O | numeric | --- | Fundamental kW Tot | PT_CT_KW | MEM | None
Fundamental Reactive Power A | 21504 | 2 | FLOAT32 | VAR | R/O | numeric | --- | Fundamental kVAR A | PT_CT_KVAR | MEM | None
Fundamental Reactive Power B | 21506 | 2 | FLOAT32 | VAR | R/O | numeric | --- | Fundamental kVAR B | PT_CT_KVAR | MEM | None
Fundamental Reactive Power C | 21508 | 2 | FLOAT32 | VAR | R/O | numeric | --- | Fundamental kVAR C | PT_CT_KVAR | MEM | None
Fundamental Reactive Power Total | 21510 | 2 | FLOAT32 | VAR | R/O | numeric | --- | Fundamental kVAR Tot | PT_CT_KVAR | MEM | None
Fundamental Apparent Power A | 21512 | 2 | FLOAT32 | VA | R/O | numeric | --- | Fundamental kVA A | PT_CT_KVA | MEM | None
Fundamental Apparent Power B | 21514 | 2 | FLOAT32 | VA | R/O | numeric | --- | Fundamental kVA B | PT_CT_KVA | MEM | None
Fundamental Apparent Power C | 21516 | 2 | FLOAT32 | VA | R/O | numeric | --- | Fundamental kVA C | PT_CT_KVA | MEM | None
Fundamental Apparent Power Total | 21518 | 2 | FLOAT32 | VA | R/O | numeric | --- | Fundamental kVA Tot | PT_CT_KVA | MEM | None
Total Cap HD Voltage 4 | 21520 | 2 | FLOAT32 | --- | R/O | numeric | --- | V4 Total Cap HD 3s | PERCENT | PQM | None
Total Ind HD Voltage 4 | 21522 | 2 | FLOAT32 | --- | R/O | numeric | --- | V4 Total Ind HD 3s | PERCENT | PQM | None
Total Even HD Voltage 4 | 21524 | 2 | FLOAT32 | --- | R/O | numeric | --- | V4 Total Even HD 3s | PERCENT | PQM | None
Total Odd HD Voltage 4 | 21526 | 2 | FLOAT32 | --- | R/O | numeric | --- | V4 Total Odd HD 3s | PERCENT | PQM | None
Current, Positive Sequence, Magnitude | 21598 | 2 | FLOAT32 | A | R/O | numeric | --- | I PosSeqMag | CT_A | PQM | BASE_PDMD_I_POSSEQMAG
Current, Positive Sequence, Angle | 21600 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I PosSeqPhs | DEGREES | PQM | PDMD_I_POSSEQMAG
Current, Negative Sequence, Magnitude | 21602 | 2 | FLOAT32 | A | R/O | numeric | --- | I NegSeqMag | CT_A | PQM | PDMD_I_POSSEQMAG
Current, Negative Sequence, Angle | 21604 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I NegSeqPhs | DEGREES | PQM | PDMD_I_POSSEQMAG
Current, Zero Sequence, Magnitude | 21606 | 2 | FLOAT32 | A | R/O | numeric | --- | I ZeroSeqMag | CT_A | PQM | PDMD_I_POSSEQMAG
Current, Zero Sequence, Angle | 21608 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I ZeroSeqPhs | DEGREES | PQM | PDMD_I_POSSEQMAG
Voltage, Positive Sequence, Magnitude | 21610 | 2 | FLOAT32 | V | R/O | numeric | --- | V PosSeqMag | PT_V | PQM | BASE_PDMD_V_POSSEQMAG
Voltage, Positive Sequence, Angle | 21612 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V PosSeqPhs | DEGREES | PQM | PDMD_V_POSSEQMAG
Voltage, Negative Sequence, Magnitude | 21614 | 2 | FLOAT32 | V | R/O | numeric | --- | V NegSeqMag | PT_V | PQM | PDMD_V_POSSEQMAG
Voltage, Negative Sequence, Angle | 21616 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V NegSeqPhs | DEGREES | PQM | PDMD_V_POSSEQMAG
Voltage, Zero Sequence, Magnitude | 21618 | 2 | FLOAT32 | V | R/O | numeric | --- | V ZeroSeqMag | PT_V | PQM | PDMD_V_POSSEQMAG
Voltage, Zero Sequence, Angle | 21620 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V ZeroSeqPhs | DEGREES | PQM | PDMD_V_POSSEQMAG
K-Factor N | 21678 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 K Factor | NONE | PQM | None
K-Factor G | 21680 | 2 | FLOAT32 | --- | R/O | numeric | --- | I5 K Factor | NONE | PQM | None
Crest Factor G | 21682 | 2 | FLOAT32 | --- | R/O | numeric | --- | I5 Crest Factor | NONE | PQM | None
Voltage A-N, H1 Magnitude, V | 22878 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H1 Mag 3s | V | PQM | BASE_PDMD_V1_H1_MAG_3S
Voltage A-N, H1 Angle | 22880 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H1 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H2 Magnitude, V | 22884 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H2 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H2 Angle | 22886 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H2 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H3 Magnitude, V | 22890 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H3 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H3 Angle | 22892 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H3 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H4 Magnitude, V | 22896 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H4 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H4 Angle | 22898 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H4 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H5 Magnitude, V | 22902 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H5 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H5 Angle | 22904 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H5 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H6 Magnitude, V | 22908 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H6 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H6 Angle | 22910 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H6 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H7 Magnitude, V | 22914 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H7 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H7 Angle | 22916 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H7 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H8 Magnitude, V | 22920 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H8 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H8 Angle | 22922 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H8 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H9 Magnitude, V | 22926 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H9 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H9 Angle | 22928 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H9 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H10 Magnitude, V | 22932 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H10 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H10 Angle | 22934 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H10 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H11 Magnitude, V | 22938 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H11 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H11 Angle | 22940 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H11 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H12 Magnitude, V | 22944 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H12 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H12 Angle | 22946 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H12 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H13 Magnitude, V | 22950 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H13 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H13 Angle | 22952 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H13 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H14 Magnitude, V | 22956 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H14 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H14 Angle | 22958 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H14 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H15 Magnitude, V | 22962 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H15 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H15 Angle | 22964 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H15 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H16 Magnitude, V | 22968 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H16 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H16 Angle | 22970 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H16 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H17 Magnitude, V | 22974 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H17 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H17 Angle | 22976 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H17 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H18 Magnitude, V | 22980 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H18 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H18 Angle | 22982 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H18 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H19 Magnitude, V | 22986 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H19 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H19 Angle | 22988 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H19 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H20 Magnitude, V | 22992 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H20 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H20 Angle | 22994 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H20 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H21 Magnitude, V | 22998 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H21 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H21 Angle | 23000 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H21 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H22 Magnitude, V | 23004 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H22 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H22 Angle | 23006 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H22 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H23 Magnitude, V | 23010 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H23 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H23 Angle | 23012 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H23 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H24 Magnitude, V | 23016 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H24 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H24 Angle | 23018 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H24 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H25 Magnitude, V | 23022 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H25 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H25 Angle | 23024 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H25 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H26 Magnitude, V | 23028 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H26 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H26 Angle | 23030 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H26 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H27 Magnitude, V | 23034 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H27 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H27 Angle | 23036 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H27 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H28 Magnitude, V | 23040 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H28 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H28 Angle | 23042 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H28 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H29 Magnitude, V | 23046 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H29 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H29 Angle | 23048 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H29 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H30 Magnitude, V | 23052 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H30 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H30 Angle | 23054 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H30 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H31 Magnitude, V | 23058 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H31 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H31 Angle | 23060 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H31 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H32 Magnitude, V | 23064 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H32 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H32 Angle | 23066 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H32 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H33 Magnitude, V | 23070 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H33 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H33 Angle | 23072 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H33 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H34 Magnitude, V | 23076 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H34 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H34 Angle | 23078 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H34 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H35 Magnitude, V | 23082 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H35 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H35 Angle | 23084 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H35 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H36 Magnitude, V | 23088 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H36 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H36 Angle | 23090 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H36 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H37 Magnitude, V | 23094 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H37 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H37 Angle | 23096 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H37 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H38 Magnitude, V | 23100 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H38 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H38 Angle | 23102 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H38 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H39 Magnitude, V | 23106 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H39 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H39 Angle | 23108 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H39 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H40 Magnitude, V | 23112 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H40 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H40 Angle | 23114 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H40 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H41 Magnitude, V | 23118 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H41 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H41 Angle | 23120 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H41 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H42 Magnitude, V | 23124 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H42 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H42 Angle | 23126 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H42 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H43 Magnitude, V | 23130 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H43 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H43 Angle | 23132 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H43 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H44 Magnitude, V | 23136 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H44 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H44 Angle | 23138 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H44 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H45 Magnitude, V | 23142 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H45 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H45 Angle | 23144 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H45 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H46 Magnitude, V | 23148 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H46 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H46 Angle | 23150 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H46 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H47 Magnitude, V | 23154 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H47 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H47 Angle | 23156 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H47 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H48 Magnitude, V | 23160 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H48 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H48 Angle | 23162 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H48 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H49 Magnitude, V | 23166 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H49 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H49 Angle | 23168 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H49 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H50 Magnitude, V | 23172 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H50 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H50 Angle | 23174 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H50 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H51 Magnitude, V | 23178 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H51 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H51 Angle | 23180 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H51 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H52 Magnitude, V | 23184 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H52 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H52 Angle | 23186 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H52 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H53 Magnitude, V | 23190 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H53 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H53 Angle | 23192 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H53 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H54 Magnitude, V | 23196 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H54 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H54 Angle | 23198 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H54 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H55 Magnitude, V | 23202 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H55 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H55 Angle | 23204 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H55 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H56 Magnitude, V | 23208 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H56 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H56 Angle | 23210 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H56 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H57 Magnitude, V | 23214 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H57 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H57 Angle | 23216 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H57 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H58 Magnitude, V | 23220 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H58 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H58 Angle | 23222 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H58 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H59 Magnitude, V | 23226 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H59 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H59 Angle | 23228 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H59 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H60 Magnitude, V | 23232 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H60 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H60 Angle | 23234 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H60 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H61 Magnitude, V | 23238 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H61 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H61 Angle | 23240 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H61 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H62 Magnitude, V | 23244 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H62 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H62 Angle | 23246 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H62 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H63 Magnitude, V | 23250 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H63 Mag 3s | V | PQM | PDMD_V1_H1_MAG_3S
Voltage A-N, H63 Angle | 23252 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H63 Ang 3s | DEGREES | PQM | PDMD_V1_H1_MAG_3S
Voltage B-N, H1 Magnitude, V | 23266 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H1 Mag 3s | V | PQM | BASE_PDMD_V2_H1_MAG_3S
Voltage B-N, H1 Angle | 23268 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H1 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H2 Magnitude, V | 23272 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H2 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H2 Angle | 23274 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H2 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H3 Magnitude, V | 23278 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H3 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H3 Angle | 23280 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H3 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H4 Magnitude, V | 23284 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H4 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H4 Angle | 23286 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H4 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H5 Magnitude, V | 23290 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H5 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H5 Angle | 23292 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H5 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H6 Magnitude, V | 23296 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H6 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H6 Angle | 23298 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H6 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H7 Magnitude, V | 23302 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H7 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H7 Angle | 23304 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H7 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H8 Magnitude, V | 23308 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H8 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H8 Angle | 23310 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H8 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H9 Magnitude, V | 23314 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H9 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H9 Angle | 23316 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H9 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H10 Magnitude, V | 23320 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H10 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H10 Angle | 23322 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H10 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H11 Magnitude, V | 23326 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H11 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H11 Angle | 23328 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H11 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H12 Magnitude, V | 23332 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H12 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H12 Angle | 23334 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H12 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H13 Magnitude, V | 23338 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H13 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H13 Angle | 23340 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H13 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H14 Magnitude, V | 23344 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H14 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H14 Angle | 23346 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H14 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H15 Magnitude, V | 23350 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H15 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H15 Angle | 23352 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H15 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H16 Magnitude, V | 23356 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H16 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H16 Angle | 23358 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H16 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H17 Magnitude, V | 23362 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H17 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H17 Angle | 23364 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H17 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H18 Magnitude, V | 23368 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H18 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H18 Angle | 23370 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H18 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H19 Magnitude, V | 23374 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H19 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H19 Angle | 23376 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H19 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H20 Magnitude, V | 23380 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H20 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H20 Angle | 23382 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H20 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H21 Magnitude, V | 23386 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H21 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H21 Angle | 23388 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H21 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H22 Magnitude, V | 23392 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H22 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H22 Angle | 23394 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H22 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H23 Magnitude, V | 23398 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H23 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H23 Angle | 23400 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H23 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H24 Magnitude, V | 23404 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H24 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H24 Angle | 23406 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H24 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H25 Magnitude, V | 23410 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H25 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H25 Angle | 23412 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H25 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H26 Magnitude, V | 23416 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H26 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H26 Angle | 23418 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H26 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H27 Magnitude, V | 23422 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H27 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H27 Angle | 23424 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H27 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H28 Magnitude, V | 23428 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H28 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H28 Angle | 23430 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H28 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H29 Magnitude, V | 23434 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H29 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H29 Angle | 23436 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H29 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H30 Magnitude, V | 23440 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H30 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H30 Angle | 23442 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H30 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H31 Magnitude, V | 23446 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H31 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H31 Angle | 23448 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H31 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H32 Magnitude, V | 23452 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H32 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H32 Angle | 23454 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H32 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H33 Magnitude, V | 23458 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H33 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H33 Angle | 23460 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H33 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H34 Magnitude, V | 23464 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H34 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H34 Angle | 23466 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H34 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H35 Magnitude, V | 23470 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H35 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H35 Angle | 23472 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H35 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H36 Magnitude, V | 23476 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H36 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H36 Angle | 23478 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H36 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H37 Magnitude, V | 23482 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H37 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H37 Angle | 23484 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H37 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H38 Magnitude, V | 23488 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H38 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H38 Angle | 23490 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H38 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H39 Magnitude, V | 23494 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H39 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H39 Angle | 23496 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H39 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H40 Magnitude, V | 23500 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H40 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H40 Angle | 23502 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H40 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H41 Magnitude, V | 23506 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H41 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H41 Angle | 23508 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H41 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H42 Magnitude, V | 23512 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H42 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H42 Angle | 23514 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H42 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H43 Magnitude, V | 23518 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H43 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H43 Angle | 23520 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H43 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H44 Magnitude, V | 23524 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H44 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H44 Angle | 23526 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H44 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H45 Magnitude, V | 23530 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H45 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H45 Angle | 23532 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H45 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H46 Magnitude, V | 23536 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H46 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H46 Angle | 23538 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H46 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H47 Magnitude, V | 23542 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H47 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H47 Angle | 23544 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H47 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H48 Magnitude, V | 23548 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H48 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H48 Angle | 23550 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H48 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H49 Magnitude, V | 23554 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H49 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H49 Angle | 23556 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H49 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H50 Magnitude, V | 23560 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H50 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H50 Angle | 23562 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H50 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H51 Magnitude, V | 23566 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H51 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H51 Angle | 23568 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H51 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H52 Magnitude, V | 23572 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H52 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H52 Angle | 23574 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H52 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H53 Magnitude, V | 23578 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H53 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H53 Angle | 23580 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H53 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H54 Magnitude, V | 23584 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H54 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H54 Angle | 23586 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H54 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H55 Magnitude, V | 23590 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H55 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H55 Angle | 23592 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H55 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H56 Magnitude, V | 23596 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H56 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H56 Angle | 23598 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H56 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H57 Magnitude, V | 23602 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H57 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H57 Angle | 23604 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H57 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H58 Magnitude, V | 23608 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H58 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H58 Angle | 23610 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H58 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H59 Magnitude, V | 23614 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H59 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H59 Angle | 23616 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H59 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H60 Magnitude, V | 23620 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H60 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H60 Angle | 23622 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H60 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H61 Magnitude, V | 23626 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H61 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H61 Angle | 23628 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H61 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H62 Magnitude, V | 23632 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H62 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H62 Angle | 23634 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H62 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H63 Magnitude, V | 23638 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H63 Mag 3s | V | PQM | PDMD_V2_H1_MAG_3S
Voltage B-N, H63 Angle | 23640 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H63 Ang 3s | DEGREES | PQM | PDMD_V2_H1_MAG_3S
Voltage C-N, H1 Magnitude, V | 23654 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H1 Mag 3s | V | PQM | BASE_PDMD_V3_H1_MAG_3S
Voltage C-N, H1 Angle | 23656 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H1 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H2 Magnitude, V | 23660 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H2 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H2 Angle | 23662 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H2 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H3 Magnitude, V | 23666 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H3 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H3 Angle | 23668 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H3 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H4 Magnitude, V | 23672 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H4 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H4 Angle | 23674 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H4 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H5 Magnitude, V | 23678 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H5 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H5 Angle | 23680 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H5 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H6 Magnitude, V | 23684 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H6 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H6 Angle | 23686 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H6 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H7 Magnitude, V | 23690 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H7 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H7 Angle | 23692 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H7 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H8 Magnitude, V | 23696 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H8 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H8 Angle | 23698 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H8 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H9 Magnitude, V | 23702 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H9 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H9 Angle | 23704 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H9 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H10 Magnitude, V | 23708 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H10 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H10 Angle | 23710 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H10 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H11 Magnitude, V | 23714 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H11 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H11 Angle | 23716 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H11 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H12 Magnitude, V | 23720 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H12 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H12 Angle | 23722 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H12 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H13 Magnitude, V | 23726 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H13 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H13 Angle | 23728 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H13 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H14 Magnitude, V | 23732 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H14 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H14 Angle | 23734 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H14 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H15 Magnitude, V | 23738 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H15 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H15 Angle | 23740 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H15 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H16 Magnitude, V | 23744 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H16 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H16 Angle | 23746 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H16 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H17 Magnitude, V | 23750 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H17 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H17 Angle | 23752 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H17 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H18 Magnitude, V | 23756 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H18 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H18 Angle | 23758 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H18 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H19 Magnitude, V | 23762 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H19 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H19 Angle | 23764 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H19 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H20 Magnitude, V | 23768 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H20 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H20 Angle | 23770 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H20 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H21 Magnitude, V | 23774 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H21 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H21 Angle | 23776 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H21 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H22 Magnitude, V | 23780 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H22 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H22 Angle | 23782 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H22 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H23 Magnitude, V | 23786 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H23 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H23 Angle | 23788 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H23 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H24 Magnitude, V | 23792 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H24 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H24 Angle | 23794 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H24 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H25 Magnitude, V | 23798 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H25 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H25 Angle | 23800 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H25 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H26 Magnitude, V | 23804 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H26 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H26 Angle | 23806 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H26 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H27 Magnitude, V | 23810 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H27 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H27 Angle | 23812 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H27 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H28 Magnitude, V | 23816 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H28 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H28 Angle | 23818 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H28 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H29 Magnitude, V | 23822 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H29 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H29 Angle | 23824 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H29 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H30 Magnitude, V | 23828 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H30 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H30 Angle | 23830 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H30 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H31 Magnitude, V | 23834 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H31 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H31 Angle | 23836 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H31 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H32 Magnitude, V | 23840 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H32 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H32 Angle | 23842 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H32 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H33 Magnitude, V | 23846 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H33 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H33 Angle | 23848 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H33 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H34 Magnitude, V | 23852 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H34 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H34 Angle | 23854 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H34 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H35 Magnitude, V | 23858 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H35 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H35 Angle | 23860 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H35 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H36 Magnitude, V | 23864 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H36 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H36 Angle | 23866 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H36 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H37 Magnitude, V | 23870 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H37 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H37 Angle | 23872 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H37 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H38 Magnitude, V | 23876 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H38 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H38 Angle | 23878 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H38 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H39 Magnitude, V | 23882 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H39 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H39 Angle | 23884 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H39 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H40 Magnitude, V | 23888 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H40 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H40 Angle | 23890 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H40 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H41 Magnitude, V | 23894 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H41 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H41 Angle | 23896 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H41 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H42 Magnitude, V | 23900 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H42 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H42 Angle | 23902 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H42 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H43 Magnitude, V | 23906 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H43 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H43 Angle | 23908 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H43 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H44 Magnitude, V | 23912 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H44 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H44 Angle | 23914 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H44 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H45 Magnitude, V | 23918 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H45 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H45 Angle | 23920 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H45 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H46 Magnitude, V | 23924 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H46 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H46 Angle | 23926 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H46 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H47 Magnitude, V | 23930 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H47 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H47 Angle | 23932 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H47 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H48 Magnitude, V | 23936 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H48 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H48 Angle | 23938 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H48 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H49 Magnitude, V | 23942 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H49 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H49 Angle | 23944 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H49 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H50 Magnitude, V | 23948 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H50 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H50 Angle | 23950 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H50 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H51 Magnitude, V | 23954 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H51 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H51 Angle | 23956 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H51 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H52 Magnitude, V | 23960 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H52 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H52 Angle | 23962 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H52 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H53 Magnitude, V | 23966 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H53 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H53 Angle | 23968 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H53 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H54 Magnitude, V | 23972 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H54 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H54 Angle | 23974 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H54 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H55 Magnitude, V | 23978 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H55 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H55 Angle | 23980 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H55 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H56 Magnitude, V | 23984 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H56 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H56 Angle | 23986 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H56 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H57 Magnitude, V | 23990 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H57 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H57 Angle | 23992 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H57 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H58 Magnitude, V | 23996 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H58 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H58 Angle | 23998 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H58 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H59 Magnitude, V | 24002 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H59 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H59 Angle | 24004 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H59 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H60 Magnitude, V | 24008 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H60 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H60 Angle | 24010 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H60 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H61 Magnitude, V | 24014 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H61 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H61 Angle | 24016 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H61 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H62 Magnitude, V | 24020 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H62 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H62 Angle | 24022 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H62 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H63 Magnitude, V | 24026 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H63 Mag 3s | V | PQM | PDMD_V3_H1_MAG_3S
Voltage C-N, H63 Angle | 24028 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H63 Ang 3s | DEGREES | PQM | PDMD_V3_H1_MAG_3S
Voltage 4-N, H1 Magnitude, V | 24042 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H1 Mag 3s | V | PQM | BASE_PDMD_V4_H1_MAG_3S
Voltage 4-N, H1 Angle | 24044 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H1 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H2 Magnitude, V | 24048 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H2 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H2 Angle | 24050 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H2 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H3 Magnitude, V | 24054 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H3 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H3 Angle | 24056 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H3 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H4 Magnitude, V | 24060 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H4 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H4 Angle | 24062 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H4 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H5 Magnitude, V | 24066 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H5 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H5 Angle | 24068 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H5 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H6 Magnitude, V | 24072 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H6 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H6 Angle | 24074 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H6 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H7 Magnitude, V | 24078 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H7 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H7 Angle | 24080 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H7 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H8 Magnitude, V | 24084 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H8 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H8 Angle | 24086 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H8 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H9 Magnitude, V | 24090 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H9 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H9 Angle | 24092 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H9 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H10 Magnitude, V | 24096 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H10 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H10 Angle | 24098 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H10 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H11 Magnitude, V | 24102 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H11 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H11 Angle | 24104 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H11 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H12 Magnitude, V | 24108 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H12 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H12 Angle | 24110 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H12 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H13 Magnitude, V | 24114 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H13 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H13 Angle | 24116 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H13 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H14 Magnitude, V | 24120 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H14 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H14 Angle | 24122 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H14 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H15 Magnitude, V | 24126 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H15 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H15 Angle | 24128 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H15 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H16 Magnitude, V | 24132 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H16 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H16 Angle | 24134 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H16 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H17 Magnitude, V | 24138 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H17 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H17 Angle | 24140 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H17 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H18 Magnitude, V | 24144 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H18 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H18 Angle | 24146 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H18 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H19 Magnitude, V | 24150 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H19 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H19 Angle | 24152 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H19 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H20 Magnitude, V | 24156 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H20 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H20 Angle | 24158 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H20 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H21 Magnitude, V | 24162 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H21 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H21 Angle | 24164 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H21 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H22 Magnitude, V | 24168 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H22 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H22 Angle | 24170 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H22 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H23 Magnitude, V | 24174 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H23 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H23 Angle | 24176 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H23 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H24 Magnitude, V | 24180 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H24 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H24 Angle | 24182 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H24 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H25 Magnitude, V | 24186 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H25 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H25 Angle | 24188 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H25 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H26 Magnitude, V | 24192 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H26 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H26 Angle | 24194 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H26 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H27 Magnitude, V | 24198 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H27 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H27 Angle | 24200 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H27 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H28 Magnitude, V | 24204 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H28 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H28 Angle | 24206 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H28 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H29 Magnitude, V | 24210 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H29 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H29 Angle | 24212 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H29 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H30 Magnitude, V | 24216 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H30 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H30 Angle | 24218 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H30 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H31 Magnitude, V | 24222 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H31 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H31 Angle | 24224 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H31 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H32 Magnitude, V | 24228 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H32 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H32 Angle | 24230 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H32 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H33 Magnitude, V | 24234 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H33 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H33 Angle | 24236 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H33 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H34 Magnitude, V | 24240 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H34 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H34 Angle | 24242 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H34 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H35 Magnitude, V | 24246 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H35 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H35 Angle | 24248 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H35 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H36 Magnitude, V | 24252 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H36 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H36 Angle | 24254 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H36 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H37 Magnitude, V | 24258 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H37 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H37 Angle | 24260 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H37 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H38 Magnitude, V | 24264 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H38 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H38 Angle | 24266 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H38 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H39 Magnitude, V | 24270 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H39 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H39 Angle | 24272 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H39 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H40 Magnitude, V | 24276 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H40 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H40 Angle | 24278 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H40 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H41 Magnitude, V | 24282 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H41 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H41 Angle | 24284 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H41 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H42 Magnitude, V | 24288 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H42 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H42 Angle | 24290 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H42 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H43 Magnitude, V | 24294 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H43 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H43 Angle | 24296 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H43 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H44 Magnitude, V | 24300 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H44 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H44 Angle | 24302 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H44 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H45 Magnitude, V | 24306 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H45 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H45 Angle | 24308 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H45 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H46 Magnitude, V | 24312 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H46 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H46 Angle | 24314 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H46 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H47 Magnitude, V | 24318 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H47 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H47 Angle | 24320 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H47 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H48 Magnitude, V | 24324 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H48 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H48 Angle | 24326 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H48 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H49 Magnitude, V | 24330 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H49 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H49 Angle | 24332 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H49 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H50 Magnitude, V | 24336 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H50 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H50 Angle | 24338 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H50 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H51 Magnitude, V | 24342 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H51 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H51 Angle | 24344 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H51 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H52 Magnitude, V | 24348 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H52 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H52 Angle | 24350 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H52 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H53 Magnitude, V | 24354 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H53 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H53 Angle | 24356 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H53 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H54 Magnitude, V | 24360 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H54 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H54 Angle | 24362 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H54 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H55 Magnitude, V | 24366 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H55 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H55 Angle | 24368 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H55 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H56 Magnitude, V | 24372 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H56 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H56 Angle | 24374 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H56 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H57 Magnitude, V | 24378 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H57 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H57 Angle | 24380 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H57 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H58 Magnitude, V | 24384 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H58 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H58 Angle | 24386 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H58 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H59 Magnitude, V | 24390 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H59 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H59 Angle | 24392 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H59 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H60 Magnitude, V | 24396 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H60 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H60 Angle | 24398 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H60 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H61 Magnitude, V | 24402 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H61 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H61 Angle | 24404 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H61 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H62 Magnitude, V | 24408 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H62 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H62 Angle | 24410 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H62 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H63 Magnitude, V | 24414 | 2 | FLOAT32 | V | R/O | numeric | --- | V4 H63 Mag 3s | V | PQM | PDMD_V4_H1_MAG_3S
Voltage 4-N, H63 Angle | 24416 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V4 H63 Ang 3s | DEGREES | PQM | PDMD_V4_H1_MAG_3S
Current A, H1 Magnitude, A | 24430 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H1 Mag 3s | A | PQM | BASE_PDMD_I1_H1_MAG_3S
Current A, H1 Angle | 24432 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H1 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H2 Magnitude, A | 24436 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H2 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H2 Angle | 24438 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H2 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H3 Magnitude, A | 24442 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H3 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H3 Angle | 24444 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H3 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H4 Magnitude, A | 24448 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H4 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H4 Angle | 24450 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H4 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H5 Magnitude, A | 24454 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H5 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H5 Angle | 24456 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H5 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H6 Magnitude, A | 24460 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H6 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H6 Angle | 24462 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H6 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H7 Magnitude, A | 24466 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H7 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H7 Angle | 24468 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H7 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H8 Magnitude, A | 24472 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H8 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H8 Angle | 24474 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H8 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H9 Magnitude, A | 24478 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H9 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H9 Angle | 24480 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H9 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H10 Magnitude, A | 24484 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H10 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H10 Angle | 24486 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H10 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H11 Magnitude, A | 24490 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H11 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H11 Angle | 24492 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H11 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H12 Magnitude, A | 24496 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H12 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H12 Angle | 24498 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H12 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H13 Magnitude, A | 24502 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H13 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H13 Angle | 24504 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H13 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H14 Magnitude, A | 24508 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H14 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H14 Angle | 24510 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H14 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H15 Magnitude, A | 24514 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H15 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H15 Angle | 24516 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H15 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H16 Magnitude, A | 24520 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H16 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H16 Angle | 24522 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H16 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H17 Magnitude, A | 24526 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H17 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H17 Angle | 24528 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H17 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H18 Magnitude, A | 24532 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H18 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H18 Angle | 24534 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H18 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H19 Magnitude, A | 24538 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H19 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H19 Angle | 24540 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H19 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H20 Magnitude, A | 24544 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H20 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H20 Angle | 24546 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H20 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H21 Magnitude, A | 24550 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H21 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H21 Angle | 24552 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H21 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H22 Magnitude, A | 24556 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H22 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H22 Angle | 24558 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H22 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H23 Magnitude, A | 24562 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H23 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H23 Angle | 24564 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H23 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H24 Magnitude, A | 24568 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H24 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H24 Angle | 24570 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H24 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H25 Magnitude, A | 24574 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H25 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H25 Angle | 24576 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H25 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H26 Magnitude, A | 24580 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H26 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H26 Angle | 24582 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H26 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H27 Magnitude, A | 24586 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H27 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H27 Angle | 24588 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H27 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H28 Magnitude, A | 24592 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H28 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H28 Angle | 24594 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H28 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H29 Magnitude, A | 24598 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H29 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H29 Angle | 24600 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H29 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H30 Magnitude, A | 24604 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H30 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H30 Angle | 24606 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H30 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H31 Magnitude, A | 24610 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H31 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H31 Angle | 24612 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H31 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H32 Magnitude, A | 24616 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H32 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H32 Angle | 24618 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H32 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H33 Magnitude, A | 24622 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H33 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H33 Angle | 24624 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H33 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H34 Magnitude, A | 24628 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H34 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H34 Angle | 24630 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H34 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H35 Magnitude, A | 24634 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H35 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H35 Angle | 24636 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H35 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H36 Magnitude, A | 24640 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H36 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H36 Angle | 24642 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H36 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H37 Magnitude, A | 24646 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H37 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H37 Angle | 24648 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H37 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H38 Magnitude, A | 24652 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H38 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H38 Angle | 24654 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H38 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H39 Magnitude, A | 24658 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H39 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H39 Angle | 24660 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H39 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H40 Magnitude, A | 24664 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H40 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H40 Angle | 24666 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H40 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H41 Magnitude, A | 24670 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H41 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H41 Angle | 24672 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H41 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H42 Magnitude, A | 24676 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H42 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H42 Angle | 24678 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H42 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H43 Magnitude, A | 24682 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H43 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H43 Angle | 24684 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H43 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H44 Magnitude, A | 24688 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H44 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H44 Angle | 24690 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H44 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H45 Magnitude, A | 24694 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H45 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H45 Angle | 24696 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H45 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H46 Magnitude, A | 24700 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H46 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H46 Angle | 24702 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H46 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H47 Magnitude, A | 24706 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H47 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H47 Angle | 24708 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H47 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H48 Magnitude, A | 24712 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H48 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H48 Angle | 24714 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H48 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H49 Magnitude, A | 24718 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H49 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H49 Angle | 24720 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H49 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H50 Magnitude, A | 24724 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H50 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H50 Angle | 24726 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H50 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H51 Magnitude, A | 24730 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H51 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H51 Angle | 24732 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H51 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H52 Magnitude, A | 24736 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H52 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H52 Angle | 24738 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H52 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H53 Magnitude, A | 24742 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H53 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H53 Angle | 24744 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H53 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H54 Magnitude, A | 24748 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H54 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H54 Angle | 24750 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H54 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H55 Magnitude, A | 24754 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H55 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H55 Angle | 24756 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H55 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H56 Magnitude, A | 24760 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H56 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H56 Angle | 24762 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H56 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H57 Magnitude, A | 24766 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H57 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H57 Angle | 24768 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H57 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H58 Magnitude, A | 24772 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H58 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H58 Angle | 24774 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H58 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H59 Magnitude, A | 24778 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H59 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H59 Angle | 24780 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H59 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H60 Magnitude, A | 24784 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H60 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H60 Angle | 24786 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H60 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H61 Magnitude, A | 24790 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H61 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H61 Angle | 24792 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H61 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H62 Magnitude, A | 24796 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H62 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H62 Angle | 24798 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H62 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current A, H63 Magnitude, A | 24802 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H63 Mag 3s | A | PQM | PDMD_I1_H1_MAG_3S
Current A, H63 Angle | 24804 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H63 Ang 3s | DEGREES | PQM | PDMD_I1_H1_MAG_3S
Current B, H1 Magnitude, A | 24818 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H1 Mag 3s | A | PQM | BASE_PDMD_I2_H1_MAG_3S
Current B, H1 Angle | 24820 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H1 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H2 Magnitude, A | 24824 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H2 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H2 Angle | 24826 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H2 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H3 Magnitude, A | 24830 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H3 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H3 Angle | 24832 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H3 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H4 Magnitude, A | 24836 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H4 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H4 Angle | 24838 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H4 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H5 Magnitude, A | 24842 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H5 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H5 Angle | 24844 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H5 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H6 Magnitude, A | 24848 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H6 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H6 Angle | 24850 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H6 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H7 Magnitude, A | 24854 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H7 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H7 Angle | 24856 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H7 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H8 Magnitude, A | 24860 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H8 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H8 Angle | 24862 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H8 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H9 Magnitude, A | 24866 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H9 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H9 Angle | 24868 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H9 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H10 Magnitude, A | 24872 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H10 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H10 Angle | 24874 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H10 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H11 Magnitude, A | 24878 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H11 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H11 Angle | 24880 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H11 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H12 Magnitude, A | 24884 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H12 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H12 Angle | 24886 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H12 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H13 Magnitude, A | 24890 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H13 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H13 Angle | 24892 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H13 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H14 Magnitude, A | 24896 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H14 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H14 Angle | 24898 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H14 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H15 Magnitude, A | 24902 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H15 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H15 Angle | 24904 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H15 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H16 Magnitude, A | 24908 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H16 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H16 Angle | 24910 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H16 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H17 Magnitude, A | 24914 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H17 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H17 Angle | 24916 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H17 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H18 Magnitude, A | 24920 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H18 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H18 Angle | 24922 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H18 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H19 Magnitude, A | 24926 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H19 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H19 Angle | 24928 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H19 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H20 Magnitude, A | 24932 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H20 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H20 Angle | 24934 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H20 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H21 Magnitude, A | 24938 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H21 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H21 Angle | 24940 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H21 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H22 Magnitude, A | 24944 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H22 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H22 Angle | 24946 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H22 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H23 Magnitude, A | 24950 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H23 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H23 Angle | 24952 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H23 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H24 Magnitude, A | 24956 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H24 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H24 Angle | 24958 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H24 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H25 Magnitude, A | 24962 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H25 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H25 Angle | 24964 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H25 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H26 Magnitude, A | 24968 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H26 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H26 Angle | 24970 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H26 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H27 Magnitude, A | 24974 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H27 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H27 Angle | 24976 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H27 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H28 Magnitude, A | 24980 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H28 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H28 Angle | 24982 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H28 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H29 Magnitude, A | 24986 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H29 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H29 Angle | 24988 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H29 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H30 Magnitude, A | 24992 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H30 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H30 Angle | 24994 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H30 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H31 Magnitude, A | 24998 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H31 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H31 Angle | 25000 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H31 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H32 Magnitude, A | 25004 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H32 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H32 Angle | 25006 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H32 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H33 Magnitude, A | 25010 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H33 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H33 Angle | 25012 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H33 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H34 Magnitude, A | 25016 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H34 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H34 Angle | 25018 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H34 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H35 Magnitude, A | 25022 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H35 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H35 Angle | 25024 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H35 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H36 Magnitude, A | 25028 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H36 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H36 Angle | 25030 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H36 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H37 Magnitude, A | 25034 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H37 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H37 Angle | 25036 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H37 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H38 Magnitude, A | 25040 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H38 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H38 Angle | 25042 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H38 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H39 Magnitude, A | 25046 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H39 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H39 Angle | 25048 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H39 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H40 Magnitude, A | 25052 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H40 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H40 Angle | 25054 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H40 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H41 Magnitude, A | 25058 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H41 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H41 Angle | 25060 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H41 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H42 Magnitude, A | 25064 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H42 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H42 Angle | 25066 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H42 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H43 Magnitude, A | 25070 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H43 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H43 Angle | 25072 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H43 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H44 Magnitude, A | 25076 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H44 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H44 Angle | 25078 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H44 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H45 Magnitude, A | 25082 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H45 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H45 Angle | 25084 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H45 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H46 Magnitude, A | 25088 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H46 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H46 Angle | 25090 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H46 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H47 Magnitude, A | 25094 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H47 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H47 Angle | 25096 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H47 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H48 Magnitude, A | 25100 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H48 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H48 Angle | 25102 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H48 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H49 Magnitude, A | 25106 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H49 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H49 Angle | 25108 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H49 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H50 Magnitude, A | 25112 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H50 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H50 Angle | 25114 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H50 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H51 Magnitude, A | 25118 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H51 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H51 Angle | 25120 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H51 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H52 Magnitude, A | 25124 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H52 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H52 Angle | 25126 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H52 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H53 Magnitude, A | 25130 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H53 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H53 Angle | 25132 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H53 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H54 Magnitude, A | 25136 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H54 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H54 Angle | 25138 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H54 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H55 Magnitude, A | 25142 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H55 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H55 Angle | 25144 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H55 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H56 Magnitude, A | 25148 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H56 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H56 Angle | 25150 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H56 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H57 Magnitude, A | 25154 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H57 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H57 Angle | 25156 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H57 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H58 Magnitude, A | 25160 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H58 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H58 Angle | 25162 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H58 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H59 Magnitude, A | 25166 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H59 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H59 Angle | 25168 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H59 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H60 Magnitude, A | 25172 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H60 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H60 Angle | 25174 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H60 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H61 Magnitude, A | 25178 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H61 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H61 Angle | 25180 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H61 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H62 Magnitude, A | 25184 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H62 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H62 Angle | 25186 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H62 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current B, H63 Magnitude, A | 25190 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H63 Mag 3s | A | PQM | PDMD_I2_H1_MAG_3S
Current B, H63 Angle | 25192 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H63 Ang 3s | DEGREES | PQM | PDMD_I2_H1_MAG_3S
Current C, H1 Magnitude, A | 25206 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H1 Mag 3s | A | PQM | BASE_PDMD_I3_H1_MAG_3S
Current C, H1 Angle | 25208 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H1 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H2 Magnitude, A | 25212 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H2 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H2 Angle | 25214 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H2 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H3 Magnitude, A | 25218 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H3 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H3 Angle | 25220 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H3 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H4 Magnitude, A | 25224 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H4 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H4 Angle | 25226 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H4 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H5 Magnitude, A | 25230 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H5 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H5 Angle | 25232 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H5 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H6 Magnitude, A | 25236 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H6 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H6 Angle | 25238 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H6 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H7 Magnitude, A | 25242 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H7 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H7 Angle | 25244 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H7 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H8 Magnitude, A | 25248 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H8 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H8 Angle | 25250 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H8 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H9 Magnitude, A | 25254 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H9 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H9 Angle | 25256 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H9 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H10 Magnitude, A | 25260 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H10 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H10 Angle | 25262 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H10 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H11 Magnitude, A | 25266 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H11 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H11 Angle | 25268 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H11 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H12 Magnitude, A | 25272 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H12 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H12 Angle | 25274 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H12 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H13 Magnitude, A | 25278 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H13 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H13 Angle | 25280 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H13 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H14 Magnitude, A | 25284 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H14 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H14 Angle | 25286 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H14 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H15 Magnitude, A | 25290 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H15 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H15 Angle | 25292 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H15 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H16 Magnitude, A | 25296 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H16 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H16 Angle | 25298 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H16 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H17 Magnitude, A | 25302 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H17 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H17 Angle | 25304 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H17 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H18 Magnitude, A | 25308 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H18 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H18 Angle | 25310 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H18 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H19 Magnitude, A | 25314 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H19 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H19 Angle | 25316 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H19 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H20 Magnitude, A | 25320 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H20 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H20 Angle | 25322 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H20 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H21 Magnitude, A | 25326 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H21 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H21 Angle | 25328 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H21 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H22 Magnitude, A | 25332 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H22 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H22 Angle | 25334 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H22 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H23 Magnitude, A | 25338 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H23 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H23 Angle | 25340 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H23 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H24 Magnitude, A | 25344 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H24 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H24 Angle | 25346 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H24 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H25 Magnitude, A | 25350 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H25 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H25 Angle | 25352 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H25 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H26 Magnitude, A | 25356 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H26 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H26 Angle | 25358 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H26 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H27 Magnitude, A | 25362 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H27 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H27 Angle | 25364 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H27 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H28 Magnitude, A | 25368 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H28 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H28 Angle | 25370 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H28 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H29 Magnitude, A | 25374 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H29 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H29 Angle | 25376 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H29 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H30 Magnitude, A | 25380 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H30 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H30 Angle | 25382 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H30 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H31 Magnitude, A | 25386 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H31 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H31 Angle | 25388 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H31 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H32 Magnitude, A | 25392 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H32 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H32 Angle | 25394 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H32 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H33 Magnitude, A | 25398 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H33 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H33 Angle | 25400 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H33 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H34 Magnitude, A | 25404 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H34 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H34 Angle | 25406 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H34 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H35 Magnitude, A | 25410 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H35 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H35 Angle | 25412 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H35 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H36 Magnitude, A | 25416 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H36 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H36 Angle | 25418 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H36 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H37 Magnitude, A | 25422 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H37 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H37 Angle | 25424 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H37 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H38 Magnitude, A | 25428 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H38 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H38 Angle | 25430 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H38 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H39 Magnitude, A | 25434 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H39 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H39 Angle | 25436 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H39 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H40 Magnitude, A | 25440 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H40 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H40 Angle | 25442 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H40 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H41 Magnitude, A | 25446 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H41 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H41 Angle | 25448 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H41 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H42 Magnitude, A | 25452 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H42 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H42 Angle | 25454 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H42 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H43 Magnitude, A | 25458 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H43 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H43 Angle | 25460 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H43 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H44 Magnitude, A | 25464 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H44 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H44 Angle | 25466 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H44 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H45 Magnitude, A | 25470 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H45 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H45 Angle | 25472 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H45 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H46 Magnitude, A | 25476 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H46 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H46 Angle | 25478 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H46 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H47 Magnitude, A | 25482 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H47 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H47 Angle | 25484 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H47 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H48 Magnitude, A | 25488 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H48 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H48 Angle | 25490 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H48 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H49 Magnitude, A | 25494 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H49 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H49 Angle | 25496 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H49 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H50 Magnitude, A | 25500 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H50 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H50 Angle | 25502 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H50 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H51 Magnitude, A | 25506 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H51 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H51 Angle | 25508 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H51 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H52 Magnitude, A | 25512 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H52 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H52 Angle | 25514 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H52 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H53 Magnitude, A | 25518 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H53 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H53 Angle | 25520 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H53 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H54 Magnitude, A | 25524 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H54 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H54 Angle | 25526 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H54 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H55 Magnitude, A | 25530 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H55 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H55 Angle | 25532 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H55 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H56 Magnitude, A | 25536 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H56 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H56 Angle | 25538 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H56 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H57 Magnitude, A | 25542 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H57 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H57 Angle | 25544 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H57 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H58 Magnitude, A | 25548 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H58 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H58 Angle | 25550 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H58 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H59 Magnitude, A | 25554 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H59 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H59 Angle | 25556 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H59 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H60 Magnitude, A | 25560 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H60 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H60 Angle | 25562 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H60 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H61 Magnitude, A | 25566 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H61 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H61 Angle | 25568 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H61 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H62 Magnitude, A | 25572 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H62 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H62 Angle | 25574 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H62 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current C, H63 Magnitude, A | 25578 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H63 Mag 3s | A | PQM | PDMD_I3_H1_MAG_3S
Current C, H63 Angle | 25580 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H63 Ang 3s | DEGREES | PQM | PDMD_I3_H1_MAG_3S
Current N, H1 Magnitude, A | 25594 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H1 Mag 3s | A | PQM | BASE_PDMD_I4_H1_MAG_3S
Current N, H1 Angle | 25596 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H1 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H2 Magnitude, A | 25600 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H2 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H2 Angle | 25602 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H2 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H3 Magnitude, A | 25606 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H3 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H3 Angle | 25608 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H3 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H4 Magnitude, A | 25612 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H4 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H4 Angle | 25614 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H4 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H5 Magnitude, A | 25618 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H5 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H5 Angle | 25620 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H5 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H6 Magnitude, A | 25624 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H6 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H6 Angle | 25626 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H6 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H7 Magnitude, A | 25630 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H7 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H7 Angle | 25632 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H7 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H8 Magnitude, A | 25636 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H8 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H8 Angle | 25638 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H8 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H9 Magnitude, A | 25642 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H9 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H9 Angle | 25644 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H9 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H10 Magnitude, A | 25648 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H10 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H10 Angle | 25650 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H10 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H11 Magnitude, A | 25654 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H11 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H11 Angle | 25656 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H11 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H12 Magnitude, A | 25660 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H12 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H12 Angle | 25662 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H12 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H13 Magnitude, A | 25666 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H13 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H13 Angle | 25668 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H13 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H14 Magnitude, A | 25672 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H14 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H14 Angle | 25674 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H14 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H15 Magnitude, A | 25678 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H15 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H15 Angle | 25680 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H15 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H16 Magnitude, A | 25684 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H16 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H16 Angle | 25686 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H16 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H17 Magnitude, A | 25690 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H17 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H17 Angle | 25692 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H17 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H18 Magnitude, A | 25696 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H18 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H18 Angle | 25698 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H18 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H19 Magnitude, A | 25702 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H19 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H19 Angle | 25704 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H19 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H20 Magnitude, A | 25708 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H20 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H20 Angle | 25710 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H20 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H21 Magnitude, A | 25714 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H21 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H21 Angle | 25716 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H21 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H22 Magnitude, A | 25720 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H22 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H22 Angle | 25722 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H22 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H23 Magnitude, A | 25726 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H23 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H23 Angle | 25728 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H23 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H24 Magnitude, A | 25732 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H24 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H24 Angle | 25734 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H24 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H25 Magnitude, A | 25738 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H25 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H25 Angle | 25740 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H25 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H26 Magnitude, A | 25744 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H26 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H26 Angle | 25746 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H26 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H27 Magnitude, A | 25750 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H27 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H27 Angle | 25752 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H27 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H28 Magnitude, A | 25756 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H28 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H28 Angle | 25758 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H28 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H29 Magnitude, A | 25762 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H29 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H29 Angle | 25764 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H29 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H30 Magnitude, A | 25768 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H30 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H30 Angle | 25770 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H30 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H31 Magnitude, A | 25774 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H31 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H31 Angle | 25776 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H31 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H32 Magnitude, A | 25780 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H32 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H32 Angle | 25782 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H32 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H33 Magnitude, A | 25786 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H33 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H33 Angle | 25788 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H33 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H34 Magnitude, A | 25792 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H34 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H34 Angle | 25794 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H34 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H35 Magnitude, A | 25798 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H35 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H35 Angle | 25800 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H35 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H36 Magnitude, A | 25804 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H36 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H36 Angle | 25806 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H36 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H37 Magnitude, A | 25810 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H37 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H37 Angle | 25812 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H37 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H38 Magnitude, A | 25816 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H38 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H38 Angle | 25818 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H38 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H39 Magnitude, A | 25822 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H39 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H39 Angle | 25824 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H39 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H40 Magnitude, A | 25828 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H40 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H40 Angle | 25830 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H40 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H41 Magnitude, A | 25834 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H41 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H41 Angle | 25836 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H41 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H42 Magnitude, A | 25840 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H42 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H42 Angle | 25842 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H42 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H43 Magnitude, A | 25846 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H43 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H43 Angle | 25848 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H43 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H44 Magnitude, A | 25852 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H44 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H44 Angle | 25854 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H44 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H45 Magnitude, A | 25858 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H45 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H45 Angle | 25860 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H45 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H46 Magnitude, A | 25864 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H46 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H46 Angle | 25866 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H46 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H47 Magnitude, A | 25870 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H47 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H47 Angle | 25872 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H47 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H48 Magnitude, A | 25876 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H48 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H48 Angle | 25878 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H48 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H49 Magnitude, A | 25882 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H49 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H49 Angle | 25884 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H49 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H50 Magnitude, A | 25888 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H50 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H50 Angle | 25890 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H50 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H51 Magnitude, A | 25894 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H51 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H51 Angle | 25896 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H51 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H52 Magnitude, A | 25900 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H52 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H52 Angle | 25902 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H52 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H53 Magnitude, A | 25906 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H53 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H53 Angle | 25908 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H53 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H54 Magnitude, A | 25912 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H54 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H54 Angle | 25914 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H54 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H55 Magnitude, A | 25918 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H55 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H55 Angle | 25920 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H55 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H56 Magnitude, A | 25924 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H56 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H56 Angle | 25926 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H56 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H57 Magnitude, A | 25930 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H57 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H57 Angle | 25932 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H57 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H58 Magnitude, A | 25936 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H58 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H58 Angle | 25938 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H58 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H59 Magnitude, A | 25942 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H59 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H59 Angle | 25944 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H59 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H60 Magnitude, A | 25948 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H60 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H60 Angle | 25950 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H60 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H61 Magnitude, A | 25954 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H61 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H61 Angle | 25956 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H61 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H62 Magnitude, A | 25960 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H62 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H62 Angle | 25962 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H62 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current N, H63 Magnitude, A | 25966 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 H63 Mag 3s | A | PQM | PDMD_I4_H1_MAG_3S
Current N, H63 Angle | 25968 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I4 H63 Ang 3s | DEGREES | PQM | PDMD_I4_H1_MAG_3S
Current G, H1 Magnitude, A | 25982 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H1 Mag 3s | A | PQM | BASE_PDMD_I5_H1_MAG_3S
Current G, H1 Angle | 25984 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H1 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H2 Magnitude, A | 25988 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H2 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H2 Angle | 25990 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H2 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H3 Magnitude, A | 25994 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H3 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H3 Angle | 25996 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H3 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H4 Magnitude, A | 26000 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H4 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H4 Angle | 26002 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H4 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H5 Magnitude, A | 26006 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H5 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H5 Angle | 26008 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H5 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H6 Magnitude, A | 26012 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H6 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H6 Angle | 26014 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H6 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H7 Magnitude, A | 26018 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H7 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H7 Angle | 26020 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H7 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H8 Magnitude, A | 26024 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H8 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H8 Angle | 26026 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H8 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H9 Magnitude, A | 26030 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H9 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H9 Angle | 26032 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H9 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H10 Magnitude, A | 26036 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H10 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H10 Angle | 26038 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H10 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H11 Magnitude, A | 26042 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H11 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H11 Angle | 26044 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H11 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H12 Magnitude, A | 26048 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H12 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H12 Angle | 26050 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H12 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H13 Magnitude, A | 26054 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H13 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H13 Angle | 26056 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H13 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H14 Magnitude, A | 26060 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H14 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H14 Angle | 26062 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H14 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H15 Magnitude, A | 26066 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H15 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H15 Angle | 26068 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H15 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H16 Magnitude, A | 26072 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H16 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H16 Angle | 26074 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H16 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H17 Magnitude, A | 26078 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H17 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H17 Angle | 26080 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H17 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H18 Magnitude, A | 26084 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H18 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H18 Angle | 26086 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H18 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H19 Magnitude, A | 26090 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H19 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H19 Angle | 26092 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H19 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H20 Magnitude, A | 26096 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H20 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H20 Angle | 26098 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H20 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H21 Magnitude, A | 26102 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H21 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H21 Angle | 26104 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H21 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H22 Magnitude, A | 26108 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H22 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H22 Angle | 26110 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H22 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H23 Magnitude, A | 26114 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H23 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H23 Angle | 26116 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H23 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H24 Magnitude, A | 26120 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H24 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H24 Angle | 26122 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H24 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H25 Magnitude, A | 26126 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H25 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H25 Angle | 26128 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H25 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H26 Magnitude, A | 26132 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H26 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H26 Angle | 26134 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H26 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H27 Magnitude, A | 26138 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H27 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H27 Angle | 26140 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H27 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H28 Magnitude, A | 26144 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H28 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H28 Angle | 26146 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H28 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H29 Magnitude, A | 26150 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H29 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H29 Angle | 26152 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H29 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H30 Magnitude, A | 26156 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H30 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H30 Angle | 26158 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H30 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H31 Magnitude, A | 26162 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H31 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H31 Angle | 26164 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H31 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H32 Magnitude, A | 26168 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H32 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H32 Angle | 26170 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H32 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H33 Magnitude, A | 26174 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H33 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H33 Angle | 26176 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H33 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H34 Magnitude, A | 26180 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H34 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H34 Angle | 26182 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H34 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H35 Magnitude, A | 26186 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H35 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H35 Angle | 26188 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H35 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H36 Magnitude, A | 26192 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H36 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H36 Angle | 26194 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H36 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H37 Magnitude, A | 26198 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H37 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H37 Angle | 26200 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H37 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H38 Magnitude, A | 26204 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H38 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H38 Angle | 26206 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H38 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H39 Magnitude, A | 26210 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H39 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H39 Angle | 26212 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H39 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H40 Magnitude, A | 26216 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H40 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H40 Angle | 26218 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H40 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H41 Magnitude, A | 26222 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H41 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H41 Angle | 26224 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H41 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H42 Magnitude, A | 26228 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H42 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H42 Angle | 26230 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H42 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H43 Magnitude, A | 26234 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H43 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H43 Angle | 26236 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H43 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H44 Magnitude, A | 26240 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H44 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H44 Angle | 26242 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H44 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H45 Magnitude, A | 26246 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H45 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H45 Angle | 26248 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H45 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H46 Magnitude, A | 26252 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H46 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H46 Angle | 26254 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H46 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H47 Magnitude, A | 26258 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H47 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H47 Angle | 26260 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H47 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H48 Magnitude, A | 26264 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H48 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H48 Angle | 26266 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H48 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H49 Magnitude, A | 26270 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H49 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H49 Angle | 26272 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H49 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H50 Magnitude, A | 26276 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H50 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H50 Angle | 26278 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H50 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H51 Magnitude, A | 26282 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H51 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H51 Angle | 26284 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H51 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H52 Magnitude, A | 26288 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H52 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H52 Angle | 26290 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H52 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H53 Magnitude, A | 26294 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H53 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H53 Angle | 26296 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H53 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H54 Magnitude, A | 26300 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H54 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H54 Angle | 26302 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H54 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H55 Magnitude, A | 26306 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H55 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H55 Angle | 26308 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H55 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H56 Magnitude, A | 26312 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H56 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H56 Angle | 26314 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H56 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H57 Magnitude, A | 26318 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H57 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H57 Angle | 26320 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H57 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H58 Magnitude, A | 26324 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H58 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H58 Angle | 26326 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H58 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H59 Magnitude, A | 26330 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H59 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H59 Angle | 26332 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H59 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H60 Magnitude, A | 26336 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H60 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H60 Angle | 26338 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H60 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H61 Magnitude, A | 26342 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H61 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H61 Angle | 26344 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H61 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H62 Magnitude, A | 26348 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H62 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H62 Angle | 26350 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H62 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Current G, H63 Magnitude, A | 26354 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 H63 Mag 3s | A | PQM | PDMD_I5_H1_MAG_3S
Current G, H63 Angle | 26356 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I5 H63 Ang 3s | DEGREES | PQM | PDMD_I5_H1_MAG_3S
Min Current A | 27218 | 2 | FLOAT32 | A | R/O | numeric | --- | I a mn | CT_A | STM | None
Min Current B | 27220 | 2 | FLOAT32 | A | R/O | numeric | --- | I b mn | CT_A | STM | None
Min Current C | 27222 | 2 | FLOAT32 | A | R/O | numeric | --- | I c mn | CT_A | STM | None
Min Current N | 27224 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 mn | CT_A | STM | None
Min Current G | 27226 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 mn | CT_A | STM | None
Min Current Avg | 27228 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg mn | CT_A | STM | None
Min Voltage A-B | 27238 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ab mn | PT_V | STM | None
Min Voltage B-C | 27240 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll bc mn | PT_V | STM | None
Min Voltage C-A | 27242 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ca mn | PT_V | STM | None
Min Voltage L-L Avg | 27244 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll avg mn | PT_V | STM | None
Min Voltage A-N | 27246 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln a mn | PT_V | STM | None
Min Voltage B-N | 27248 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln b mn | PT_V | STM | None
Min Voltage C-N | 27250 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln c mn | PT_V | STM | None
Min Voltage L-N Avg | 27254 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln avg mn | PT_V | STM | None
Min Voltage Unbalance L-N Worst | 27270 | 2 | FLOAT32 | --- | R/O | numeric | --- | V unbal mn | PERCENT | STM | None
Min Active Power Total | 27278 | 2 | FLOAT32 | W | R/O | numeric | --- | kW tot mn | PT_CT_KW | STM | None
Min Reactive Power Total | 27286 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR tot mn | PT_CT_KVAR | STM | None
Min Apparent Power Total | 27294 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA tot mn | PT_CT_KVA | STM | None
Min Power Factor Lagging | 27322 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag mn | PF | STM | None
Min Power Factor Leading | 27324 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead mn | PF | STM | None
Min THD Current A | 27338 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 THD mn | PERCENT | STM | None
Min THD Current B | 27340 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 THD mn | PERCENT | STM | None
Min THD Current C | 27342 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 THD mn | PERCENT | STM | None
Min THD Current N | 27344 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 THD mn | PERCENT | STM | None
Min THD Voltage A-N | 27368 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 THD mn | PERCENT | STM | None
Min THD Voltage B-N | 27370 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 THD mn | PERCENT | STM | None
Min THD Voltage C-N | 27372 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 THD mn | PERCENT | STM | None
Min Frequency | 27616 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Freq mn | HZ | STM | None
Current A Low | 27644 | 2 | FLOAT32 | A | R/O | numeric | --- | I a low | CT_A | STM | None
Current B Low | 27646 | 2 | FLOAT32 | A | R/O | numeric | --- | I b low | CT_A | STM | None
Current C Low | 27648 | 2 | FLOAT32 | A | R/O | numeric | --- | I c low | CT_A | STM | None
Current N Low | 27650 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 low | CT_A | STM | None
Current Avg Low | 27652 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg low | CT_A | STM | None
Voltage A-B Low | 27654 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ab low | PT_V | STM | None
Voltage B-C Low | 27656 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll bc low | PT_V | STM | None
Voltage C-A Low | 27658 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ca low | PT_V | STM | None
Voltage L-L Avg Low | 27660 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll avg low | PT_V | STM | None
Voltage Unbalance Low | 27670 | 2 | FLOAT32 | --- | R/O | numeric | --- | V unbal low | PERCENT | STM | None
Active Power Low | 27672 | 2 | FLOAT32 | W | R/O | numeric | --- | kW tot low | PT_CT_KW | STM | None
Reactive Power Low | 27674 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR tot low | PT_CT_KVAR | STM | None
Apparent Power Low | 27676 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA tot low | PT_CT_KVA | STM | None
Power Factor Lagging Low | 27678 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag low | PF | STM | None
Power Factor Leading Low | 27680 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead low | PF | STM | None
Frequency Low | 27682 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Freq low | HZ | STM | None
Max Current A | 27694 | 2 | FLOAT32 | A | R/O | numeric | --- | I a mx | CT_A | STM | None
Max Current B | 27696 | 2 | FLOAT32 | A | R/O | numeric | --- | I b mx | CT_A | STM | None
Max Current C | 27698 | 2 | FLOAT32 | A | R/O | numeric | --- | I c mx | CT_A | STM | None
Max Current N | 27700 | 2 | FLOAT32 | A | R/O | numeric | --- | I4 mx | CT_A | STM | None
Max Current G | 27702 | 2 | FLOAT32 | A | R/O | numeric | --- | I5 mx | CT_A | STM | None
Max Current Avg | 27704 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg mx | CT_A | STM | None
Max Voltage A-B | 27714 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ab mx | PT_V | STM | None
Max Voltage B-C | 27716 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll bc mx | PT_V | STM | None
Max Voltage C-A | 27718 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ca mx | PT_V | STM | None
Max Voltage L-L Avg | 27720 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll avg mx | PT_V | STM | None
Max Voltage A-N | 27722 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln a mx | PT_V | STM | None
Max Voltage B-N | 27724 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln b mx | PT_V | STM | None
Max Voltage C-N | 27726 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln c mx | PT_V | STM | None
Max Voltage L-N Avg | 27730 | 2 | FLOAT32 | V | R/O | numeric | --- | Vln avg mx | PT_V | STM | None
Max Voltage Unbalance L-N Worst | 27746 | 2 | FLOAT32 | --- | R/O | numeric | --- | V unbal mx | PERCENT | STM | None
Max Active Power Total | 27754 | 2 | FLOAT32 | W | R/O | numeric | --- | kW tot mx | PT_CT_KW | STM | None
Max Reactive Power Total | 27762 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR tot mx | PT_CT_KVAR | STM | None
Max Apparent Power Total | 27770 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA tot mx | PT_CT_KVA | STM | None
Max Power Factor Lagging | 27798 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag mx | PF | STM | None
Max Power Factor Leading | 27800 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead mx | PF | STM | None
Max THD Current A | 27814 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 THD mx | PERCENT | STM | None
Max THD Current B | 27816 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 THD mx | PERCENT | STM | None
Max THD Current C | 27818 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 THD mx | PERCENT | STM | None
Max THD Current N | 27820 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 THD mx | PERCENT | STM | None
Max THD Voltage A-N | 27844 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 THD mx | PERCENT | STM | None
Max THD Voltage B-N | 27846 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 THD mx | PERCENT | STM | None
Max THD Voltage C-N | 27848 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 THD mx | PERCENT | STM | None
Max Frequency | 28092 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Freq mx | HZ | STM | None
Current A High | 28120 | 2 | FLOAT32 | A | R/O | numeric | --- | I a high | CT_A | STM | None
Current B High | 28122 | 2 | FLOAT32 | A | R/O | numeric | --- | I b high | CT_A | STM | None
Current C High | 28124 | 2 | FLOAT32 | A | R/O | numeric | --- | I c high | CT_A | STM | None
Current N High | 28126 | 2 | FLOAT32 | A | R/O | numeric | --- | I 4 high | CT_A | STM | None
Current Avg High | 28128 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg high | A | STM | None
Voltage A-B High | 28130 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ab high | PT_V | STM | None
Voltage B-C High | 28132 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll bc high | PT_V | STM | None
Voltage C-A High | 28134 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ca high | PT_V | STM | None
Voltage L-L Avg High | 28136 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll avg high | PT_V | STM | None
Voltage Unbalance High | 28146 | 2 | FLOAT32 | --- | R/O | numeric | --- | V unbal high | PERCENT | STM | None
THD Current A High | 28148 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 THD high | PERCENT | STM | None
THD Current B High | 28150 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 THD high | PERCENT | STM | None
THD Current C High | 28152 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 THD high | PERCENT | STM | None
THD Current N High | 28154 | 2 | FLOAT32 | --- | R/O | numeric | --- | I4 THD high | PERCENT | STM | None
THD Voltage V1 High | 28156 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 THD high | PERCENT | STM | None
THD Voltage V2 High | 28158 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 THD high | PERCENT | STM | None
THD Voltage V3 High | 28160 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 THD high | PERCENT | STM | None
Active Power High | 28162 | 2 | FLOAT32 | W | R/O | numeric | --- | kW tot high | PT_CT_KW | STM | None
Reactive Power High | 28164 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR tot high | PT_CT_KVAR | STM | None
Apparent Power High | 28166 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA tot high | PT_CT_KVA | STM | None
Power Factor Lagging High | 28168 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag high | PF | STM | None
Power Factor Leading High | 28170 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead high | PF | STM | None
Frequency High | 28172 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Freq high | HZ | STM | None
Current A K Factor High | 28174 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 K Fac high | NONE | STM | None
Current B K Factor High | 28176 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 K Fac high | NONE | STM | None
Current C K Factor High | 28178 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 K Fac high | NONE | STM | None
Current A Mean | 28180 | 2 | FLOAT32 | A | R/O | numeric | --- | I a mean | CT_A | STM | None
Current B Mean | 28182 | 2 | FLOAT32 | A | R/O | numeric | --- | I b mean | CT_A | STM | None
Current C Mean | 28184 | 2 | FLOAT32 | A | R/O | numeric | --- | I c mean | CT_A | STM | None
Current N Mean | 28186 | 2 | FLOAT32 | A | R/O | numeric | --- | I 4 mean | CT_A | STM | None
Current Avg Mean | 28188 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg mean | CT_A | STM | None
Voltage A-B Mean | 28190 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ab mean | PT_V | STM | None
Voltage B-C Mean | 28192 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll bc mean | PT_V | STM | None
Voltage C-A Mean | 28194 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll ca mean | PT_V | STM | None
Voltage L-L Avg Mean | 28196 | 2 | FLOAT32 | V | R/O | numeric | --- | Vll avg mean | PT_V | STM | None
Voltage Unbalance Mean | 28206 | 2 | FLOAT32 | --- | R/O | numeric | --- | V unbal mean | PERCENT | STM | None
Active Power Mean | 28208 | 2 | FLOAT32 | W | R/O | numeric | --- | kW tot mean | PT_CT_KW | STM | None
Reactive Power Mean | 28210 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR tot mean | PT_CT_KVAR | STM | None
Apparent Power Mean | 28212 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA tot mean | PT_CT_KVA | STM | None
Power Factor Lagging Mean | 28214 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lag mean | PF | STM | None
Power Factor Leading Mean | 28216 | 2 | FLOAT32 | --- | R/O | numeric | --- | PF lead mean | PF | STM | None
Frequency Mean | 28218 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Freq mean | HZ | STM | None
Block Demand Current A Subinterval Duration | 29880 | 1 | INT16U | seconds | R/O | numeric | --- | I a sd Sub Intvl | NONE | DEM | PDMD_I_A_SD
Block Demand Current A # Subintervals | 29881 | 1 | INT16U | --- | R/O | numeric | --- | I a sd #SubIntvls | NONE | DEM | PDMD_I_A_SD
Block Demand Current A Pred Resp | 29882 | 1 | INT16U | --- | R/O | numeric | --- | I a sd Pred Resp | NONE | DEM | PDMD_I_A_SD
Block Demand Current A Update Rate | 29883 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | I a sd Update Rate | NONE | DEM | PDMD_I_A_SD
Current A Last Demand | 29884 | 2 | FLOAT32 | A | R/O | numeric | --- | I a sd | A | DEM | BASE_PDMD_I_A_SD
Current A Predicted Demand | 29886 | 2 | FLOAT32 | A | R/O | numeric | --- | I a sd pred | A | DEM | PDMD_I_A_SD
Current A Peak Demand | 29888 | 6 | TIMESTAMPED_FLOAT32 | A | R/O | numeric | --- | I a sd mx | A | DEM | None
Block Demand Current B Subinterval Duration | 29894 | 1 | INT16U | seconds | R/O | numeric | --- | I b sd Sub Intvl | NONE | DEM | PDMD_I_B_SD
Block Demand Current B # Subintervals | 29895 | 1 | INT16U | --- | R/O | numeric | --- | I b sd #SubIntvls | NONE | DEM | PDMD_I_B_SD
Block Demand Current B Pred Resp | 29896 | 1 | INT16U | --- | R/O | numeric | --- | I b sd Pred Resp | NONE | DEM | PDMD_I_B_SD
Block Demand Current B Update Rate | 29897 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | I b sd Update Rate | NONE | DEM | PDMD_I_B_SD
Current B Last Demand | 29898 | 2 | FLOAT32 | A | R/O | numeric | --- | I b sd | A | DEM | BASE_PDMD_I_B_SD
Current B Predicted Demand | 29900 | 2 | FLOAT32 | A | R/O | numeric | --- | I b sd pred | A | DEM | PDMD_I_B_SD
Current B Peak Demand | 29902 | 6 | TIMESTAMPED_FLOAT32 | A | R/O | numeric | --- | I b sd mx | A | DEM | None
Block Demand Current C Subinterval Duration | 29908 | 1 | INT16U | seconds | R/O | numeric | --- | I c sd Sub Intvl | NONE | DEM | PDMD_I_C_SD
Block Demand Current C # Subintervals | 29909 | 1 | INT16U | --- | R/O | numeric | --- | I c sd #SubIntvls | NONE | DEM | PDMD_I_C_SD
Block Demand Current C Pred Resp | 29910 | 1 | INT16U | --- | R/O | numeric | --- | I c sd Pred Resp | NONE | DEM | PDMD_I_C_SD
Block Demand Current C Update Rate | 29911 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | I c sd Update Rate | NONE | DEM | PDMD_I_C_SD
Current C Last Demand | 29912 | 2 | FLOAT32 | A | R/O | numeric | --- | I c sd | A | DEM | BASE_PDMD_I_C_SD
Current C Predicted Demand | 29914 | 2 | FLOAT32 | A | R/O | numeric | --- | I c sd pred | A | DEM | PDMD_I_C_SD
Current C Peak Demand | 29916 | 6 | TIMESTAMPED_FLOAT32 | A | R/O | numeric | --- | I c sd mx | A | DEM | None
Block Demand Current 4 Subinterval Duration | 29922 | 1 | INT16U | seconds | R/O | numeric | --- | I 4 sd Sub Intvl | NONE | DEM | PDMD_I_4_SD
Block Demand Current 4 # Subintervals | 29923 | 1 | INT16U | --- | R/O | numeric | --- | I 4 sd #SubIntvls | NONE | DEM | PDMD_I_4_SD
Block Demand Current 4 Pred Resp | 29924 | 1 | INT16U | --- | R/O | numeric | --- | I 4 sd Pred Resp | NONE | DEM | PDMD_I_4_SD
Block Demand Current 4 Update Rate | 29925 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | I 4 sd Update Rate | NONE | DEM | PDMD_I_4_SD
Current 4 Last Demand | 29926 | 2 | FLOAT32 | A | R/O | numeric | --- | I 4 sd | A | DEM | BASE_PDMD_I_4_SD
Current 4 Predicted Demand | 29928 | 2 | FLOAT32 | A | R/O | numeric | --- | I 4 sd pred | A | DEM | PDMD_I_4_SD
Current 4 Peak Demand | 29930 | 6 | TIMESTAMPED_FLOAT32 | A | R/O | numeric | --- | I 4 sd mx | A | DEM | None
Block Demand Current Avg Subinterval Duration | 29936 | 1 | INT16U | seconds | R/O | numeric | --- | I avg sd Sub Intvl | NONE | DEM | PDMD_I_AVG_SD
Block Demand Current Avg # Subintervals | 29937 | 1 | INT16U | --- | R/O | numeric | --- | I avg sd #SubIntvls | NONE | DEM | PDMD_I_AVG_SD
Block Demand Current Avg Pred Resp | 29938 | 1 | INT16U | --- | R/O | numeric | --- | I avg sd Pred Resp | NONE | DEM | PDMD_I_AVG_SD
Block Demand Current Avg Update Rate | 29939 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | I avg sd Update Rate | NONE | DEM | PDMD_I_AVG_SD
Current Avg Last Demand | 29940 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg sd | A | DEM | BASE_PDMD_I_AVG_SD
Current Avg Predicted Demand | 29942 | 2 | FLOAT32 | A | R/O | numeric | --- | I avg sd pred | A | DEM | PDMD_I_AVG_SD
Current Avg Peak Demand | 29944 | 6 | TIMESTAMPED_FLOAT32 | A | R/O | numeric | --- | I avg sd mx | A | DEM | None
Block Demand Active Power Subinterval Duration | 29950 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd d-r Sub Intvl | NONE | DEM | PDMD_KW_SD_DEL_REC
Block Demand Active Power # Subintervals | 29951 | 1 | INT16U | --- | R/O | numeric | --- | kW sd d-r #SubIntvls | NONE | DEM | PDMD_KW_SD_DEL_REC
Block Demand Active Power Pred Resp | 29952 | 1 | INT16U | --- | R/O | numeric | --- | kW sd d-r Pred Resp | NONE | DEM | PDMD_KW_SD_DEL_REC
Block Demand Active Power Update Rate | 29953 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd d-r Update Rate | NONE | DEM | PDMD_KW_SD_DEL_REC
Active Power Last Demand | 29954 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd del-rec | PT_CT_KW | DEM | BASE_PDMD_KW_SD_DEL_REC
Active Power Predicted Demand | 29956 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr del-rec | PT_CT_KW | DEM | PDMD_KW_SD_DEL_REC
Active Power Peak Demand | 29958 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx d-r | PT_CT_KW | DEM | None
Block Demand Active Power Del Subinterval Duration | 29964 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd del Sub Intvl | NONE | DEM | PDMD_KW_SD_DEL
Block Demand Active Power Del # Subintervals | 29965 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del #SubIntvls | NONE | DEM | PDMD_KW_SD_DEL
Block Demand Active Power Del Pred Resp | 29966 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del Pred Resp | NONE | DEM | PDMD_KW_SD_DEL
Block Demand Active Power Del Update Rate | 29967 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd del Update Rate | NONE | DEM | PDMD_KW_SD_DEL
Active Power Del Last Demand | 29968 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd del | PT_CT_KW | DEM | BASE_PDMD_KW_SD_DEL
Active Power Del Predicted Demand | 29970 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr del | PT_CT_KW | DEM | PDMD_KW_SD_DEL
Active Power Del Peak Demand | 29972 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx del | PT_CT_KW | DEM | None
Block Demand Active Power Rec Subinterval Duration | 29978 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd rec Sub Intvl | NONE | DEM | PDMD_KW_SD_REC
Block Demand Active Power Rec # Subintervals | 29979 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec #SubIntvls | NONE | DEM | PDMD_KW_SD_REC
Block Demand Active Power Rec Pred Resp | 29980 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec Pred Resp | NONE | DEM | PDMD_KW_SD_REC
Block Demand Active Power Rec Update Rate | 29981 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd rec Update Rate | NONE | DEM | PDMD_KW_SD_REC
Active Power Rec Last Demand | 29982 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd rec | PT_CT_KW | DEM | BASE_PDMD_KW_SD_REC
Active Power Rec Predicted Demand | 29984 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr rec | PT_CT_KW | DEM | PDMD_KW_SD_REC
Active Power Rec Peak Demand | 29986 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx rec | PT_CT_KW | DEM | None
Block Demand Active Power Total Subinterval Duration | 29992 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd d+r Sub Intvl | NONE | DEM | PDMD_KW_SD_TOT
Block Demand Active Power Total # Subintervals | 29993 | 1 | INT16U | --- | R/O | numeric | --- | kW sd d+r #SubIntvls | NONE | DEM | PDMD_KW_SD_TOT
Block Demand Active Power Total Pred Resp | 29994 | 1 | INT16U | --- | R/O | numeric | --- | kW sd d+r Pred Resp | NONE | DEM | PDMD_KW_SD_TOT
Block Demand Active Power Total Update Rate | 29995 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd d+r Update Rate | NONE | DEM | PDMD_KW_SD_TOT
Active Power Total Last Demand | 29996 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd del+rec | PT_CT_KW | DEM | BASE_PDMD_KW_SD_TOT
Active Power Total Predicted Demand | 29998 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr del+rec | PT_CT_KW | DEM | PDMD_KW_SD_TOT
Active Power Total Peak Demand | 30000 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx d+r | PT_CT_KW | DEM | None
Block Demand Reactive Power Subinterval Duration | 30006 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd d-r Sub Intvl | NONE | DEM | PDMD_KVAR_SD_DEL_REC
Block Demand Reactive Power # Subintervals | 30007 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd d-r #SubIntvls | NONE | DEM | PDMD_KVAR_SD_DEL_REC
Block Demand Reactive Power Pred Resp | 30008 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd d-r Pred Resp | NONE | DEM | PDMD_KVAR_SD_DEL_REC
Block Demand Reactive Power Update Rate | 30009 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd d-r Update Rate | NONE | DEM | PDMD_KVAR_SD_DEL_REC
Reactive Power Last Demand | 30010 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd del-rec | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_DEL_REC
Reactive Power Predicted Demand | 30012 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr del-rec | PT_CT_KVAR | DEM | PDMD_KVAR_SD_DEL_REC
Reactive Power Peak Demand | 30014 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx d-r | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Del Subinterval Duration | 30020 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd del Sub Intvl | NONE | DEM | PDMD_KVAR_SD_DEL
Block Demand Reactive Power Del # Subintervals | 30021 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del #SubIntvls | NONE | DEM | PDMD_KVAR_SD_DEL
Block Demand Reactive Power Del Pred Resp | 30022 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del Pred Resp | NONE | DEM | PDMD_KVAR_SD_DEL
Block Demand Reactive Power Del Update Rate | 30023 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd del Update Rate | NONE | DEM | PDMD_KVAR_SD_DEL
Reactive Power Del Last Demand | 30024 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd del | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_DEL
Reactive Power Del Predicted Demand | 30026 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr del | PT_CT_KVAR | DEM | PDMD_KVAR_SD_DEL
Reactive Power Del Peak Demand | 30028 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx del | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Rec Subinterval Duration | 30034 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd rec Sub Intvl | NONE | DEM | PDMD_KVAR_SD_REC
Block Demand Reactive Power Rec # Subintervals | 30035 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec #SubIntvls | NONE | DEM | PDMD_KVAR_SD_REC
Block Demand Reactive Power Rec Pred Resp | 30036 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec Pred Resp | NONE | DEM | PDMD_KVAR_SD_REC
Block Demand Reactive Power Rec Update Rate | 30037 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd rec Update Rate | NONE | DEM | PDMD_KVAR_SD_REC
Reactive Power Rec Last Demand | 30038 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd rec | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_REC
Reactive Power Rec Predicted Demand | 30040 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr rec | PT_CT_KVAR | DEM | PDMD_KVAR_SD_REC
Reactive Power Rec Peak Demand | 30042 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx rec | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Total Subinterval Duration | 30048 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd d+r Sub Intvl | NONE | DEM | PDMD_KVAR_SD_TOT
Block Demand Reactive Power Total # Subintervals | 30049 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd d+r #SubIntvls | NONE | DEM | PDMD_KVAR_SD_TOT
Block Demand Reactive Power Total Pred Resp | 30050 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd d+r Pred Resp | NONE | DEM | PDMD_KVAR_SD_TOT
Block Demand Reactive Power Total Update Rate | 30051 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd d+r Update Rate | NONE | DEM | PDMD_KVAR_SD_TOT
Reactive Power Total Last Demand | 30052 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd del+rec | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_TOT
Reactive Power Total Predicted Demand | 30054 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr del+rec | PT_CT_KVAR | DEM | PDMD_KVAR_SD_TOT
Reactive Power Total Peak Demand | 30056 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx d+r | PT_CT_KVAR | DEM | None
Block Demand Apparent Power Subinterval Duration | 30062 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd d-r Sub Intvl | NONE | DEM | PDMD_KVA_SD_DEL_REC
Block Demand Apparent Power # Subintervals | 30063 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd d-r #SubIntvls | NONE | DEM | PDMD_KVA_SD_DEL_REC
Block Demand Apparent Power Pred Resp | 30064 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd d-r Pred Resp | NONE | DEM | PDMD_KVA_SD_DEL_REC
Block Demand Apparent Power Update Rate | 30065 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd d-r Update Rate | NONE | DEM | PDMD_KVA_SD_DEL_REC
Apparent Power Last Demand | 30066 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd del-rec | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_DEL_REC
Apparent Power Predicted Demand | 30068 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr del-rec | PT_CT_KVA | DEM | PDMD_KVA_SD_DEL_REC
Apparent Power Peak Demand | 30070 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx d-r | PT_CT_KVA | DEM | None
Block Demand Apparent Power Del Subinterval Duration | 30076 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd del Sub Intvl | NONE | DEM | PDMD_KVA_SD_DEL
Block Demand Apparent Power Del # Subintervals | 30077 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del #SubIntvls | NONE | DEM | PDMD_KVA_SD_DEL
Block Demand Apparent Power Del Pred Resp | 30078 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del Pred Resp | NONE | DEM | PDMD_KVA_SD_DEL
Block Demand Apparent Power Del Update Rate | 30079 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd del Update Rate | NONE | DEM | PDMD_KVA_SD_DEL
Apparent Power Del Last Demand | 30080 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd del | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_DEL
Apparent Power Del Predicted Demand | 30082 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr del | PT_CT_KVA | DEM | PDMD_KVA_SD_DEL
Apparent Power Del Peak Demand | 30084 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx del | PT_CT_KVA | DEM | None
Block Demand Apparent Power Rec Subinterval Duration | 30090 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd rec Sub Intvl | NONE | DEM | PDMD_KVA_SD_REC
Block Demand Apparent Power Rec # Subintervals | 30091 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec #SubIntvls | NONE | DEM | PDMD_KVA_SD_REC
Block Demand Apparent Power Rec Pred Resp | 30092 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec Pred Resp | NONE | DEM | PDMD_KVA_SD_REC
Block Demand Apparent Power Rec Update Rate | 30093 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd rec Update Rate | NONE | DEM | PDMD_KVA_SD_REC
Apparent Power Rec Last Demand | 30094 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd rec | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_REC
Apparent Power Rec Predicted Demand | 30096 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr rec | PT_CT_KVA | DEM | PDMD_KVA_SD_REC
Apparent Power Rec Peak Demand | 30098 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx rec | PT_CT_KVA | DEM | None
Block Demand Apparent Power Total Subinterval Duration | 30104 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd d+r Sub Intvl | NONE | DEM | PDMD_KVA_SD_TOT
Block Demand Apparent Power Total # Subintervals | 30105 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd d+r #SubIntvls | NONE | DEM | PDMD_KVA_SD_TOT
Block Demand Apparent Power Total Pred Resp | 30106 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd d+r Pred Resp | NONE | DEM | PDMD_KVA_SD_TOT
Block Demand Apparent Power Total Update Rate | 30107 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd d+r Update Rate | NONE | DEM | PDMD_KVA_SD_TOT
Apparent Power Total Last Demand | 30108 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd del+rec | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_TOT
Apparent Power Total Predicted Demand | 30110 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr del+rec | PT_CT_KVA | DEM | PDMD_KVA_SD_TOT
Apparent Power Total Peak Demand | 30112 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx d+r | PT_CT_KVA | DEM | None
Block Demand Active Power Del A Subinterval Duration | 30218 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd del A Sub Intvl | NONE | TOM | PDMD_KW_SD_DEL_A
Block Demand Active Power Del A # Subintervals | 30219 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del A #SubIntvls | NONE | TOM | PDMD_KW_SD_DEL_A
Block Demand Active Power Del A Pred Resp | 30220 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del A Pred Resp | NONE | TOM | PDMD_KW_SD_DEL_A
Block Demand Active Power Del A Update Rate | 30221 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd del A Update Rate | NONE | TOM | PDMD_KW_SD_DEL_A
Active Power Del A Last Demand | 30222 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd del A | PT_CT_KW | TOM | BASE_PDMD_KW_SD_DEL_A
Active Power Del A Predicted Demand | 30224 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr del A | PT_CT_KW | TOM | PDMD_KW_SD_DEL_A
Active Power Del A Peak Demand | 30226 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx del A | PT_CT_KW | TOM | None
Block Demand Active Power Del B Subinterval Duration | 30232 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd del B Sub Intvl | NONE | TOM | PDMD_KW_SD_DEL_B
Block Demand Active Power Del B # Subintervals | 30233 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del B #SubIntvls | NONE | TOM | PDMD_KW_SD_DEL_B
Block Demand Active Power Del B Pred Resp | 30234 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del B Pred Resp | NONE | TOM | PDMD_KW_SD_DEL_B
Block Demand Active Power Del B Update Rate | 30235 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd del B Update Rate | NONE | TOM | PDMD_KW_SD_DEL_B
Active Power Del B Last Demand | 30236 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd del B | PT_CT_KW | TOM | BASE_PDMD_KW_SD_DEL_B
Active Power Del B Predicted Demand | 30238 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr del B | PT_CT_KW | TOM | PDMD_KW_SD_DEL_B
Active Power Del B Peak Demand | 30240 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx del B | PT_CT_KW | TOM | None
Block Demand Active Power Del C Subinterval Duration | 30246 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd del C Sub Intvl | NONE | TOM | PDMD_KW_SD_DEL_C
Block Demand Active Power Del C # Subintervals | 30247 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del C #SubIntvls | NONE | TOM | PDMD_KW_SD_DEL_C
Block Demand Active Power Del C Pred Resp | 30248 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del C Pred Resp | NONE | TOM | PDMD_KW_SD_DEL_C
Block Demand Active Power Del C Update Rate | 30249 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd del C Update Rate | NONE | TOM | PDMD_KW_SD_DEL_C
Active Power Del C Last Demand | 30250 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd del C | PT_CT_KW | TOM | BASE_PDMD_KW_SD_DEL_C
Active Power Del C Predicted Demand | 30252 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr del C | PT_CT_KW | TOM | PDMD_KW_SD_DEL_C
Active Power Del C Peak Demand | 30254 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx del C | PT_CT_KW | TOM | None
Block Demand Active Power Del D Subinterval Duration | 30260 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd del D Sub Intvl | NONE | TOM | PDMD_KW_SD_DEL_D
Block Demand Active Power Del D # Subintervals | 30261 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del D #SubIntvls | NONE | TOM | PDMD_KW_SD_DEL_D
Block Demand Active Power Del D Pred Resp | 30262 | 1 | INT16U | --- | R/O | numeric | --- | kW sd del D Pred Resp | NONE | TOM | PDMD_KW_SD_DEL_D
Block Demand Active Power Del D Update Rate | 30263 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd del D Update Rate | NONE | TOM | PDMD_KW_SD_DEL_D
Active Power Del D Last Demand | 30264 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd del D | PT_CT_KW | TOM | BASE_PDMD_KW_SD_DEL_D
Active Power Del D Predicted Demand | 30266 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr del D | PT_CT_KW | TOM | PDMD_KW_SD_DEL_D
Active Power Del D Peak Demand | 30268 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx del D | PT_CT_KW | TOM | None
Block Demand Active Power Rec A Subinterval Duration | 30274 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd rec A Sub Intvl | NONE | TOM | PDMD_KW_SD_REC_A
Block Demand Active Power Rec A # Subintervals | 30275 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec A #SubIntvls | NONE | TOM | PDMD_KW_SD_REC_A
Block Demand Active Power Rec A Pred Resp | 30276 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec A Pred Resp | NONE | TOM | PDMD_KW_SD_REC_A
Block Demand Active Power Rec A Update Rate | 30277 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd rec A Update Rate | NONE | TOM | PDMD_KW_SD_REC_A
Active Power Rec A Last Demand | 30278 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd rec A | PT_CT_KW | TOM | BASE_PDMD_KW_SD_REC_A
Active Power Rec A Predicted Demand | 30280 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr rec A | PT_CT_KW | TOM | PDMD_KW_SD_REC_A
Active Power Rec A Peak Demand | 30282 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx rec A | PT_CT_KW | TOM | None
Block Demand Active Power Rec B Subinterval Duration | 30288 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd rec B Sub Intvl | NONE | TOM | PDMD_KW_SD_REC_B
Block Demand Active Power Rec B # Subintervals | 30289 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec B #SubIntvls | NONE | TOM | PDMD_KW_SD_REC_B
Block Demand Active Power Rec B Pred Resp | 30290 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec B Pred Resp | NONE | TOM | PDMD_KW_SD_REC_B
Block Demand Active Power Rec B Update Rate | 30291 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd rec B Update Rate | NONE | TOM | PDMD_KW_SD_REC_B
Active Power Rec B Last Demand | 30292 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd rec B | PT_CT_KW | TOM | BASE_PDMD_KW_SD_REC_B
Active Power Rec B Predicted Demand | 30294 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr rec B | PT_CT_KW | TOM | PDMD_KW_SD_REC_B
Active Power Rec B Peak Demand | 30296 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx rec B | PT_CT_KW | TOM | None
Block Demand Active Power Rec C Subinterval Duration | 30302 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd rec C Sub Intvl | NONE | TOM | PDMD_KW_SD_REC_C
Block Demand Active Power Rec C # Subintervals | 30303 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec C #SubIntvls | NONE | TOM | PDMD_KW_SD_REC_C
Block Demand Active Power Rec C Pred Resp | 30304 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec C Pred Resp | NONE | TOM | PDMD_KW_SD_REC_C
Block Demand Active Power Rec C Update Rate | 30305 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd rec C Update Rate | NONE | TOM | PDMD_KW_SD_REC_C
Active Power Rec C Last Demand | 30306 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd rec C | PT_CT_KW | TOM | BASE_PDMD_KW_SD_REC_C
Active Power Rec C Predicted Demand | 30308 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr rec C | PT_CT_KW | TOM | PDMD_KW_SD_REC_C
Active Power Rec C Peak Demand | 30310 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx rec C | PT_CT_KW | TOM | None
Block Demand Active Power Rec D Subinterval Duration | 30316 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd rec D Sub Intvl | NONE | TOM | PDMD_KW_SD_REC_D
Block Demand Active Power Rec D # Subintervals | 30317 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec D #SubIntvls | NONE | TOM | PDMD_KW_SD_REC_D
Block Demand Active Power Rec D Pred Resp | 30318 | 1 | INT16U | --- | R/O | numeric | --- | kW sd rec D Pred Resp | NONE | TOM | PDMD_KW_SD_REC_D
Block Demand Active Power Rec D Update Rate | 30319 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd rec D Update Rate | NONE | TOM | PDMD_KW_SD_REC_D
Active Power Rec D Last Demand | 30320 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd rec D | PT_CT_KW | TOM | BASE_PDMD_KW_SD_REC_D
Active Power Rec D Predicted Demand | 30322 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr rec D | PT_CT_KW | TOM | PDMD_KW_SD_REC_D
Active Power Rec D Peak Demand | 30324 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx rec D | PT_CT_KW | TOM | None
Block Demand Reactive Power Del A Subinterval Duration | 30330 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd del A Sub Intvl | NONE | TOM | PDMD_KVAR_SD_DEL_A
Block Demand Reactive Power Del A # Subintervals | 30331 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del A #SubIntvls | NONE | TOM | PDMD_KVAR_SD_DEL_A
Block Demand Reactive Power Del A Pred Resp | 30332 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del A Pred Resp | NONE | TOM | PDMD_KVAR_SD_DEL_A
Block Demand Reactive Power Del A Update Rate | 30333 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd del A Update Rate | NONE | TOM | PDMD_KVAR_SD_DEL_A
Reactive Power Del A Last Demand | 30334 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd del A | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_DEL_A
Reactive Power Del A Predicted Demand | 30336 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr del A | PT_CT_KVAR | TOM | PDMD_KVAR_SD_DEL_A
Reactive Power Del A Peak Demand | 30338 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx d A | PT_CT_KVAR | TOM | None
Block Demand Reactive Power Del B Subinterval Duration | 30344 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd del B Sub Intvl | NONE | TOM | PDMD_KVAR_SD_DEL_B
Block Demand Reactive Power Del B # Subintervals | 30345 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del B #SubIntvls | NONE | TOM | PDMD_KVAR_SD_DEL_B
Block Demand Reactive Power Del B Pred Resp | 30346 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del B Pred Resp | NONE | TOM | PDMD_KVAR_SD_DEL_B
Block Demand Reactive Power Del B Update Rate | 30347 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd del B Update Rate | NONE | TOM | PDMD_KVAR_SD_DEL_B
Reactive Power Del B Last Demand | 30348 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd del B | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_DEL_B
Reactive Power Del B Predicted Demand | 30350 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr del B | PT_CT_KVAR | TOM | PDMD_KVAR_SD_DEL_B
Reactive Power Del B Peak Demand | 30352 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx d B | PT_CT_KVAR | TOM | None
Block Demand Reactive Power Del C Subinterval Duration | 30358 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd del C Sub Intvl | NONE | TOM | PDMD_KVAR_SD_DEL_C
Block Demand Reactive Power Del C # Subintervals | 30359 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del C #SubIntvls | NONE | TOM | PDMD_KVAR_SD_DEL_C
Block Demand Reactive Power Del C Pred Resp | 30360 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del C Pred Resp | NONE | TOM | PDMD_KVAR_SD_DEL_C
Block Demand Reactive Power Del C Update Rate | 30361 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd del C Update Rate | NONE | TOM | PDMD_KVAR_SD_DEL_C
Reactive Power Del C Last Demand | 30362 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd del C | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_DEL_C
Reactive Power Del C Predicted Demand | 30364 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr del C | PT_CT_KVAR | TOM | PDMD_KVAR_SD_DEL_C
Reactive Power Del C Peak Demand | 30366 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx d C | PT_CT_KVAR | TOM | None
Block Demand Reactive Power Del D Subinterval Duration | 30372 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd del D Sub Intvl | NONE | TOM | PDMD_KVAR_SD_DEL_D
Block Demand Reactive Power Del D # Subintervals | 30373 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del D #SubIntvls | NONE | TOM | PDMD_KVAR_SD_DEL_D
Block Demand Reactive Power Del D Pred Resp | 30374 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd del D Pred Resp | NONE | TOM | PDMD_KVAR_SD_DEL_D
Block Demand Reactive Power Del D Update Rate | 30375 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd del D Update Rate | NONE | TOM | PDMD_KVAR_SD_DEL_D
Reactive Power Del D Last Demand | 30376 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd del D | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_DEL_D
Reactive Power Del D Predicted Demand | 30378 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr del D | PT_CT_KVAR | TOM | PDMD_KVAR_SD_DEL_D
Reactive Power Del D Peak Demand | 30380 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx d D | PT_CT_KVAR | TOM | None
Block Demand Reactive Power Rec A Subinterval Duration | 30386 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd rec A Sub Intvl | NONE | TOM | PDMD_KVAR_SD_REC_A
Block Demand Reactive Power Rec A # Subintervals | 30387 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec A #SubIntvls | NONE | TOM | PDMD_KVAR_SD_REC_A
Block Demand Reactive Power Rec A Pred Resp | 30388 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec A Pred Resp | NONE | TOM | PDMD_KVAR_SD_REC_A
Block Demand Reactive Power Rec A Update Rate | 30389 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd rec A Update Rate | NONE | TOM | PDMD_KVAR_SD_REC_A
Reactive Power Rec A Last Demand | 30390 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd rec A | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_REC_A
Reactive Power Rec A Predicted Demand | 30392 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr rec A | PT_CT_KVAR | TOM | PDMD_KVAR_SD_REC_A
Reactive Power Rec A Peak Demand | 30394 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx r A | PT_CT_KVAR | TOM | None
Block Demand Reactive Power Rec B Subinterval Duration | 30400 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd rec B Sub Intvl | NONE | TOM | PDMD_KVAR_SD_REC_B
Block Demand Reactive Power Rec B # Subintervals | 30401 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec B #SubIntvls | NONE | TOM | PDMD_KVAR_SD_REC_B
Block Demand Reactive Power Rec B Pred Resp | 30402 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec B Pred Resp | NONE | TOM | PDMD_KVAR_SD_REC_B
Block Demand Reactive Power Rec B Update Rate | 30403 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd rec B Update Rate | NONE | TOM | PDMD_KVAR_SD_REC_B
Reactive Power Rec B Last Demand | 30404 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd rec B | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_REC_B
Reactive Power Rec B Predicted Demand | 30406 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr rec B | PT_CT_KVAR | TOM | PDMD_KVAR_SD_REC_B
Reactive Power Rec B Peak Demand | 30408 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx r B | PT_CT_KVAR | TOM | None
Block Demand Reactive Power Rec C Subinterval Duration | 30414 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd rec C Sub Intvl | NONE | TOM | PDMD_KVAR_SD_REC_C
Block Demand Reactive Power Rec C # Subintervals | 30415 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec C #SubIntvls | NONE | TOM | PDMD_KVAR_SD_REC_C
Block Demand Reactive Power Rec C Pred Resp | 30416 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec C Pred Resp | NONE | TOM | PDMD_KVAR_SD_REC_C
Block Demand Reactive Power Rec C Update Rate | 30417 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd rec C Update Rate | NONE | TOM | PDMD_KVAR_SD_REC_C
Reactive Power Rec C Last Demand | 30418 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd rec C | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_REC_C
Reactive Power Rec C Predicted Demand | 30420 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr rec C | PT_CT_KVAR | TOM | PDMD_KVAR_SD_REC_C
Reactive Power Rec C Peak Demand | 30422 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx r C | PT_CT_KVAR | TOM | None
Block Demand Reactive Power Rec D Subinterval Duration | 30428 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd rec D Sub Intvl | NONE | TOM | PDMD_KVAR_SD_REC_D
Block Demand Reactive Power Rec D # Subintervals | 30429 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec D #SubIntvls | NONE | TOM | PDMD_KVAR_SD_REC_D
Block Demand Reactive Power Rec D Pred Resp | 30430 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd rec D Pred Resp | NONE | TOM | PDMD_KVAR_SD_REC_D
Block Demand Reactive Power Rec D Update Rate | 30431 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd rec D Update Rate | NONE | TOM | PDMD_KVAR_SD_REC_D
Reactive Power Rec D Last Demand | 30432 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd rec D | PT_CT_KVAR | TOM | BASE_PDMD_KVAR_SD_REC_D
Reactive Power Rec D Predicted Demand | 30434 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr rec D | PT_CT_KVAR | TOM | PDMD_KVAR_SD_REC_D
Reactive Power Rec D Peak Demand | 30436 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx r D | PT_CT_KVAR | TOM | None
Block Demand Apparent Power Del A Subinterval Duration | 30442 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd del A Sub Intvl | NONE | TOM | PDMD_KVA_SD_DEL_A
Block Demand Apparent Power Del A # Subintervals | 30443 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del A #SubIntvls | NONE | TOM | PDMD_KVA_SD_DEL_A
Block Demand Apparent Power Del A Pred Resp | 30444 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del A Pred Resp | NONE | TOM | PDMD_KVA_SD_DEL_A
Block Demand Apparent Power Del A Update Rate | 30445 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd del A Update Rate | NONE | TOM | PDMD_KVA_SD_DEL_A
Apparent Power Del A Last Demand | 30446 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd del A | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_DEL_A
Apparent Power Del A Predicted Demand | 30448 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr del A | PT_CT_KVA | TOM | PDMD_KVA_SD_DEL_A
Apparent Power Del A Peak Demand | 30450 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx del A | PT_CT_KVA | TOM | None
Block Demand Apparent Power Del B Subinterval Duration | 30456 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd del B Sub Intvl | NONE | TOM | PDMD_KVA_SD_DEL_B
Block Demand Apparent Power Del B # Subintervals | 30457 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del B #SubIntvls | NONE | TOM | PDMD_KVA_SD_DEL_B
Block Demand Apparent Power Del B Pred Resp | 30458 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del B Pred Resp | NONE | TOM | PDMD_KVA_SD_DEL_B
Block Demand Apparent Power Del B Update Rate | 30459 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd del B Update Rate | NONE | TOM | PDMD_KVA_SD_DEL_B
Apparent Power Del B Last Demand | 30460 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd del B | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_DEL_B
Apparent Power Del B Predicted Demand | 30462 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr del B | PT_CT_KVA | TOM | PDMD_KVA_SD_DEL_B
Apparent Power Del B Peak Demand | 30464 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx del B | PT_CT_KVA | TOM | None
Block Demand Apparent Power Del C Subinterval Duration | 30470 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd del C Sub Intvl | NONE | TOM | PDMD_KVA_SD_DEL_C
Block Demand Apparent Power Del C # Subintervals | 30471 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del C #SubIntvls | NONE | TOM | PDMD_KVA_SD_DEL_C
Block Demand Apparent Power Del C Pred Resp | 30472 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del C Pred Resp | NONE | TOM | PDMD_KVA_SD_DEL_C
Block Demand Apparent Power Del C Update Rate | 30473 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd del C Update Rate | NONE | TOM | PDMD_KVA_SD_DEL_C
Apparent Power Del C Last Demand | 30474 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd del C | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_DEL_C
Apparent Power Del C Predicted Demand | 30476 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr del C | PT_CT_KVA | TOM | PDMD_KVA_SD_DEL_C
Apparent Power Del C Peak Demand | 30478 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx del C | PT_CT_KVA | TOM | None
Block Demand Apparent Power Del D Subinterval Duration | 30484 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd del D Sub Intvl | NONE | TOM | PDMD_KVA_SD_DEL_D
Block Demand Apparent Power Del D # Subintervals | 30485 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del D #SubIntvls | NONE | TOM | PDMD_KVA_SD_DEL_D
Block Demand Apparent Power Del D Pred Resp | 30486 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd del D Pred Resp | NONE | TOM | PDMD_KVA_SD_DEL_D
Block Demand Apparent Power Del D Update Rate | 30487 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd del D Update Rate | NONE | TOM | PDMD_KVA_SD_DEL_D
Apparent Power Del D Last Demand | 30488 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd del D | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_DEL_D
Apparent Power Del D Predicted Demand | 30490 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr del D | PT_CT_KVA | TOM | PDMD_KVA_SD_DEL_D
Apparent Power Del D Peak Demand | 30492 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx del D | PT_CT_KVA | TOM | None
Block Demand Apparent Power Rec A Subinterval Duration | 30498 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd rec A Sub Intvl | NONE | TOM | PDMD_KVA_SD_REC_A
Block Demand Apparent Power Rec A # Subintervals | 30499 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec A #SubIntvls | NONE | TOM | PDMD_KVA_SD_REC_A
Block Demand Apparent Power Rec A Pred Resp | 30500 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec A Pred Resp | NONE | TOM | PDMD_KVA_SD_REC_A
Block Demand Apparent Power Rec A Update Rate | 30501 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd rec A Update Rate | NONE | TOM | PDMD_KVA_SD_REC_A
Apparent Power Rec A Last Demand | 30502 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd rec A | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_REC_A
Apparent Power Rec A Predicted Demand | 30504 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr rec A | PT_CT_KVA | TOM | PDMD_KVA_SD_REC_A
Apparent Power Rec A Peak Demand | 30506 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx rec A | PT_CT_KVA | TOM | None
Block Demand Apparent Power Rec B Subinterval Duration | 30512 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd rec B Sub Intvl | NONE | TOM | PDMD_KVA_SD_REC_B
Block Demand Apparent Power Rec B # Subintervals | 30513 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec B #SubIntvls | NONE | TOM | PDMD_KVA_SD_REC_B
Block Demand Apparent Power Rec B Pred Resp | 30514 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec B Pred Resp | NONE | TOM | PDMD_KVA_SD_REC_B
Block Demand Apparent Power Rec B Update Rate | 30515 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd rec B Update Rate | NONE | TOM | PDMD_KVA_SD_REC_B
Apparent Power Rec B Last Demand | 30516 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd rec B | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_REC_B
Apparent Power Rec B Predicted Demand | 30518 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr rec B | PT_CT_KVA | TOM | PDMD_KVA_SD_REC_B
Apparent Power Rec B Peak Demand | 30520 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx rec B | PT_CT_KVA | TOM | None
Block Demand Apparent Power Rec C Subinterval Duration | 30526 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd rec C Sub Intvl | NONE | TOM | PDMD_KVA_SD_REC_C
Block Demand Apparent Power Rec C # Subintervals | 30527 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec C #SubIntvls | NONE | TOM | PDMD_KVA_SD_REC_C
Block Demand Apparent Power Rec C Pred Resp | 30528 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec C Pred Resp | NONE | TOM | PDMD_KVA_SD_REC_C
Block Demand Apparent Power Rec C Update Rate | 30529 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd rec C Update Rate | NONE | TOM | PDMD_KVA_SD_REC_C
Apparent Power Rec C Last Demand | 30530 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd rec C | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_REC_C
Apparent Power Rec C Predicted Demand | 30532 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr rec C | PT_CT_KVA | TOM | PDMD_KVA_SD_REC_C
Apparent Power Rec C Peak Demand | 30534 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx rec C | PT_CT_KVA | TOM | None
Block Demand Apparent Power Rec D Subinterval Duration | 30540 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd rec D Sub Intvl | NONE | TOM | PDMD_KVA_SD_REC_D
Block Demand Apparent Power Rec D # Subintervals | 30541 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec D #SubIntvls | NONE | TOM | PDMD_KVA_SD_REC_D
Block Demand Apparent Power Rec D Pred Resp | 30542 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd rec D Pred Resp | NONE | TOM | PDMD_KVA_SD_REC_D
Block Demand Apparent Power Rec D Update Rate | 30543 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd rec D Update Rate | NONE | TOM | PDMD_KVA_SD_REC_D
Apparent Power Rec D Last Demand | 30544 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd rec D | PT_CT_KVA | TOM | BASE_PDMD_KVA_SD_REC_D
Apparent Power Rec D Predicted Demand | 30546 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr rec D | PT_CT_KVA | TOM | PDMD_KVA_SD_REC_D
Apparent Power Rec D Peak Demand | 30548 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx rec D | PT_CT_KVA | TOM | None
Block Demand Active Power Q1 Subinterval Duration | 30554 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd Q1 Sub Intvl | NONE | DEM | PDMD_KW_SD_Q1
Block Demand Active Power Q1 # Subintervals | 30555 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q1 #SubIntvls | NONE | DEM | PDMD_KW_SD_Q1
Block Demand Active Power Q1 Pred Resp | 30556 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q1 Pred Resp | NONE | DEM | PDMD_KW_SD_Q1
Block Demand Active Power Q1 Update Rate | 30557 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd Q1 Update Rate | NONE | DEM | PDMD_KW_SD_Q1
Active Power Q1 Last Demand | 30558 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd Q1 | PT_CT_KW | DEM | BASE_PDMD_KW_SD_Q1
Active Power Q1 Predicted Demand | 30560 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr Q1 | PT_CT_KW | DEM | PDMD_KW_SD_Q1
Active Power Q1 Peak Demand | 30562 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx Q1 | PT_CT_KW | DEM | None
Block Demand Active Power Q2 Subinterval Duration | 30568 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd Q2 Sub Intvl | NONE | DEM | PDMD_KW_SD_Q2
Block Demand Active Power Q2 # Subintervals | 30569 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q2 #SubIntvls | NONE | DEM | PDMD_KW_SD_Q2
Block Demand Active Power Q2 Pred Resp | 30570 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q2 Pred Resp | NONE | DEM | PDMD_KW_SD_Q2
Block Demand Active Power Q2 Update Rate | 30571 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd Q2 Update Rate | NONE | DEM | PDMD_KW_SD_Q2
Active Power Q2 Last Demand | 30572 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd Q2 | PT_CT_KW | DEM | BASE_PDMD_KW_SD_Q2
Active Power Q2 Predicted Demand | 30574 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr Q2 | PT_CT_KW | DEM | PDMD_KW_SD_Q2
Active Power Q2 Peak Demand | 30576 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx Q2 | PT_CT_KW | DEM | None
Block Demand Active Power Q3 Subinterval Duration | 30582 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd Q3 Sub Intvl | NONE | DEM | PDMD_KW_SD_Q3
Block Demand Active Power Q3 # Subintervals | 30583 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q3 #SubIntvls | NONE | DEM | PDMD_KW_SD_Q3
Block Demand Active Power Q3 Pred Resp | 30584 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q3 Pred Resp | NONE | DEM | PDMD_KW_SD_Q3
Block Demand Active Power Q3 Update Rate | 30585 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd Q3 Update Rate | NONE | DEM | PDMD_KW_SD_Q3
Active Power Q3 Last Demand | 30586 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd Q3 | PT_CT_KW | DEM | BASE_PDMD_KW_SD_Q3
Active Power Q3 Predicted Demand | 30588 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr Q3 | PT_CT_KW | DEM | PDMD_KW_SD_Q3
Active Power Q3 Peak Demand | 30590 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx Q3 | PT_CT_KW | DEM | None
Block Demand Active Power Q4 Subinterval Duration | 30596 | 1 | INT16U | seconds | R/O | numeric | --- | kW sd Q4 Sub Intvl | NONE | DEM | PDMD_KW_SD_Q4
Block Demand Active Power Q4 # Subintervals | 30597 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q4 #SubIntvls | NONE | DEM | PDMD_KW_SD_Q4
Block Demand Active Power Q4 Pred Resp | 30598 | 1 | INT16U | --- | R/O | numeric | --- | kW sd Q4 Pred Resp | NONE | DEM | PDMD_KW_SD_Q4
Block Demand Active Power Q4 Update Rate | 30599 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kW sd Q4 Update Rate | NONE | DEM | PDMD_KW_SD_Q4
Active Power Q4 Last Demand | 30600 | 2 | FLOAT32 | W | R/O | numeric | --- | kW sd Q4 | PT_CT_KW | DEM | BASE_PDMD_KW_SD_Q4
Active Power Q4 Predicted Demand | 30602 | 2 | FLOAT32 | W | R/O | numeric | --- | kW pr Q4 | PT_CT_KW | DEM | PDMD_KW_SD_Q4
Active Power Q4 Peak Demand | 30604 | 6 | TIMESTAMPED_FLOAT32 | W | R/O | numeric | --- | kW sd mx Q4 | PT_CT_KW | DEM | None
Block Demand Reactive Power Q1 Subinterval Duration | 30610 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd Q1 Sub Intvl | NONE | DEM | PDMD_KVAR_SD_Q1
Block Demand Reactive Power Q1 # Subintervals | 30611 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q1 #SubIntvls | NONE | DEM | PDMD_KVAR_SD_Q1
Block Demand Reactive Power Q1 Pred Resp | 30612 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q1 Pred Resp | NONE | DEM | PDMD_KVAR_SD_Q1
Block Demand Reactive Power Q1 Update Rate | 30613 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd Q1 Update Rate | NONE | DEM | PDMD_KVAR_SD_Q1
Reactive Power Q1 Last Demand | 30614 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd Q1 | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_Q1
Reactive Power Q1 Predicted Demand | 30616 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr Q1 | PT_CT_KVAR | DEM | PDMD_KVAR_SD_Q1
Reactive Power Q1 Peak Demand | 30618 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx Q1 | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Q2 Subinterval Duration | 30624 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd Q2 Sub Intvl | NONE | DEM | PDMD_KVAR_SD_Q2
Block Demand Reactive Power Q2 # Subintervals | 30625 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q2 #SubIntvls | NONE | DEM | PDMD_KVAR_SD_Q2
Block Demand Reactive Power Q2 Pred Resp | 30626 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q2 Pred Resp | NONE | DEM | PDMD_KVAR_SD_Q2
Block Demand Reactive Power Q2 Update Rate | 30627 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd Q2 Update Rate | NONE | DEM | PDMD_KVAR_SD_Q2
Reactive Power Q2 Last Demand | 30628 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd Q2 | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_Q2
Reactive Power Q2 Predicted Demand | 30630 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr Q2 | PT_CT_KVAR | DEM | PDMD_KVAR_SD_Q2
Reactive Power Q2 Peak Demand | 30632 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx Q2 | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Q3 Subinterval Duration | 30638 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd Q3 Sub Intvl | NONE | DEM | PDMD_KVAR_SD_Q3
Block Demand Reactive Power Q3 # Subintervals | 30639 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q3 #SubIntvls | NONE | DEM | PDMD_KVAR_SD_Q3
Block Demand Reactive Power Q3 Pred Resp | 30640 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q3 Pred Resp | NONE | DEM | PDMD_KVAR_SD_Q3
Block Demand Reactive Power Q3 Update Rate | 30641 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd Q3 Update Rate | NONE | DEM | PDMD_KVAR_SD_Q3
Reactive Power Q3 Last Demand | 30642 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd Q3 | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_Q3
Reactive Power Q3 Predicted Demand | 30644 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr Q3 | PT_CT_KVAR | DEM | PDMD_KVAR_SD_Q3
Reactive Power Q3 Peak Demand | 30646 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx Q3 | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Q4 Subinterval Duration | 30652 | 1 | INT16U | seconds | R/O | numeric | --- | kVAR sd Q4 Sub Intvl | NONE | DEM | PDMD_KVAR_SD_Q4
Block Demand Reactive Power Q4 # Subintervals | 30653 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q4 #SubIntvls | NONE | DEM | PDMD_KVAR_SD_Q4
Block Demand Reactive Power Q4 Pred Resp | 30654 | 1 | INT16U | --- | R/O | numeric | --- | kVAR sd Q4 Pred Resp | NONE | DEM | PDMD_KVAR_SD_Q4
Block Demand Reactive Power Q4 Update Rate | 30655 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVAR sd Q4 Update Rate | NONE | DEM | PDMD_KVAR_SD_Q4
Reactive Power Q4 Last Demand | 30656 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR sd Q4 | PT_CT_KVAR | DEM | BASE_PDMD_KVAR_SD_Q4
Reactive Power Q4 Predicted Demand | 30658 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVAR pr Q4 | PT_CT_KVAR | DEM | PDMD_KVAR_SD_Q4
Reactive Power Q4 Peak Demand | 30660 | 6 | TIMESTAMPED_FLOAT32 | VAR | R/O | numeric | --- | kVAR sd mx Q4 | PT_CT_KVAR | DEM | None
Block Demand Apparent Power Q1 Subinterval Duration | 30666 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd Q1 Sub Intvl | NONE | DEM | PDMD_KVA_SD_Q1
Block Demand Apparent Power Q1 # Subintervals | 30667 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q1 #SubIntvls | NONE | DEM | PDMD_KVA_SD_Q1
Block Demand Apparent Power Q1 Pred Resp | 30668 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q1 Pred Resp | NONE | DEM | PDMD_KVA_SD_Q1
Block Demand Apparent Power Q1 Update Rate | 30669 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd Q1 Update Rate | NONE | DEM | PDMD_KVA_SD_Q1
Apparent Power Q1 Last Demand | 30670 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd Q1 | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_Q1
Apparent Power Q1 Predicted Demand | 30672 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr Q1 | PT_CT_KVA | DEM | PDMD_KVA_SD_Q1
Apparent Power Q1 Peak Demand | 30674 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx Q1 | PT_CT_KVA | DEM | None
Block Demand Apparent Power Q2 Subinterval Duration | 30680 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd Q2 Sub Intvl | NONE | DEM | PDMD_KVA_SD_Q2
Block Demand Apparent Power Q2 # Subintervals | 30681 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q2 #SubIntvls | NONE | DEM | PDMD_KVA_SD_Q2
Block Demand Apparent Power Q2 Pred Resp | 30682 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q2 Pred Resp | NONE | DEM | PDMD_KVA_SD_Q2
Block Demand Apparent Power Q2 Update Rate | 30683 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd Q2 Update Rate | NONE | DEM | PDMD_KVA_SD_Q2
Apparent Power Q2 Last Demand | 30684 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd Q2 | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_Q2
Apparent Power Q2 Predicted Demand | 30686 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr Q2 | PT_CT_KVA | DEM | PDMD_KVA_SD_Q2
Apparent Power Q2 Peak Demand | 30688 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx Q2 | PT_CT_KVA | DEM | None
Block Demand Apparent Power Q3 Subinterval Duration | 30694 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd Q3 Sub Intvl | NONE | DEM | PDMD_KVA_SD_Q3
Block Demand Apparent Power Q3 # Subintervals | 30695 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q3 #SubIntvls | NONE | DEM | PDMD_KVA_SD_Q3
Block Demand Apparent Power Q3 Pred Resp | 30696 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q3 Pred Resp | NONE | DEM | PDMD_KVA_SD_Q3
Block Demand Apparent Power Q3 Update Rate | 30697 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd Q3 Update Rate | NONE | DEM | PDMD_KVA_SD_Q3
Apparent Power Q3 Last Demand | 30698 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd Q3 | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_Q3
Apparent Power Q3 Predicted Demand | 30700 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr Q3 | PT_CT_KVA | DEM | PDMD_KVA_SD_Q3
Apparent Power Q3 Peak Demand | 30702 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx Q3 | PT_CT_KVA | DEM | None
Block Demand Apparent Power Q4 Subinterval Duration | 30708 | 1 | INT16U | seconds | R/O | numeric | --- | kVA sd Q4 Sub Intvl | NONE | DEM | PDMD_KVA_SD_Q4
Block Demand Apparent Power Q4 # Subintervals | 30709 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q4 #SubIntvls | NONE | DEM | PDMD_KVA_SD_Q4
Block Demand Apparent Power Q4 Pred Resp | 30710 | 1 | INT16U | --- | R/O | numeric | --- | kVA sd Q4 Pred Resp | NONE | DEM | PDMD_KVA_SD_Q4
Block Demand Apparent Power Q4 Update Rate | 30711 | 1 | INT16U | --- | R/O | enum | 0 - End of Sub-Interval 1 - Every Second | kVA sd Q4 Update Rate | NONE | DEM | PDMD_KVA_SD_Q4
Apparent Power Q4 Last Demand | 30712 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA sd Q4 | PT_CT_KVA | DEM | BASE_PDMD_KVA_SD_Q4
Apparent Power Q4 Predicted Demand | 30714 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVA pr Q4 | PT_CT_KVA | DEM | PDMD_KVA_SD_Q4
Apparent Power Q4 Peak Demand | 30716 | 6 | TIMESTAMPED_FLOAT32 | VA | R/O | numeric | --- | kVA sd mx Q4 | PT_CT_KVA | DEM | None
Block Demand Active Power | 30822 | 2 | FLOAT32 | W | R/O | numeric | --- | kVA co kW d-r | PT_CT_KW | DEM | None
Block Demand Active Power Into the Load | 30824 | 2 | FLOAT32 | W | R/O | numeric | --- | kVA co kW del | PT_CT_KW | DEM | None
Block Demand Active Power Out of the Load | 30826 | 2 | FLOAT32 | W | R/O | numeric | --- | kVA co kW rec | PT_CT_KW | DEM | None
Block Demand Active Power Total | 30828 | 2 | FLOAT32 | W | R/O | numeric | --- | kVA co kW d+r | PT_CT_KW | DEM | None
Block Demand Reactive Power | 30830 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVA co kVAR d-r | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Into the Load | 30832 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVA co kVAR del | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Out of the Load | 30834 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVA co kVAR rec | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Total | 30836 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kVA co kVAR d+r | PT_CT_KVAR | DEM | None
Block Demand Active Power | 30838 | 2 | FLOAT32 | W | R/O | numeric | --- | kVAR co kW d-r | PT_CT_KW | DEM | None
Block Demand Active Power Into the Load | 30840 | 2 | FLOAT32 | W | R/O | numeric | --- | kVAR co kW del | PT_CT_KW | DEM | None
Block Demand Active Power Out of the Load | 30842 | 2 | FLOAT32 | W | R/O | numeric | --- | kVAR co kW rec | PT_CT_KW | DEM | None
Block Demand Active Power Total | 30844 | 2 | FLOAT32 | W | R/O | numeric | --- | kVAR co kW d+r | PT_CT_KW | DEM | None
Block Demand Apparent Power | 30846 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVAR co kVA d-r | PT_CT_KVA | DEM | None
Block Demand Apparent Power Into the Load | 30848 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVAR co kVA del | PT_CT_KVA | DEM | None
Block Demand Apparent Power Out of the Load | 30850 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVAR co kVA rec | PT_CT_KVA | DEM | None
Block Demand Apparent Power Total | 30852 | 2 | FLOAT32 | VA | R/O | numeric | --- | kVAR co kVA d+r | PT_CT_KVA | DEM | None
Block Demand Reactive Power | 30854 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kW co kVAR d-r | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Into the Load | 30856 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kW co kVAR del | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Out of the Load | 30858 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kW co kVAR rec | PT_CT_KVAR | DEM | None
Block Demand Reactive Power Total | 30860 | 2 | FLOAT32 | VAR | R/O | numeric | --- | kW co kVAR d+r | PT_CT_KVAR | DEM | None
Block Demand Apparent Power | 30862 | 2 | FLOAT32 | VA | R/O | numeric | --- | kW co kVA d-r | PT_CT_KVA | DEM | None
Block Demand Apparent Power Into the Load | 30864 | 2 | FLOAT32 | VA | R/O | numeric | --- | kW co kVA del | PT_CT_KVA | DEM | None
Block Demand Apparent Power Out of the Load | 30866 | 2 | FLOAT32 | VA | R/O | numeric | --- | kW co kVA rec | PT_CT_KVA | DEM | None
Block Demand Apparent Power Total | 30868 | 2 | FLOAT32 | VA | R/O | numeric | --- | kW co kVA d+r | PT_CT_KVA | DEM | None
Active Energy Delivered Rate 1 | 30870 | 4 | INT64 | Wh | R/O | numeric | --- | PB kWh del A | KWH | TOM | None
Active Energy Delivered Rate 2 | 30874 | 4 | INT64 | Wh | R/O | numeric | --- | PB kWh del B | KWH | TOM | None
Active Energy Delivered Rate 3 | 30878 | 4 | INT64 | Wh | R/O | numeric | --- | PB kWh del C | KWH | TOM | None
Active Energy Delivered Rate 4 | 30882 | 4 | INT64 | Wh | R/O | numeric | --- | PB kWh del D | KWH | TOM | None
Active Energy Delivered | 30886 | 4 | INT64 | Wh | R/O | numeric | --- | PB kWh del | KWH | TOM | None
Active Energy Received | 30890 | 4 | INT64 | Wh | R/O | numeric | --- | PB kWh rec | KWH | TOM | None
Reactive Energy Delivered | 30894 | 4 | INT64 | VARh | R/O | numeric | --- | PB kVARh del | KVARH | TOM | None
Reactive Energy Received | 30898 | 4 | INT64 | VARh | R/O | numeric | --- | PB kVARh rec | KVARH | TOM | None
Apparent Energy Delivered | 30902 | 4 | INT64 | VAh | R/O | numeric | --- | PB kVAh del | KVAH | TOM | None
Apparent Energy Received | 30906 | 4 | INT64 | VAh | R/O | numeric | --- | PB kVAh rec | KVAH | TOM | None
Peak Block Demand Active Power Delived Rate 1 | 30910 | 2 | FLOAT32 | W | R/O | numeric | --- | PB kW sd mx d A | PT_CT_KW | TOM | None
Peak Block Demand Active Power Delived Rate 2 | 30912 | 2 | FLOAT32 | W | R/O | numeric | --- | PB kW sd mx d B | PT_CT_KW | TOM | None
Peak Block Demand Active Power Delived Rate 3 | 30914 | 2 | FLOAT32 | W | R/O | numeric | --- | PB kW sd mx d C | PT_CT_KW | TOM | None
Peak Block Demand Active Power Delived Rate 4 | 30916 | 2 | FLOAT32 | W | R/O | numeric | --- | PB kW sd mx d D | PT_CT_KW | TOM | None
Peak Block Demand Active Power Received | 30918 | 2 | FLOAT32 | W | R/O | numeric | --- | PB kW sd mx rec | PT_CT_KW | TOM | None
Peak Block Demand Reactive Power Delivered | 30920 | 2 | FLOAT32 | VAR | R/O | numeric | --- | PB kVAR sd mx d | PT_CT_KVAR | TOM | None
Peak Block Demand Reactive Power Received | 30922 | 2 | FLOAT32 | VAR | R/O | numeric | --- | PB kVAR sd mx r | PT_CT_KVAR | TOM | None
Peak Block Demand Apparent Power Delivered | 30924 | 2 | FLOAT32 | VA | R/O | numeric | --- | PB kVA sd mx d | PT_CT_KVA | TOM | None
Peak Block Demand Apparent Power Received | 30926 | 2 | FLOAT32 | VA | R/O | numeric | --- | PB kVA sd mx r | PT_CT_KVA | TOM | None
Active Energy Delivered Rate 1 | 30928 | 4 | INT64 | Wh | R/O | numeric | --- | PS kWh del A | KWH | TOM | None
Active Energy Delivered Rate 2 | 30932 | 4 | INT64 | Wh | R/O | numeric | --- | PS kWh del B | KWH | TOM | None
Active Energy Delivered Rate 3 | 30936 | 4 | INT64 | Wh | R/O | numeric | --- | PS kWh del C | KWH | TOM | None
Active Energy Delivered Rate 4 | 30940 | 4 | INT64 | Wh | R/O | numeric | --- | PS kWh del D | KWH | TOM | None
Active Energy Delivered | 30944 | 4 | INT64 | Wh | R/O | numeric | --- | PS kWh del | KWH | TOM | None
Active Energy Received | 30948 | 4 | INT64 | Wh | R/O | numeric | --- | PS kWh rec | KWH | TOM | None
Reactive Energy Delivered | 30952 | 4 | INT64 | VARh | R/O | numeric | --- | PS kVARh del | KVARH | TOM | None
Reactive Energy Received | 30956 | 4 | INT64 | VARh | R/O | numeric | --- | PS kVARh rec | KVARH | TOM | None
Apparent Energy Delivered | 30960 | 4 | INT64 | VAh | R/O | numeric | --- | PS kVAh del | KVAH | TOM | None
Apparent Energy Received | 30964 | 4 | INT64 | VAh | R/O | numeric | --- | PS kVAh rec | KVAH | TOM | None
Peak Block Demand Active Power Delived Rate 1 | 30968 | 2 | FLOAT32 | W | R/O | numeric | --- | PS kW sd mx d A | PT_CT_KW | TOM | None
Peak Block Demand Active Power Delived Rate 2 | 30970 | 2 | FLOAT32 | W | R/O | numeric | --- | PS kW sd mx d B | PT_CT_KW | TOM | None
Peak Block Demand Active Power Delived Rate 3 | 30972 | 2 | FLOAT32 | W | R/O | numeric | --- | PS kW sd mx d C | PT_CT_KW | TOM | None
Peak Block Demand Active Power Delived Rate 4 | 30974 | 2 | FLOAT32 | W | R/O | numeric | --- | PS kW sd mx d D | PT_CT_KW | TOM | None
Peak Block Demand Active Power Received | 30976 | 2 | FLOAT32 | W | R/O | numeric | --- | PS kW sd mx rec | PT_CT_KW | TOM | None
Peak Block Demand Reactive Power Delivered | 30978 | 2 | FLOAT32 | VAR | R/O | numeric | --- | PS kVAR sd mx d | PT_CT_KVAR | TOM | None
Peak Block Demand Reactive Power Received | 30980 | 2 | FLOAT32 | VAR | R/O | numeric | --- | PS kVAR sd mx r | PT_CT_KVAR | TOM | None
Peak Block Demand Apparent Power Delivered | 30982 | 2 | FLOAT32 | VA | R/O | numeric | --- | PS kVA sd mx d | PT_CT_KVA | TOM | None
Peak Block Demand Apparent Power Received | 30984 | 2 | FLOAT32 | VA | R/O | numeric | --- | PS kVA sd mx r | PT_CT_KVA | TOM | None
Active Energy Delivered Rate 1 | 30986 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PB kWh del A | KWH | TOM | None
Active Energy Delivered Rate 2 | 30988 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PB kWh del B | KWH | TOM | None
Active Energy Delivered Rate 3 | 30990 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PB kWh del C | KWH | TOM | None
Active Energy Delivered Rate 4 | 30992 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PB kWh del D | KWH | TOM | None
Active Energy Delivered | 30994 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PB kWh del | KWH | TOM | None
Active Energy Received | 30996 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PB kWh rec | KWH | TOM | None
Reactive Energy Delivered | 30998 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | PB kVARh del | KVARH | TOM | None
Reactive Energy Received | 31000 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | PB kVARh rec | KVARH | TOM | None
Apparent Energy Delivered | 31002 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | PB kVAh del | KVAH | TOM | None
Apparent Energy Received | 31004 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | PB kVAh rec | KVAH | TOM | None
Active Energy Delivered Rate 1 | 31006 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PS kWh del A | KWH | TOM | None
Active Energy Delivered Rate 2 | 31008 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PS kWh del B | KWH | TOM | None
Active Energy Delivered Rate 3 | 31010 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PS kWh del C | KWH | TOM | None
Active Energy Delivered Rate 4 | 31012 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PS kWh del D | KWH | TOM | None
Active Energy Delivered | 31014 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PS kWh del | KWH | TOM | None
Active Energy Received | 31016 | 2 | FLOAT32 | kWh | R/O | numeric | --- | PS kWh rec | KWH | TOM | None
Reactive Energy Delivered | 31018 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | PS kVARh del | KVARH | TOM | None
Reactive Energy Received | 31020 | 2 | FLOAT32 | kVARh | R/O | numeric | --- | PS kVARh rec | KVARH | TOM | None
Apparent Energy Delivered | 31022 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | PS kVAh del | KVAH | TOM | None
Apparent Energy Received | 31024 | 2 | FLOAT32 | kVAh | R/O | numeric | --- | PS kVAh rec | KVAH | TOM | None
Current, Phase A 3 Second (150/180 Cycles) | 34352 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 3s | A | PQM | PDMD_V1_3S
Current, Phase A 10 Minute | 34354 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 10m | A | PQM | PDMD_V1_3S
Current, Phase A 2 Hour | 34356 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 2hr | A | PQM | None
Current, Phase B 3 Second (150/180 Cycles) | 34358 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 3s | A | PQM | PDMD_V1_3S
Current, Phase B 10 Minute | 34360 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 10m | A | PQM | PDMD_V1_3S
Current, Phase B 2 Hour | 34362 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 2hr | A | PQM | None
Current, Phase C 3 Second (150/180 Cycles) | 34364 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 3s | A | PQM | PDMD_V1_3S
Current, Phase C 10 Minute | 34366 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 10m | A | PQM | PDMD_V1_3S
Current, Phase C 2 Hour | 34368 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 2hr | A | PQM | None
Voltage, A-N 3 Second (150/180 Cycles) | 34400 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 3s | V | PQM | BASE_PDMD_V1_3S
Voltage, A-N 10 Minute | 34402 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 10m | V | PQM | PDMD_V1_3S
Voltage, A-N 2 Hour | 34404 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 2hr | V | PQM | None
Voltage, B-N 3 Second (150/180 Cycles) | 34406 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 3s | V | PQM | PDMD_V1_3S
Voltage, B-N 10 Minute | 34408 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 10m | V | PQM | PDMD_V1_3S
Voltage, B-N 2 Hour | 34410 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 2hr | V | PQM | None
Voltage, C-N 3 Second (150/180 Cycles) | 34412 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 3s | V | PQM | PDMD_V1_3S
Voltage, C-N 10 Minute | 34414 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 10m | V | PQM | PDMD_V1_3S
Voltage, C-N 2 Hour | 34416 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 2hr | V | PQM | None
Unbalance, Neg Seq 3 Second (150/180 Cycles) | 34460 | 2 | FLOAT32 | --- | R/O | numeric | --- | NegSeqComp 3s | PERCENT | PQM | None
Unbalance, Neg Seq 10 Minute | 34462 | 2 | FLOAT32 | --- | R/O | numeric | --- | NegSeqComp 10m | PERCENT | PQM | None
Unbalance, Neg Seq 2 Hour | 34464 | 2 | FLOAT32 | --- | R/O | numeric | --- | NegSeqComp 2hr | PERCENT | PQM | None
Unbalance, Zero Seq 3 Second (150/180 Cycles) | 34466 | 2 | FLOAT32 | --- | R/O | numeric | --- | ZeroSeqComp 3s | PERCENT | PQM | None
Unbalance, Zero Seq 10 Minute | 34468 | 2 | FLOAT32 | --- | R/O | numeric | --- | ZeroSeqComp 10m | PERCENT | PQM | None
Unbalance, Zero Seq 2 Hour | 34470 | 2 | FLOAT32 | --- | R/O | numeric | --- | ZeroSeqComp 2hr | PERCENT | PQM | None
Power Frequency 3 Second (150/180 Cycles) | 34472 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Power Frequency | HZ | PQM | PDMD_V1_3S
Power Frequency 10 Minute | 34474 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Power Freq 10m | HZ | PQM | None
Power Frequency 2 Hour | 34476 | 2 | FLOAT32 | Hz | R/O | numeric | --- | Power Freq 2hr | HZ | PQM | None
THD Current A 10 Minute | 34479 | 2 | FLOAT32 | % | R/O | numeric | --- | I1 THD 10m | PERCENT | PQM | None
THD Current B 10 Minute | 34481 | 2 | FLOAT32 | % | R/O | numeric | --- | I2 THD 10m | PERCENT | PQM | None
THD Current C 10 Minute | 34483 | 2 | FLOAT32 | % | R/O | numeric | --- | I3 THD 10m | PERCENT | PQM | None
K Factor Current A 10 Minute | 34537 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 K Factor 10m | NONE | PQM | None
K Factor Current B 10 Minute | 34539 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 K Factor 10m | NONE | PQM | None
K Factor Current C 10 Minute | 34541 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 K Factor 10m | NONE | PQM | None
Crest Factor Current A 10 Minute | 34543 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 Crest Factor 10m | NONE | PQM | None
Crest Factor Current B 10 Minute | 34545 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 Crest Factor 10m | NONE | PQM | None
Crest Factor Current C 10 Minute | 34547 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 Crest Factor 10m | NONE | PQM | None
Current, Positive Sequence, Magnitude | 34611 | 2 | FLOAT32 | A | R/O | numeric | --- | I PosSeqMag10m | A | PQM | PDMD_I_POSSEQMAG
Current, Positive Sequence, Angle | 34613 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I PosSeqPhs10m | DEGREES | PQM | PDMD_I_POSSEQMAG
Current, Negative Sequence, Magnitude | 34615 | 2 | FLOAT32 | A | R/O | numeric | --- | I NegSeqMag10m | A | PQM | PDMD_I_POSSEQMAG
Current, Negative Sequence, Angle | 34617 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I NegSeqPhs10m | DEGREES | PQM | PDMD_I_POSSEQMAG
Current, Zero Sequence, Magnitude | 34619 | 2 | FLOAT32 | A | R/O | numeric | --- | I ZeroSeqMag10m | A | PQM | PDMD_I_POSSEQMAG
Current, Zero Sequence, Angle | 34621 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I ZeroSeqPhs10m | DEGREES | PQM | PDMD_I_POSSEQMAG
Voltage, Positive Sequence, Magnitude | 34623 | 2 | FLOAT32 | V | R/O | numeric | --- | V PosSeqMag10m | V | PQM | PDMD_V_POSSEQMAG
Voltage, Positive Sequence, Angle | 34625 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V PosSeqPhs10m | DEGREES | PQM | PDMD_V_POSSEQMAG
Voltage, Negative Sequence, Magnitude | 34627 | 2 | FLOAT32 | V | R/O | numeric | --- | V NegSeqMag10m | V | PQM | PDMD_V_POSSEQMAG
Voltage, Negative Sequence, Angle | 34629 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V NegSeqPhs10m | DEGREES | PQM | PDMD_V_POSSEQMAG
Voltage, Zero Sequence, Magnitude | 34631 | 2 | FLOAT32 | V | R/O | numeric | --- | V ZeroSeqMag10m | V | PQM | PDMD_V_POSSEQMAG
Voltage, Zero Sequence, Angle | 34633 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V ZeroSeqPhs10m | DEGREES | PQM | PDMD_V_POSSEQMAG
Short-Term Flicker (Pst), A-N | 34649 | 2 | FLOAT32 | --- | R/O | numeric | --- | Phase 1 Pst | NONE | PQM | None
Short-Term Flicker (Pst), B-N | 34651 | 2 | FLOAT32 | --- | R/O | numeric | --- | Phase 2 Pst | NONE | PQM | None
Short-Term Flicker (Pst), C-N | 34653 | 2 | FLOAT32 | --- | R/O | numeric | --- | Phase 3 Pst | NONE | PQM | None
TEHD Current A 10 Minute | 34657 | 2 | FLOAT32 | % | R/O | numeric | --- | I1 Total Even HD 10m | PERCENT | PQM | None
TEHD Current B 10 Minute | 34659 | 2 | FLOAT32 | % | R/O | numeric | --- | I2 Total Even HD 10m | PERCENT | PQM | None
TEHD Current C 10 Minute | 34661 | 2 | FLOAT32 | % | R/O | numeric | --- | I3 Total Even HD 10m | PERCENT | PQM | None
TOHD Current A 10 Minute | 34663 | 2 | FLOAT32 | % | R/O | numeric | --- | I1 Total Odd HD 10m | PERCENT | PQM | None
TOHD Current B 10 Minute | 34665 | 2 | FLOAT32 | % | R/O | numeric | --- | I2 Total Odd HD 10m | PERCENT | PQM | None
TOHD Current C 10 Minute | 34667 | 2 | FLOAT32 | % | R/O | numeric | --- | I3 Total Odd HD 10m | PERCENT | PQM | None
Current Unbalance, Neg Seq 3 Second (150/180 Cycles) | 34669 | 2 | FLOAT32 | --- | R/O | numeric | --- | IUnbal u2 3s | PERCENT | PQM | None
Current Unbalance, Neg Seq 10 Minute | 34671 | 2 | FLOAT32 | --- | R/O | numeric | --- | IUnbal u2 10m | PERCENT | PQM | None
Current Unbalance, Neg Seq 2 Hour | 34673 | 2 | FLOAT32 | --- | R/O | numeric | --- | IUnbal u2 2hr | PERCENT | PQM | None
Current Unbalance, Zero Seq 3 Second (150/180 Cycles) | 34675 | 2 | FLOAT32 | --- | R/O | numeric | --- | IUnbal u0 3s | PERCENT | PQM | None
Current Unbalance, Zero Seq 10 Minute | 34677 | 2 | FLOAT32 | --- | R/O | numeric | --- | IUnbal u0 10m | PERCENT | PQM | None
Current Unbalance, Zero Seq 2 Hour | 34679 | 2 | FLOAT32 | --- | R/O | numeric | --- | IUnbal u0 2hr | PERCENT | PQM | None
TDD Current A 10 Minute | 34681 | 2 | FLOAT32 | % | R/O | numeric | --- | I1 TDD 10m | PERCENT | PQM | None
TDD Current B 10 Minute | 34683 | 2 | FLOAT32 | % | R/O | numeric | --- | I2 TDD 10m | PERCENT | PQM | None
TDD Current C 10 Minute | 34685 | 2 | FLOAT32 | % | R/O | numeric | --- | I3 TDD 10m | PERCENT | PQM | None
Voltage A-N, H1 Magnitude, V | 35891 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H1 Mag 10m | V | PQM | BASE_PDMD_V1_H1_MAG_10M
Voltage A-N, H1 Angle | 35893 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H1 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H2 Magnitude, V | 35897 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H2 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H2 Angle | 35899 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H2 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H3 Magnitude, V | 35903 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H3 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H3 Angle | 35905 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H3 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H4 Magnitude, V | 35909 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H4 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H4 Angle | 35911 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H4 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H5 Magnitude, V | 35915 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H5 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H5 Angle | 35917 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H5 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H6 Magnitude, V | 35921 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H6 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H6 Angle | 35923 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H6 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H7 Magnitude, V | 35927 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H7 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H7 Angle | 35929 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H7 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H8 Magnitude, V | 35933 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H8 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H8 Angle | 35935 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H8 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H9 Magnitude, V | 35939 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H9 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H9 Angle | 35941 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H9 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H10 Magnitude, V | 35945 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H10 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H10 Angle | 35947 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H10 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H11 Magnitude, V | 35951 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H11 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H11 Angle | 35953 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H11 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H12 Magnitude, V | 35957 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H12 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H12 Angle | 35959 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H12 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H13 Magnitude, V | 35963 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H13 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H13 Angle | 35965 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H13 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H14 Magnitude, V | 35969 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H14 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H14 Angle | 35971 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H14 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H15 Magnitude, V | 35975 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H15 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H15 Angle | 35977 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H15 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H16 Magnitude, V | 35981 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H16 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H16 Angle | 35983 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H16 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H17 Magnitude, V | 35987 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H17 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H17 Angle | 35989 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H17 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H18 Magnitude, V | 35993 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H18 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H18 Angle | 35995 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H18 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H19 Magnitude, V | 35999 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H19 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H19 Angle | 36001 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H19 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H20 Magnitude, V | 36005 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H20 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H20 Angle | 36007 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H20 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H21 Magnitude, V | 36011 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H21 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H21 Angle | 36013 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H21 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H22 Magnitude, V | 36017 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H22 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H22 Angle | 36019 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H22 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H23 Magnitude, V | 36023 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H23 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H23 Angle | 36025 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H23 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H24 Magnitude, V | 36029 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H24 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H24 Angle | 36031 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H24 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H25 Magnitude, V | 36035 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H25 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H25 Angle | 36037 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H25 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H26 Magnitude, V | 36041 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H26 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H26 Angle | 36043 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H26 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H27 Magnitude, V | 36047 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H27 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H27 Angle | 36049 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H27 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H28 Magnitude, V | 36053 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H28 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H28 Angle | 36055 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H28 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H29 Magnitude, V | 36059 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H29 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H29 Angle | 36061 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H29 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H30 Magnitude, V | 36065 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H30 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H30 Angle | 36067 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H30 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H31 Magnitude, V | 36071 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H31 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H31 Angle | 36073 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H31 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H32 Magnitude, V | 36077 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H32 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H32 Angle | 36079 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H32 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H33 Magnitude, V | 36083 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H33 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H33 Angle | 36085 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H33 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H34 Magnitude, V | 36089 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H34 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H34 Angle | 36091 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H34 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H35 Magnitude, V | 36095 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H35 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H35 Angle | 36097 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H35 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H36 Magnitude, V | 36101 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H36 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H36 Angle | 36103 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H36 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H37 Magnitude, V | 36107 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H37 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H37 Angle | 36109 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H37 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H38 Magnitude, V | 36113 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H38 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H38 Angle | 36115 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H38 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H39 Magnitude, V | 36119 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H39 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H39 Angle | 36121 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H39 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H40 Magnitude, V | 36125 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H40 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H40 Angle | 36127 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H40 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H41 Magnitude, V | 36131 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H41 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H41 Angle | 36133 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H41 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H42 Magnitude, V | 36137 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H42 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H42 Angle | 36139 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H42 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H43 Magnitude, V | 36143 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H43 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H43 Angle | 36145 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H43 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H44 Magnitude, V | 36149 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H44 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H44 Angle | 36151 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H44 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H45 Magnitude, V | 36155 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H45 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H45 Angle | 36157 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H45 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H46 Magnitude, V | 36161 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H46 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H46 Angle | 36163 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H46 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H47 Magnitude, V | 36167 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H47 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H47 Angle | 36169 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H47 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H48 Magnitude, V | 36173 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H48 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H48 Angle | 36175 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H48 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H49 Magnitude, V | 36179 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H49 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H49 Angle | 36181 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H49 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H50 Magnitude, V | 36185 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H50 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H50 Angle | 36187 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H50 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H51 Magnitude, V | 36191 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H51 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H51 Angle | 36193 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H51 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H52 Magnitude, V | 36197 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H52 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H52 Angle | 36199 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H52 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H53 Magnitude, V | 36203 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H53 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H53 Angle | 36205 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H53 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H54 Magnitude, V | 36209 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H54 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H54 Angle | 36211 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H54 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H55 Magnitude, V | 36215 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H55 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H55 Angle | 36217 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H55 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H56 Magnitude, V | 36221 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H56 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H56 Angle | 36223 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H56 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H57 Magnitude, V | 36227 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H57 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H57 Angle | 36229 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H57 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H58 Magnitude, V | 36233 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H58 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H58 Angle | 36235 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H58 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H59 Magnitude, V | 36239 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H59 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H59 Angle | 36241 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H59 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H60 Magnitude, V | 36245 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H60 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H60 Angle | 36247 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H60 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H61 Magnitude, V | 36251 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H61 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H61 Angle | 36253 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H61 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H62 Magnitude, V | 36257 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H62 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H62 Angle | 36259 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H62 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H63 Magnitude, V | 36263 | 2 | FLOAT32 | V | R/O | numeric | --- | V1 H63 Mag 10m | V | PQM | PDMD_V1_H1_MAG_10M
Voltage A-N, H63 Angle | 36265 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V1 H63 Ang 10m | DEGREES | PQM | PDMD_V1_H1_MAG_10M
Voltage B-N, H1 Magnitude, V | 36279 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H1 Mag 10m | V | PQM | BASE_PDMD_V2_H1_MAG_10M
Voltage B-N, H1 Angle | 36281 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H1 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H2 Magnitude, V | 36285 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H2 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H2 Angle | 36287 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H2 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H3 Magnitude, V | 36291 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H3 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H3 Angle | 36293 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H3 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H4 Magnitude, V | 36297 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H4 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H4 Angle | 36299 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H4 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H5 Magnitude, V | 36303 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H5 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H5 Angle | 36305 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H5 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H6 Magnitude, V | 36309 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H6 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H6 Angle | 36311 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H6 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H7 Magnitude, V | 36315 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H7 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H7 Angle | 36317 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H7 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H8 Magnitude, V | 36321 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H8 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H8 Angle | 36323 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H8 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H9 Magnitude, V | 36327 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H9 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H9 Angle | 36329 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H9 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H10 Magnitude, V | 36333 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H10 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H10 Angle | 36335 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H10 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H11 Magnitude, V | 36339 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H11 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H11 Angle | 36341 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H11 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H12 Magnitude, V | 36345 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H12 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H12 Angle | 36347 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H12 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H13 Magnitude, V | 36351 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H13 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H13 Angle | 36353 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H13 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H14 Magnitude, V | 36357 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H14 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H14 Angle | 36359 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H14 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H15 Magnitude, V | 36363 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H15 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H15 Angle | 36365 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H15 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H16 Magnitude, V | 36369 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H16 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H16 Angle | 36371 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H16 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H17 Magnitude, V | 36375 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H17 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H17 Angle | 36377 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H17 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H18 Magnitude, V | 36381 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H18 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H18 Angle | 36383 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H18 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H19 Magnitude, V | 36387 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H19 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H19 Angle | 36389 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H19 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H20 Magnitude, V | 36393 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H20 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H20 Angle | 36395 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H20 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H21 Magnitude, V | 36399 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H21 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H21 Angle | 36401 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H21 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H22 Magnitude, V | 36405 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H22 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H22 Angle | 36407 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H22 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H23 Magnitude, V | 36411 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H23 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H23 Angle | 36413 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H23 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H24 Magnitude, V | 36417 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H24 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H24 Angle | 36419 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H24 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H25 Magnitude, V | 36423 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H25 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H25 Angle | 36425 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H25 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H26 Magnitude, V | 36429 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H26 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H26 Angle | 36431 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H26 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H27 Magnitude, V | 36435 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H27 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H27 Angle | 36437 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H27 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H28 Magnitude, V | 36441 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H28 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H28 Angle | 36443 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H28 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H29 Magnitude, V | 36447 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H29 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H29 Angle | 36449 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H29 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H30 Magnitude, V | 36453 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H30 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H30 Angle | 36455 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H30 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H31 Magnitude, V | 36459 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H31 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H31 Angle | 36461 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H31 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H32 Magnitude, V | 36465 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H32 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H32 Angle | 36467 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H32 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H33 Magnitude, V | 36471 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H33 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H33 Angle | 36473 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H33 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H34 Magnitude, V | 36477 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H34 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H34 Angle | 36479 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H34 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H35 Magnitude, V | 36483 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H35 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H35 Angle | 36485 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H35 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H36 Magnitude, V | 36489 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H36 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H36 Angle | 36491 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H36 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H37 Magnitude, V | 36495 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H37 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H37 Angle | 36497 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H37 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H38 Magnitude, V | 36501 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H38 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H38 Angle | 36503 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H38 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H39 Magnitude, V | 36507 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H39 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H39 Angle | 36509 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H39 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H40 Magnitude, V | 36513 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H40 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H40 Angle | 36515 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H40 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H41 Magnitude, V | 36519 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H41 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H41 Angle | 36521 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H41 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H42 Magnitude, V | 36525 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H42 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H42 Angle | 36527 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H42 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H43 Magnitude, V | 36531 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H43 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H43 Angle | 36533 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H43 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H44 Magnitude, V | 36537 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H44 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H44 Angle | 36539 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H44 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H45 Magnitude, V | 36543 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H45 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H45 Angle | 36545 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H45 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H46 Magnitude, V | 36549 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H46 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H46 Angle | 36551 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H46 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H47 Magnitude, V | 36555 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H47 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H47 Angle | 36557 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H47 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H48 Magnitude, V | 36561 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H48 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H48 Angle | 36563 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H48 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H49 Magnitude, V | 36567 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H49 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H49 Angle | 36569 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H49 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H50 Magnitude, V | 36573 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H50 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H50 Angle | 36575 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H50 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H51 Magnitude, V | 36579 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H51 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H51 Angle | 36581 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H51 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H52 Magnitude, V | 36585 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H52 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H52 Angle | 36587 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H52 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H53 Magnitude, V | 36591 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H53 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H53 Angle | 36593 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H53 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H54 Magnitude, V | 36597 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H54 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H54 Angle | 36599 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H54 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H55 Magnitude, V | 36603 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H55 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H55 Angle | 36605 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H55 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H56 Magnitude, V | 36609 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H56 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H56 Angle | 36611 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H56 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H57 Magnitude, V | 36615 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H57 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H57 Angle | 36617 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H57 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H58 Magnitude, V | 36621 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H58 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H58 Angle | 36623 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H58 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H59 Magnitude, V | 36627 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H59 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H59 Angle | 36629 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H59 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H60 Magnitude, V | 36633 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H60 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H60 Angle | 36635 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H60 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H61 Magnitude, V | 36639 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H61 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H61 Angle | 36641 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H61 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H62 Magnitude, V | 36645 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H62 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H62 Angle | 36647 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H62 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H63 Magnitude, V | 36651 | 2 | FLOAT32 | V | R/O | numeric | --- | V2 H63 Mag 10m | V | PQM | PDMD_V2_H1_MAG_10M
Voltage B-N, H63 Angle | 36653 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V2 H63 Ang 10m | DEGREES | PQM | PDMD_V2_H1_MAG_10M
Voltage C-N, H1 Magnitude, V | 36667 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H1 Mag 10m | V | PQM | BASE_PDMD_V3_H1_MAG_10M
Voltage C-N, H1 Angle | 36669 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H1 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H2 Magnitude, V | 36673 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H2 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H2 Angle | 36675 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H2 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H3 Magnitude, V | 36679 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H3 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H3 Angle | 36681 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H3 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H4 Magnitude, V | 36685 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H4 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H4 Angle | 36687 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H4 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H5 Magnitude, V | 36691 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H5 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H5 Angle | 36693 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H5 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H6 Magnitude, V | 36697 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H6 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H6 Angle | 36699 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H6 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H7 Magnitude, V | 36703 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H7 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H7 Angle | 36705 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H7 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H8 Magnitude, V | 36709 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H8 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H8 Angle | 36711 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H8 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H9 Magnitude, V | 36715 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H9 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H9 Angle | 36717 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H9 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H10 Magnitude, V | 36721 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H10 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H10 Angle | 36723 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H10 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H11 Magnitude, V | 36727 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H11 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H11 Angle | 36729 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H11 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H12 Magnitude, V | 36733 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H12 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H12 Angle | 36735 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H12 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H13 Magnitude, V | 36739 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H13 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H13 Angle | 36741 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H13 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H14 Magnitude, V | 36745 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H14 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H14 Angle | 36747 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H14 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H15 Magnitude, V | 36751 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H15 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H15 Angle | 36753 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H15 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H16 Magnitude, V | 36757 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H16 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H16 Angle | 36759 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H16 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H17 Magnitude, V | 36763 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H17 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H17 Angle | 36765 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H17 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H18 Magnitude, V | 36769 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H18 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H18 Angle | 36771 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H18 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H19 Magnitude, V | 36775 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H19 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H19 Angle | 36777 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H19 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H20 Magnitude, V | 36781 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H20 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H20 Angle | 36783 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H20 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H21 Magnitude, V | 36787 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H21 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H21 Angle | 36789 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H21 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H22 Magnitude, V | 36793 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H22 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H22 Angle | 36795 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H22 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H23 Magnitude, V | 36799 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H23 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H23 Angle | 36801 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H23 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H24 Magnitude, V | 36805 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H24 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H24 Angle | 36807 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H24 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H25 Magnitude, V | 36811 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H25 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H25 Angle | 36813 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H25 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H26 Magnitude, V | 36817 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H26 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H26 Angle | 36819 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H26 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H27 Magnitude, V | 36823 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H27 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H27 Angle | 36825 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H27 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H28 Magnitude, V | 36829 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H28 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H28 Angle | 36831 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H28 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H29 Magnitude, V | 36835 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H29 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H29 Angle | 36837 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H29 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H30 Magnitude, V | 36841 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H30 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H30 Angle | 36843 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H30 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H31 Magnitude, V | 36847 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H31 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H31 Angle | 36849 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H31 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H32 Magnitude, V | 36853 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H32 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H32 Angle | 36855 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H32 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H33 Magnitude, V | 36859 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H33 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H33 Angle | 36861 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H33 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H34 Magnitude, V | 36865 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H34 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H34 Angle | 36867 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H34 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H35 Magnitude, V | 36871 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H35 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H35 Angle | 36873 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H35 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H36 Magnitude, V | 36877 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H36 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H36 Angle | 36879 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H36 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H37 Magnitude, V | 36883 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H37 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H37 Angle | 36885 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H37 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H38 Magnitude, V | 36889 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H38 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H38 Angle | 36891 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H38 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H39 Magnitude, V | 36895 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H39 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H39 Angle | 36897 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H39 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H40 Magnitude, V | 36901 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H40 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H40 Angle | 36903 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H40 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H41 Magnitude, V | 36907 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H41 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H41 Angle | 36909 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H41 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H42 Magnitude, V | 36913 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H42 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H42 Angle | 36915 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H42 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H43 Magnitude, V | 36919 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H43 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H43 Angle | 36921 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H43 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H44 Magnitude, V | 36925 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H44 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H44 Angle | 36927 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H44 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H45 Magnitude, V | 36931 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H45 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H45 Angle | 36933 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H45 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H46 Magnitude, V | 36937 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H46 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H46 Angle | 36939 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H46 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H47 Magnitude, V | 36943 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H47 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H47 Angle | 36945 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H47 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H48 Magnitude, V | 36949 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H48 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H48 Angle | 36951 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H48 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H49 Magnitude, V | 36955 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H49 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H49 Angle | 36957 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H49 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H50 Magnitude, V | 36961 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H50 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H50 Angle | 36963 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H50 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H51 Magnitude, V | 36967 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H51 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H51 Angle | 36969 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H51 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H52 Magnitude, V | 36973 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H52 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H52 Angle | 36975 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H52 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H53 Magnitude, V | 36979 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H53 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H53 Angle | 36981 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H53 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H54 Magnitude, V | 36985 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H54 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H54 Angle | 36987 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H54 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H55 Magnitude, V | 36991 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H55 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H55 Angle | 36993 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H55 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H56 Magnitude, V | 36997 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H56 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H56 Angle | 36999 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H56 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H57 Magnitude, V | 37003 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H57 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H57 Angle | 37005 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H57 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H58 Magnitude, V | 37009 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H58 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H58 Angle | 37011 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H58 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H59 Magnitude, V | 37015 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H59 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H59 Angle | 37017 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H59 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H60 Magnitude, V | 37021 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H60 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H60 Angle | 37023 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H60 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H61 Magnitude, V | 37027 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H61 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H61 Angle | 37029 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H61 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H62 Magnitude, V | 37033 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H62 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H62 Angle | 37035 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H62 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H63 Magnitude, V | 37039 | 2 | FLOAT32 | V | R/O | numeric | --- | V3 H63 Mag 10m | V | PQM | PDMD_V3_H1_MAG_10M
Voltage C-N, H63 Angle | 37041 | 2 | FLOAT32 | degrees | R/O | numeric | --- | V3 H63 Ang 10m | DEGREES | PQM | PDMD_V3_H1_MAG_10M
Current A, H1 Magnitude, A | 37443 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H1 Mag 10m | A | PQM | BASE_PDMD_I1_H1_MAG_10M
Current A, H1 Angle | 37445 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H1 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H2 Magnitude, A | 37449 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H2 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H2 Angle | 37451 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H2 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H3 Magnitude, A | 37455 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H3 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H3 Angle | 37457 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H3 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H4 Magnitude, A | 37461 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H4 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H4 Angle | 37463 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H4 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H5 Magnitude, A | 37467 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H5 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H5 Angle | 37469 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H5 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H6 Magnitude, A | 37473 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H6 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H6 Angle | 37475 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H6 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H7 Magnitude, A | 37479 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H7 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H7 Angle | 37481 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H7 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H8 Magnitude, A | 37485 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H8 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H8 Angle | 37487 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H8 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H9 Magnitude, A | 37491 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H9 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H9 Angle | 37493 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H9 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H10 Magnitude, A | 37497 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H10 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H10 Angle | 37499 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H10 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H11 Magnitude, A | 37503 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H11 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H11 Angle | 37505 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H11 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H12 Magnitude, A | 37509 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H12 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H12 Angle | 37511 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H12 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H13 Magnitude, A | 37515 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H13 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H13 Angle | 37517 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H13 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H14 Magnitude, A | 37521 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H14 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H14 Angle | 37523 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H14 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H15 Magnitude, A | 37527 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H15 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H15 Angle | 37529 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H15 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H16 Magnitude, A | 37533 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H16 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H16 Angle | 37535 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H16 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H17 Magnitude, A | 37539 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H17 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H17 Angle | 37541 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H17 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H18 Magnitude, A | 37545 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H18 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H18 Angle | 37547 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H18 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H19 Magnitude, A | 37551 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H19 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H19 Angle | 37553 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H19 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H20 Magnitude, A | 37557 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H20 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H20 Angle | 37559 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H20 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H21 Magnitude, A | 37563 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H21 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H21 Angle | 37565 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H21 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H22 Magnitude, A | 37569 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H22 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H22 Angle | 37571 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H22 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H23 Magnitude, A | 37575 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H23 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H23 Angle | 37577 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H23 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H24 Magnitude, A | 37581 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H24 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H24 Angle | 37583 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H24 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H25 Magnitude, A | 37587 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H25 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H25 Angle | 37589 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H25 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H26 Magnitude, A | 37593 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H26 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H26 Angle | 37595 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H26 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H27 Magnitude, A | 37599 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H27 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H27 Angle | 37601 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H27 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H28 Magnitude, A | 37605 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H28 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H28 Angle | 37607 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H28 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H29 Magnitude, A | 37611 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H29 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H29 Angle | 37613 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H29 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H30 Magnitude, A | 37617 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H30 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H30 Angle | 37619 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H30 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H31 Magnitude, A | 37623 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H31 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H31 Angle | 37625 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H31 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H32 Magnitude, A | 37629 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H32 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H32 Angle | 37631 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H32 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H33 Magnitude, A | 37635 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H33 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H33 Angle | 37637 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H33 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H34 Magnitude, A | 37641 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H34 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H34 Angle | 37643 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H34 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H35 Magnitude, A | 37647 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H35 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H35 Angle | 37649 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H35 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H36 Magnitude, A | 37653 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H36 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H36 Angle | 37655 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H36 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H37 Magnitude, A | 37659 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H37 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H37 Angle | 37661 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H37 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H38 Magnitude, A | 37665 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H38 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H38 Angle | 37667 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H38 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H39 Magnitude, A | 37671 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H39 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H39 Angle | 37673 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H39 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H40 Magnitude, A | 37677 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H40 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H40 Angle | 37679 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H40 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H41 Magnitude, A | 37683 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H41 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H41 Angle | 37685 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H41 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H42 Magnitude, A | 37689 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H42 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H42 Angle | 37691 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H42 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H43 Magnitude, A | 37695 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H43 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H43 Angle | 37697 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H43 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H44 Magnitude, A | 37701 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H44 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H44 Angle | 37703 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H44 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H45 Magnitude, A | 37707 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H45 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H45 Angle | 37709 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H45 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H46 Magnitude, A | 37713 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H46 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H46 Angle | 37715 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H46 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H47 Magnitude, A | 37719 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H47 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H47 Angle | 37721 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H47 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H48 Magnitude, A | 37725 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H48 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H48 Angle | 37727 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H48 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H49 Magnitude, A | 37731 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H49 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H49 Angle | 37733 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H49 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H50 Magnitude, A | 37737 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H50 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H50 Angle | 37739 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H50 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H51 Magnitude, A | 37743 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H51 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H51 Angle | 37745 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H51 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H52 Magnitude, A | 37749 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H52 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H52 Angle | 37751 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H52 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H53 Magnitude, A | 37755 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H53 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H53 Angle | 37757 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H53 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H54 Magnitude, A | 37761 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H54 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H54 Angle | 37763 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H54 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H55 Magnitude, A | 37767 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H55 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H55 Angle | 37769 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H55 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H56 Magnitude, A | 37773 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H56 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H56 Angle | 37775 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H56 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H57 Magnitude, A | 37779 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H57 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H57 Angle | 37781 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H57 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H58 Magnitude, A | 37785 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H58 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H58 Angle | 37787 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H58 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H59 Magnitude, A | 37791 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H59 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H59 Angle | 37793 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H59 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H60 Magnitude, A | 37797 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H60 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H60 Angle | 37799 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H60 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H61 Magnitude, A | 37803 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H61 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H61 Angle | 37805 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H61 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H62 Magnitude, A | 37809 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H62 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H62 Angle | 37811 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H62 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current A, H63 Magnitude, A | 37815 | 2 | FLOAT32 | A | R/O | numeric | --- | I1 H63 Mag 10m | A | PQM | PDMD_I1_H1_MAG_10M
Current A, H63 Angle | 37817 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I1 H63 Ang 10m | DEGREES | PQM | PDMD_I1_H1_MAG_10M
Current B, H1 Magnitude, A | 37831 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H1 Mag 10m | A | PQM | BASE_PDMD_I2_H1_MAG_10M
Current B, H1 Angle | 37833 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H1 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H2 Magnitude, A | 37837 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H2 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H2 Angle | 37839 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H2 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H3 Magnitude, A | 37843 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H3 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H3 Angle | 37845 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H3 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H4 Magnitude, A | 37849 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H4 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H4 Angle | 37851 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H4 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H5 Magnitude, A | 37855 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H5 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H5 Angle | 37857 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H5 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H6 Magnitude, A | 37861 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H6 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H6 Angle | 37863 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H6 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H7 Magnitude, A | 37867 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H7 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H7 Angle | 37869 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H7 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H8 Magnitude, A | 37873 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H8 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H8 Angle | 37875 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H8 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H9 Magnitude, A | 37879 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H9 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H9 Angle | 37881 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H9 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H10 Magnitude, A | 37885 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H10 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H10 Angle | 37887 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H10 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H11 Magnitude, A | 37891 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H11 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H11 Angle | 37893 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H11 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H12 Magnitude, A | 37897 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H12 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H12 Angle | 37899 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H12 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H13 Magnitude, A | 37903 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H13 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H13 Angle | 37905 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H13 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H14 Magnitude, A | 37909 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H14 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H14 Angle | 37911 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H14 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H15 Magnitude, A | 37915 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H15 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H15 Angle | 37917 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H15 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H16 Magnitude, A | 37921 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H16 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H16 Angle | 37923 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H16 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H17 Magnitude, A | 37927 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H17 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H17 Angle | 37929 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H17 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H18 Magnitude, A | 37933 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H18 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H18 Angle | 37935 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H18 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H19 Magnitude, A | 37939 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H19 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H19 Angle | 37941 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H19 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H20 Magnitude, A | 37945 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H20 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H20 Angle | 37947 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H20 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H21 Magnitude, A | 37951 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H21 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H21 Angle | 37953 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H21 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H22 Magnitude, A | 37957 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H22 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H22 Angle | 37959 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H22 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H23 Magnitude, A | 37963 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H23 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H23 Angle | 37965 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H23 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H24 Magnitude, A | 37969 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H24 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H24 Angle | 37971 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H24 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H25 Magnitude, A | 37975 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H25 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H25 Angle | 37977 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H25 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H26 Magnitude, A | 37981 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H26 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H26 Angle | 37983 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H26 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H27 Magnitude, A | 37987 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H27 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H27 Angle | 37989 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H27 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H28 Magnitude, A | 37993 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H28 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H28 Angle | 37995 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H28 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H29 Magnitude, A | 37999 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H29 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H29 Angle | 38001 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H29 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H30 Magnitude, A | 38005 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H30 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H30 Angle | 38007 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H30 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H31 Magnitude, A | 38011 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H31 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H31 Angle | 38013 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H31 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H32 Magnitude, A | 38017 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H32 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H32 Angle | 38019 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H32 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H33 Magnitude, A | 38023 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H33 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H33 Angle | 38025 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H33 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H34 Magnitude, A | 38029 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H34 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H34 Angle | 38031 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H34 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H35 Magnitude, A | 38035 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H35 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H35 Angle | 38037 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H35 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H36 Magnitude, A | 38041 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H36 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H36 Angle | 38043 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H36 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H37 Magnitude, A | 38047 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H37 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H37 Angle | 38049 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H37 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H38 Magnitude, A | 38053 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H38 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H38 Angle | 38055 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H38 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H39 Magnitude, A | 38059 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H39 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H39 Angle | 38061 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H39 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H40 Magnitude, A | 38065 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H40 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H40 Angle | 38067 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H40 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H41 Magnitude, A | 38071 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H41 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H41 Angle | 38073 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H41 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H42 Magnitude, A | 38077 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H42 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H42 Angle | 38079 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H42 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H43 Magnitude, A | 38083 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H43 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H43 Angle | 38085 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H43 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H44 Magnitude, A | 38089 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H44 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H44 Angle | 38091 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H44 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H45 Magnitude, A | 38095 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H45 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H45 Angle | 38097 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H45 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H46 Magnitude, A | 38101 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H46 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H46 Angle | 38103 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H46 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H47 Magnitude, A | 38107 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H47 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H47 Angle | 38109 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H47 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H48 Magnitude, A | 38113 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H48 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H48 Angle | 38115 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H48 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H49 Magnitude, A | 38119 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H49 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H49 Angle | 38121 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H49 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H50 Magnitude, A | 38125 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H50 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H50 Angle | 38127 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H50 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H51 Magnitude, A | 38131 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H51 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H51 Angle | 38133 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H51 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H52 Magnitude, A | 38137 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H52 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H52 Angle | 38139 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H52 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H53 Magnitude, A | 38143 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H53 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H53 Angle | 38145 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H53 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H54 Magnitude, A | 38149 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H54 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H54 Angle | 38151 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H54 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H55 Magnitude, A | 38155 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H55 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H55 Angle | 38157 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H55 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H56 Magnitude, A | 38161 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H56 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H56 Angle | 38163 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H56 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H57 Magnitude, A | 38167 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H57 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H57 Angle | 38169 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H57 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H58 Magnitude, A | 38173 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H58 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H58 Angle | 38175 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H58 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H59 Magnitude, A | 38179 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H59 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H59 Angle | 38181 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H59 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H60 Magnitude, A | 38185 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H60 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H60 Angle | 38187 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H60 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H61 Magnitude, A | 38191 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H61 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H61 Angle | 38193 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H61 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H62 Magnitude, A | 38197 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H62 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H62 Angle | 38199 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H62 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current B, H63 Magnitude, A | 38203 | 2 | FLOAT32 | A | R/O | numeric | --- | I2 H63 Mag 10m | A | PQM | PDMD_I2_H1_MAG_10M
Current B, H63 Angle | 38205 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I2 H63 Ang 10m | DEGREES | PQM | PDMD_I2_H1_MAG_10M
Current C, H1 Magnitude, A | 38219 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H1 Mag 10m | A | PQM | BASE_PDMD_I3_H1_MAG_10M
Current C, H1 Angle | 38221 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H1 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H2 Magnitude, A | 38225 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H2 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H2 Angle | 38227 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H2 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H3 Magnitude, A | 38231 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H3 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H3 Angle | 38233 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H3 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H4 Magnitude, A | 38237 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H4 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H4 Angle | 38239 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H4 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H5 Magnitude, A | 38243 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H5 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H5 Angle | 38245 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H5 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H6 Magnitude, A | 38249 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H6 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H6 Angle | 38251 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H6 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H7 Magnitude, A | 38255 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H7 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H7 Angle | 38257 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H7 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H8 Magnitude, A | 38261 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H8 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H8 Angle | 38263 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H8 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H9 Magnitude, A | 38267 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H9 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H9 Angle | 38269 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H9 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H10 Magnitude, A | 38273 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H10 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H10 Angle | 38275 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H10 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H11 Magnitude, A | 38279 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H11 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H11 Angle | 38281 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H11 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H12 Magnitude, A | 38285 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H12 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H12 Angle | 38287 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H12 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H13 Magnitude, A | 38291 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H13 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H13 Angle | 38293 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H13 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H14 Magnitude, A | 38297 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H14 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H14 Angle | 38299 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H14 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H15 Magnitude, A | 38303 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H15 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H15 Angle | 38305 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H15 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H16 Magnitude, A | 38309 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H16 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H16 Angle | 38311 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H16 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H17 Magnitude, A | 38315 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H17 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H17 Angle | 38317 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H17 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H18 Magnitude, A | 38321 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H18 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H18 Angle | 38323 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H18 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H19 Magnitude, A | 38327 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H19 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H19 Angle | 38329 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H19 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H20 Magnitude, A | 38333 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H20 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H20 Angle | 38335 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H20 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H21 Magnitude, A | 38339 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H21 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H21 Angle | 38341 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H21 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H22 Magnitude, A | 38345 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H22 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H22 Angle | 38347 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H22 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H23 Magnitude, A | 38351 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H23 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H23 Angle | 38353 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H23 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H24 Magnitude, A | 38357 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H24 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H24 Angle | 38359 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H24 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H25 Magnitude, A | 38363 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H25 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H25 Angle | 38365 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H25 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H26 Magnitude, A | 38369 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H26 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H26 Angle | 38371 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H26 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H27 Magnitude, A | 38375 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H27 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H27 Angle | 38377 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H27 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H28 Magnitude, A | 38381 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H28 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H28 Angle | 38383 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H28 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H29 Magnitude, A | 38387 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H29 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H29 Angle | 38389 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H29 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H30 Magnitude, A | 38393 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H30 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H30 Angle | 38395 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H30 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H31 Magnitude, A | 38399 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H31 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H31 Angle | 38401 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H31 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H32 Magnitude, A | 38405 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H32 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H32 Angle | 38407 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H32 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H33 Magnitude, A | 38411 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H33 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H33 Angle | 38413 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H33 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H34 Magnitude, A | 38417 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H34 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H34 Angle | 38419 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H34 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H35 Magnitude, A | 38423 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H35 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H35 Angle | 38425 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H35 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H36 Magnitude, A | 38429 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H36 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H36 Angle | 38431 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H36 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H37 Magnitude, A | 38435 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H37 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H37 Angle | 38437 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H37 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H38 Magnitude, A | 38441 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H38 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H38 Angle | 38443 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H38 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H39 Magnitude, A | 38447 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H39 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H39 Angle | 38449 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H39 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H40 Magnitude, A | 38453 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H40 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H40 Angle | 38455 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H40 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H41 Magnitude, A | 38459 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H41 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H41 Angle | 38461 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H41 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H42 Magnitude, A | 38465 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H42 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H42 Angle | 38467 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H42 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H43 Magnitude, A | 38471 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H43 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H43 Angle | 38473 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H43 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H44 Magnitude, A | 38477 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H44 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H44 Angle | 38479 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H44 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H45 Magnitude, A | 38483 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H45 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H45 Angle | 38485 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H45 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H46 Magnitude, A | 38489 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H46 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H46 Angle | 38491 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H46 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H47 Magnitude, A | 38495 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H47 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H47 Angle | 38497 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H47 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H48 Magnitude, A | 38501 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H48 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H48 Angle | 38503 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H48 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H49 Magnitude, A | 38507 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H49 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H49 Angle | 38509 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H49 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H50 Magnitude, A | 38513 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H50 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H50 Angle | 38515 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H50 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H51 Magnitude, A | 38519 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H51 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H51 Angle | 38521 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H51 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H52 Magnitude, A | 38525 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H52 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H52 Angle | 38527 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H52 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H53 Magnitude, A | 38531 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H53 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H53 Angle | 38533 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H53 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H54 Magnitude, A | 38537 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H54 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H54 Angle | 38539 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H54 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H55 Magnitude, A | 38543 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H55 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H55 Angle | 38545 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H55 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H56 Magnitude, A | 38549 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H56 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H56 Angle | 38551 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H56 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H57 Magnitude, A | 38555 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H57 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H57 Angle | 38557 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H57 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H58 Magnitude, A | 38561 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H58 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H58 Angle | 38563 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H58 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H59 Magnitude, A | 38567 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H59 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H59 Angle | 38569 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H59 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H60 Magnitude, A | 38573 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H60 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H60 Angle | 38575 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H60 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H61 Magnitude, A | 38579 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H61 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H61 Angle | 38581 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H61 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H62 Magnitude, A | 38585 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H62 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H62 Angle | 38587 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H62 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
Current C, H63 Magnitude, A | 38591 | 2 | FLOAT32 | A | R/O | numeric | --- | I3 H63 Mag 10m | A | PQM | PDMD_I3_H1_MAG_10M
Current C, H63 Angle | 38593 | 2 | FLOAT32 | degrees | R/O | numeric | --- | I3 H63 Ang 10m | DEGREES | PQM | PDMD_I3_H1_MAG_10M
THD Current A 2 Hour | 39371 | 2 | FLOAT32 | --- | R/O | numeric | --- | I1 THD 2hr | PERCENT | PQM | None
THD Current B 2 Hour | 39373 | 2 | FLOAT32 | --- | R/O | numeric | --- | I2 THD 2hr | PERCENT | PQM | None
THD Current C 2 Hour | 39375 | 2 | FLOAT32 | --- | R/O | numeric | --- | I3 THD 2hr | PERCENT | PQM | None
THD Voltage A-N 2 Hour | 39401 | 2 | FLOAT32 | --- | R/O | numeric | --- | V1 THD 2hr | PERCENT | PQM | None
THD Voltage B-N 2 Hour | 39403 | 2 | FLOAT32 | --- | R/O | numeric | --- | V2 THD 2hr | PERCENT | PQM | None
THD Voltage C-N 2 Hour | 39405 | 2 | FLOAT32 | --- | R/O | numeric | --- | V3 THD 2hr | PERCENT | PQM | None
Voltage, Positive Sequence, Magnitude | 39441 | 2 | FLOAT32 | V | R/O | numeric | --- | V PosSeqMag2h | V | PQM | None
Voltage, Negative Sequence, Magnitude | 39445 | 2 | FLOAT32 | V | R/O | numeric | --- | V NegSeqMag2h | V | PQM | None
Voltage, Zero Sequence, Magnitude | 39449 | 2 | FLOAT32 | V | R/O | numeric | --- | V ZeroSeqMag2h | V | PQM | None
Long-Term Flicker (Plt), A-N | 39459 | 2 | FLOAT32 | --- | R/O | numeric | --- | Phase 1 Plt | NONE | PQM | None
Long-Term Flicker (Plt), B-N | 39461 | 2 | FLOAT32 | --- | R/O | numeric | --- | Phase 2 Plt | NONE | PQM | None
Long-Term Flicker (Plt), C-N | 39463 | 2 | FLOAT32 | --- | R/O | numeric | --- | Phase 3 Plt | NONE | PQM | None
Frequency 10m Mean | 40000 | 2 | FLOAT32 | Hz | R/O | numeric | --- | PQ Freq mean | HZ | ECM | None
Frequency 10m Low | 40002 | 2 | FLOAT32 | Hz | R/O | numeric | --- | PQ Freq low | HZ | ECM | None
Frequency 10m High | 40004 | 2 | FLOAT32 | Hz | R/O | numeric | --- | PQ Freq high | HZ | ECM | None
Frequency Minimum | 40006 | 2 | FLOAT32 | Hz | R/O | numeric | --- | PQ Freq mn-op | HZ | ECM | None
Frequency Maximum | 40008 | 2 | FLOAT32 | Hz | R/O | numeric | --- | PQ Freq mx-op | HZ | ECM | None
V1 10m Mean | 40010 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V1 mean | PT_V | ECM | None
V1 10m Low | 40012 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V1 low | PT_V | ECM | None
V1 10m High | 40014 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V1 high | PT_V | ECM | None
V2 10m Mean | 40016 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V2 mean | PT_V | ECM | None
V2 10m Low | 40018 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V2 low | PT_V | ECM | None
V2 10m High | 40020 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V2 high | PT_V | ECM | None
V3 10m Mean | 40022 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V3 mean | PT_V | ECM | None
V3 10m Low | 40024 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V3 low | PT_V | ECM | None
V3 10m High | 40026 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V3 high | PT_V | ECM | None
THD V1 10m Mean | 40028 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 THD 10m | PERCENT | ECM | None
THD V1 10m Low | 40030 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 THD mn | PERCENT | ECM | None
THD V1 10m High | 40032 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 THD mx | PERCENT | ECM | None
THD V2 10m Mean | 40034 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 THD 10m | PERCENT | ECM | None
THD V2 10m Low | 40036 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 THD mn | PERCENT | ECM | None
THD V2 10m High | 40038 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 THD mx | PERCENT | ECM | None
THD V3 10m Mean | 40040 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 THD 10m | PERCENT | ECM | None
THD V3 10m Low | 40042 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 THD mn | PERCENT | ECM | None
THD V3 10m High | 40044 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 THD mx | PERCENT | ECM | None
Total Even HD V1 10m Low | 40046 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 TEHD mn | PERCENT | ECM | None
Total Even HD V1 10m High | 40048 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 TEHD mx | PERCENT | ECM | None
Total Even HD V1 10m Mean | 40050 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 TEHD 10m | PERCENT | ECM | None
Total Odd HD V1 10m Low | 40052 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 TOHD mn | PERCENT | ECM | None
Total Odd HD V1 10m High | 40054 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 TOHD mx | PERCENT | ECM | None
Total Odd HD V1 10m Mean | 40056 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 TOHD 10m | PERCENT | ECM | None
Total Even HD V2 10m Low | 40058 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 TEHD mn | PERCENT | ECM | None
Total Even HD V2 10m High | 40060 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 TEHD mx | PERCENT | ECM | None
Total Even HD V2 10m Mean | 40062 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 TEHD 10m | PERCENT | ECM | None
Total Odd HD V2 10m Low | 40064 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 TOHD mn | PERCENT | ECM | None
Total Odd HD V2 10m High | 40066 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 TOHD mx | PERCENT | ECM | None
Total Odd HD V2 10m Mean | 40068 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 TOHD 10m | PERCENT | ECM | None
Total Even HD V3 10m Low | 40070 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 TEHD mn | PERCENT | ECM | None
Total Even HD V3 10m High | 40072 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 TEHD mx | PERCENT | ECM | None
Total Even HD V3 10m Mean | 40074 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 TEHD 10m | PERCENT | ECM | None
Total Odd HD V3 10m Low | 40076 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 TOHD mn | PERCENT | ECM | None
Total Odd HD V3 10m High | 40078 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 TOHD mx | PERCENT | ECM | None
Total Odd HD V3 10m Mean | 40080 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 TOHD 10m | PERCENT | ECM | None
Voltage unbalance 10m min | 40082 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ Vunbal mean mn | PERCENT | ECM | None
Voltage unbalance 10m max | 40084 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ Vunbal mean mx | PERCENT | ECM | None
V1 Dip min | 40086 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 Dip mn | PERCENT | ECM | None
V2 Dip min | 40088 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 Dip mn | PERCENT | ECM | None
V3 Dip min | 40090 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 Dip mn | PERCENT | ECM | None
V1 Overvoltage max | 40092 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 Overvolt mx | PERCENT | ECM | None
V2 Overvoltage max | 40094 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 Overvolt mx | PERCENT | ECM | None
V3 Overvoltage max | 40096 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 Overvolt mx | PERCENT | ECM | None
V1 short term min | 40098 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 Pst mn | NONE | ECM | None
V1 short term max | 40100 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V1 Pst mx | NONE | ECM | None
V2 short term min | 40102 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 Pst mn | NONE | ECM | None
V2 short term max | 40104 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V2 Pst mx | NONE | ECM | None
V3 short term min | 40106 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 Pst mn | NONE | ECM | None
V3 short term max | 40108 | 2 | FLOAT32 | --- | R/O | numeric | --- | PQ V3 Pst mx | NONE | ECM | None
V1 10m Mean max | 40110 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V1 mean mx | PT_V | ECM | None
V1 10m Mean min | 40112 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V1 mean mn | PT_V | ECM | None
V2 10m Mean max | 40114 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V2 mean mx | PT_V | ECM | None
V2 10m Mean min | 40116 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V2 mean mn | PT_V | ECM | None
V3 10m Mean max | 40118 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V3 mean mx | PT_V | ECM | None
V3 10m Mean min | 40120 | 2 | FLOAT32 | V | R/O | numeric | --- | PQ V3 mean mn | PT_V | ECM | None
THD V12 10m Mean | 40122 | 2 | FLOAT32 | % | R/O | numeric | --- | PQ V12 THD 10m | PERCENT | ECM | None
THD V23 10m Mean | 40124 | 2 | FLOAT32 | % | R/O | numeric | --- | PQ V23 THD 10m | PERCENT | ECM | None
THD V31 10m Mean | 40126 | 2 | FLOAT32 | % | R/O | numeric | --- | PQ V31 THD 10m | PERCENT | ECM | None
V1 Num Intervals Valid | 40206 | 1 | INT16U | --- | R/O | numeric | --- | V1-Mag N | NONE | ECM | None
V1 Num Intervals Exceed 1 | 40207 | 1 | INT16U | --- | R/O | numeric | --- | V1-Mag N1 | NONE | ECM | None
V1 Num Intervals Exceed 2 | 40208 | 1 | INT16U | --- | R/O | numeric | --- | V1-Mag N2 | NONE | ECM | None
V1 Num Intervals Invalid | 40209 | 1 | INT16U | --- | R/O | numeric | --- | V1-Mag N invld | NONE | ECM | None
V2 Num Intervals Valid | 40212 | 1 | INT16U | --- | R/O | numeric | --- | V2-Mag N | NONE | ECM | None
V2 Num Intervals Exceed 1 | 40213 | 1 | INT16U | --- | R/O | numeric | --- | V2-Mag N1 | NONE | ECM | None
V2 Num Intervals Exceed 2 | 40214 | 1 | INT16U | --- | R/O | numeric | --- | V2-Mag N2 | NONE | ECM | None
V2 Num Intervals Invalid | 40215 | 1 | INT16U | --- | R/O | numeric | --- | V2-Mag N invld | NONE | ECM | None
V3 Num Intervals Valid | 40218 | 1 | INT16U | --- | R/O | numeric | --- | V3-Mag N | NONE | ECM | None
V3 Num Intervals Exceed 1 | 40219 | 1 | INT16U | --- | R/O | numeric | --- | V3-Mag N1 | NONE | ECM | None
V3 Num Intervals Exceed 2 | 40220 | 1 | INT16U | --- | R/O | numeric | --- | V3-Mag N2 | NONE | ECM | None
V3 Num Intervals Invalid | 40221 | 1 | INT16U | --- | R/O | numeric | --- | V3-Mag N invld | NONE | ECM | None
V1 Harm Num Intervals Valid | 40224 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm N | NONE | ECM | None
V1 Harm Num Intervals Exceed 1 | 40225 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm N1 | NONE | ECM | None
V1 Harm Num Intervals Exceed 2 | 40226 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm N2 | NONE | ECM | None
V1 Harm Num Intervals Invalid | 40227 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm N invld | NONE | ECM | None
V2 Harm Num Intervals Valid | 40230 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm N | NONE | ECM | None
V2 Harm Num Intervals Exceed 1 | 40231 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm N1 | NONE | ECM | None
V2 Harm Num Intervals Exceed 2 | 40232 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm N2 | NONE | ECM | None
V2 Harm Num Intervals Invalid | 40233 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm N invld | NONE | ECM | None
V3 Harm Num Intervals Valid | 40236 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm N | NONE | ECM | None
V3 Harm Num Intervals Exceed 1 | 40237 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm N1 | NONE | ECM | None
V3 Harm Num Intervals Exceed 2 | 40238 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm N2 | NONE | ECM | None
V3 Harm Num Intervals Invalid | 40239 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm N invld | NONE | ECM | None
Voltage Unbal Num Intervals Valid | 40242 | 1 | INT16U | --- | R/O | numeric | --- | Vunbal N | NONE | ECM | None
Voltage Unbal Num Intervals Exceeded 1 | 40243 | 1 | INT16U | --- | R/O | numeric | --- | Vunbal N1 | NONE | ECM | None
Voltage Unbal Num Intervals Invalid | 40244 | 1 | INT16U | --- | R/O | numeric | --- | Vunbal N invld | NONE | ECM | None
V1-Dip A1 | 40246 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip A1 | NONE | ECM | BASE_PDMD_V1_DIP_A1
V1-Dip B1 | 40247 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip B1 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip C1 | 40248 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip C1 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip D1 | 40249 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip D1 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip A2 | 40250 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip A2 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip B2 | 40251 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip B2 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip C2 | 40252 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip C2 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip D2 | 40253 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip D2 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip A3 | 40254 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip A3 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip B3 | 40255 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip B3 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip C3 | 40256 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip C3 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip D3 | 40257 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip D3 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip A4 | 40258 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip A4 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip B4 | 40259 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip B4 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip C4 | 40260 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip C4 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip D4 | 40261 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip D4 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip A5 | 40262 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip A5 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip B5 | 40263 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip B5 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip C5 | 40264 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip C5 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip D5 | 40265 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip D5 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip X1 | 40266 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip X1 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip X2 | 40267 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip X2 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip X3 | 40268 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip X3 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip X4 | 40269 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip X4 | NONE | ECM | PDMD_V1_DIP_A1
V1-Dip X5 | 40270 | 1 | INT16U | --- | R/O | numeric | --- | V1-Dip X5 | NONE | ECM | PDMD_V1_DIP_A1
V2-Dip A1 | 40271 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip A1 | NONE | ECM | BASE_PDMD_V2_DIP_A1
V2-Dip B1 | 40272 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip B1 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip C1 | 40273 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip C1 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip D1 | 40274 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip D1 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip A2 | 40275 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip A2 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip B2 | 40276 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip B2 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip C2 | 40277 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip C2 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip D2 | 40278 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip D2 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip A3 | 40279 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip A3 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip B3 | 40280 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip B3 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip C3 | 40281 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip C3 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip D3 | 40282 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip D3 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip A4 | 40283 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip A4 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip B4 | 40284 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip B4 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip C4 | 40285 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip C4 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip D4 | 40286 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip D4 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip A5 | 40287 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip A5 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip B5 | 40288 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip B5 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip C5 | 40289 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip C5 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip D5 | 40290 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip D5 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip X1 | 40291 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip X1 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip X2 | 40292 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip X2 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip X3 | 40293 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip X3 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip X4 | 40294 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip X4 | NONE | ECM | PDMD_V2_DIP_A1
V2-Dip X5 | 40295 | 1 | INT16U | --- | R/O | numeric | --- | V2-Dip X5 | NONE | ECM | PDMD_V2_DIP_A1
V3-Dip A1 | 40296 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip A1 | NONE | ECM | BASE_PDMD_V3_DIP_A1
V3-Dip B1 | 40297 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip B1 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip C1 | 40298 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip C1 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip D1 | 40299 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip D1 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip A2 | 40300 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip A2 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip B2 | 40301 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip B2 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip C2 | 40302 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip C2 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip D2 | 40303 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip D2 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip A3 | 40304 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip A3 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip B3 | 40305 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip B3 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip C3 | 40306 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip C3 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip D3 | 40307 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip D3 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip A4 | 40308 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip A4 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip B4 | 40309 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip B4 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip C4 | 40310 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip C4 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip D4 | 40311 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip D4 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip A5 | 40312 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip A5 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip B5 | 40313 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip B5 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip C5 | 40314 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip C5 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip D5 | 40315 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip D5 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip X1 | 40316 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip X1 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip X2 | 40317 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip X2 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip X3 | 40318 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip X3 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip X4 | 40319 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip X4 | NONE | ECM | PDMD_V3_DIP_A1
V3-Dip X5 | 40320 | 1 | INT16U | --- | R/O | numeric | --- | V3-Dip X5 | NONE | ECM | PDMD_V3_DIP_A1
V1-Ovrvlt S1 | 40321 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt S1 | NONE | ECM | BASE_PDMD_V1_OVRVLT_S1
V1-Ovrvlt T1 | 40322 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt T1 | NONE | ECM | PDMD_V1_OVRVLT_S1
V1-Ovrvlt S2 | 40323 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt S2 | NONE | ECM | PDMD_V1_OVRVLT_S1
V1-Ovrvlt T2 | 40324 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt T2 | NONE | ECM | PDMD_V1_OVRVLT_S1
V1-Ovrvlt S3 | 40325 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt S3 | NONE | ECM | PDMD_V1_OVRVLT_S1
V1-Ovrvlt T3 | 40326 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt T3 | NONE | ECM | PDMD_V1_OVRVLT_S1
V1-Ovrvlt S4 | 40327 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt S4 | NONE | ECM | PDMD_V1_OVRVLT_S1
V1-Ovrvlt T4 | 40328 | 1 | INT16U | --- | R/O | numeric | --- | V1-Ovrvlt T4 | NONE | ECM | PDMD_V1_OVRVLT_S1
V2-Ovrvlt S1 | 40329 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt S1 | NONE | ECM | BASE_PDMD_V2_OVRVLT_S1
V2-Ovrvlt T1 | 40330 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt T1 | NONE | ECM | PDMD_V2_OVRVLT_S1
V2-Ovrvlt S2 | 40331 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt S2 | NONE | ECM | PDMD_V2_OVRVLT_S1
V2-Ovrvlt T2 | 40332 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt T2 | NONE | ECM | PDMD_V2_OVRVLT_S1
V2-Ovrvlt S3 | 40333 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt S3 | NONE | ECM | PDMD_V2_OVRVLT_S1
V2-Ovrvlt T3 | 40334 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt T3 | NONE | ECM | PDMD_V2_OVRVLT_S1
V2-Ovrvlt S4 | 40335 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt S4 | NONE | ECM | PDMD_V2_OVRVLT_S1
V2-Ovrvlt T4 | 40336 | 1 | INT16U | --- | R/O | numeric | --- | V2-Ovrvlt T4 | NONE | ECM | PDMD_V2_OVRVLT_S1
V3-Ovrvlt S1 | 40337 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt S1 | NONE | ECM | BASE_PDMD_V3_OVRVLT_S1
V3-Ovrvlt T1 | 40338 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt T1 | NONE | ECM | PDMD_V3_OVRVLT_S1
V3-Ovrvlt S2 | 40339 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt S2 | NONE | ECM | PDMD_V3_OVRVLT_S1
V3-Ovrvlt T2 | 40340 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt T2 | NONE | ECM | PDMD_V3_OVRVLT_S1
V3-Ovrvlt S3 | 40341 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt S3 | NONE | ECM | PDMD_V3_OVRVLT_S1
V3-Ovrvlt T3 | 40342 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt T3 | NONE | ECM | PDMD_V3_OVRVLT_S1
V3-Ovrvlt S4 | 40343 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt S4 | NONE | ECM | PDMD_V3_OVRVLT_S1
V3-Ovrvlt T4 | 40344 | 1 | INT16U | --- | R/O | numeric | --- | V3-Ovrvlt T4 | NONE | ECM | PDMD_V3_OVRVLT_S1
V1-Intrpt N1 | 40345 | 1 | INT16U | --- | R/O | numeric | --- | V1-Intrpt N1 | NONE | ECM | BASE_PDMD_V1_INTRPT_N1
V1-Intrpt N2 | 40346 | 1 | INT16U | --- | R/O | numeric | --- | V1-Intrpt N2 | NONE | ECM | PDMD_V1_INTRPT_N1
V1-Intrpt N3 | 40347 | 1 | INT16U | --- | R/O | numeric | --- | V1-Intrpt N3 | NONE | ECM | PDMD_V1_INTRPT_N1
V2-Intrpt N1 | 40348 | 1 | INT16U | --- | R/O | numeric | --- | V2-Intrpt N1 | NONE | ECM | BASE_PDMD_V2_INTRPT_N1
V2-Intrpt N2 | 40349 | 1 | INT16U | --- | R/O | numeric | --- | V2-Intrpt N2 | NONE | ECM | PDMD_V2_INTRPT_N1
V2-Intrpt N3 | 40350 | 1 | INT16U | --- | R/O | numeric | --- | V2-Intrpt N3 | NONE | ECM | PDMD_V2_INTRPT_N1
V3-Intrpt N1 | 40351 | 1 | INT16U | --- | R/O | numeric | --- | V3-Intrpt N1 | NONE | ECM | BASE_PDMD_V3_INTRPT_N1
V3-Intrpt N2 | 40352 | 1 | INT16U | --- | R/O | numeric | --- | V3-Intrpt N2 | NONE | ECM | PDMD_V3_INTRPT_N1
V3-Intrpt N3 | 40353 | 1 | INT16U | --- | R/O | numeric | --- | V3-Intrpt N3 | NONE | ECM | PDMD_V3_INTRPT_N1
V1-Flck N | 40354 | 1 | INT16U | --- | R/O | numeric | --- | V1-Flck N | NONE | ECM | None
V1-Flck N1 | 40355 | 1 | INT16U | --- | R/O | numeric | --- | V1-Flck N1 | NONE | ECM | None
V1-Flck N invld | 40356 | 1 | INT16U | --- | R/O | numeric | --- | V1-Flck N invld | NONE | ECM | None
V2-Flck N | 40358 | 1 | INT16U | --- | R/O | numeric | --- | V2-Flck N | NONE | ECM | None
V2-Flck N1 | 40359 | 1 | INT16U | --- | R/O | numeric | --- | V2-Flck N1 | NONE | ECM | None
V2-Flck N invld | 40360 | 1 | INT16U | --- | R/O | numeric | --- | V2-Flck N invld | NONE | ECM | None
V3-Flck N | 40362 | 1 | INT16U | --- | R/O | numeric | --- | V3-Flck N | NONE | ECM | None
V3-Flck N1 | 40363 | 1 | INT16U | --- | R/O | numeric | --- | V3-Flck N1 | NONE | ECM | None
V3-Flck N invld | 40364 | 1 | INT16U | --- | R/O | numeric | --- | V3-Flck N invld | NONE | ECM | None
V1 Interharmonics Num Intervals Valid | 40366 | 1 | INT16U | --- | R/O | numeric | --- | V1-Inthrm N | NONE | ECM | None
V1 Interharmonics Num Intervals Exceed 1 | 40367 | 1 | INT16U | --- | R/O | numeric | --- | V1-Inthrm N1 | NONE | ECM | None
V1 Interharmonics Num Intervals Invalid | 40369 | 1 | INT16U | --- | R/O | numeric | --- | V1-Inthrm N invld | NONE | ECM | None
V2 Interharmonics Num Intervals Valid | 40371 | 1 | INT16U | --- | R/O | numeric | --- | V2-Inthrm N | NONE | ECM | None
V2 Interharmonics Num Intervals Exceed 1 | 40372 | 1 | INT16U | --- | R/O | numeric | --- | V2-Inthrm N1 | NONE | ECM | None
V2 Interharmonics Num Intervals Invalid | 40374 | 1 | INT16U | --- | R/O | numeric | --- | V2-Inthrm N invld | NONE | ECM | None
V3 Interharmonics Num Intervals Valid | 40376 | 1 | INT16U | --- | R/O | numeric | --- | V3-Inthrm N | NONE | ECM | None
V3 Interharmonics Num Intervals Exceed 1 | 40377 | 1 | INT16U | --- | R/O | numeric | --- | V3-Inthrm N1 | NONE | ECM | None
V3 Interharmonics Num Intervals Invalid | 40379 | 1 | INT16U | --- | R/O | numeric | --- | V3-Inthrm N invld | NONE | ECM | None
V1 Mains Signalling Num Intervals Valid | 40381 | 1 | INT16U | --- | R/O | numeric | --- | V1-MSignal N | NONE | ECM | None
V1 Mains Signalling Num Intervals Exceed 1 | 40382 | 1 | INT16U | --- | R/O | numeric | --- | V1-MSignal N1 | NONE | ECM | None
V1 Mains Signalling Num Intervals Invalid | 40383 | 1 | INT16U | --- | R/O | numeric | --- | V1-MSignal N invld | NONE | ECM | None
V2 Mains Signalling Num Intervals Valid | 40385 | 1 | INT16U | --- | R/O | numeric | --- | V2-MSignal N | NONE | ECM | None
V2 Mains Signalling Num Intervals Exceed 1 | 40386 | 1 | INT16U | --- | R/O | numeric | --- | V2-MSignal N1 | NONE | ECM | None
V2 Mains Signalling Num Intervals Invalid | 40387 | 1 | INT16U | --- | R/O | numeric | --- | V2-MSignal N invld | NONE | ECM | None
V3 Mains Signalling Num Intervals Valid | 40389 | 1 | INT16U | --- | R/O | numeric | --- | V3-MSignal N | NONE | ECM | None
V3 Mains Signalling Num Intervals Exceed 1 | 40390 | 1 | INT16U | --- | R/O | numeric | --- | V3-MSignal N1 | NONE | ECM | None
V3 Mains Signalling Num Intervals Invalid | 40391 | 1 | INT16U | --- | R/O | numeric | --- | V3-MSignal N invld | NONE | ECM | None
Freq Num Intervals Valid | 40393 | 2 | INT32U | --- | R/O | numeric | --- | Freq N | NONE | ECM | None
Freq Num Intervals Exceed 1 | 40395 | 2 | INT32U | --- | R/O | numeric | --- | Freq N1 | NONE | ECM | None
Freq Num Intervals Exceed 2 | 40397 | 2 | INT32U | --- | R/O | numeric | --- | Freq N2 | NONE | ECM | None
Freq Num Intervals Invalid | 40399 | 2 | INT32U | --- | R/O | numeric | --- | Freq N invld | NONE | ECM | None
Freq Num Intervals Exceed 1 / Valid | 40401 | 2 | FLOAT32 | % | R/O | numeric | --- | Freq N1/N | PERCENT | ECM | None
Freq Num Intervals Exceed 2 / Valid | 40403 | 2 | FLOAT32 | % | R/O | numeric | --- | Freq N2/N | PERCENT | ECM | None
V1 Num Intervals Exceed 1 / Valid | 40405 | 2 | FLOAT32 | % | R/O | numeric | --- | V1-Mag N1/N | PERCENT | ECM | None
V1 Num Intervals Exceed 2 / Valid | 40407 | 2 | FLOAT32 | % | R/O | numeric | --- | V1-Mag N2/N | PERCENT | ECM | None
V2 Num Intervals Exceed 1 / Valid | 40409 | 2 | FLOAT32 | % | R/O | numeric | --- | V2-Mag N1/N | PERCENT | ECM | None
V2 Num Intervals Exceed 2 / Valid | 40411 | 2 | FLOAT32 | % | R/O | numeric | --- | V2-Mag N2/N | PERCENT | ECM | None
V3 Num Intervals Exceed 1 / Valid | 40413 | 2 | FLOAT32 | % | R/O | numeric | --- | V3-Mag N1/N | PERCENT | ECM | None
V3 Num Intervals Exceed 2 / Valid | 40415 | 2 | FLOAT32 | % | R/O | numeric | --- | V3-Mag N2/N | PERCENT | ECM | None
V1 Harm Num Intervals Exceed 1 / Valid | 40417 | 2 | FLOAT32 | % | R/O | numeric | --- | V1-Hrm N1/N | PERCENT | ECM | None
V1 Harm Num Intervals Exceed 2 / Valid | 40419 | 2 | FLOAT32 | % | R/O | numeric | --- | V1-Hrm N2/N | PERCENT | ECM | None
V2 Harm Num Intervals Exceed 1 / Valid | 40421 | 2 | FLOAT32 | % | R/O | numeric | --- | V2-Hrm N1/N | PERCENT | ECM | None
V2 Harm Num Intervals Exceed 2 / Valid | 40423 | 2 | FLOAT32 | % | R/O | numeric | --- | V2-Hrm N2/N | PERCENT | ECM | None
V3 Harm Num Intervals Exceed 1 / Valid | 40425 | 2 | FLOAT32 | % | R/O | numeric | --- | V3-Hrm N1/N | PERCENT | ECM | None
V3 Harm Num Intervals Exceed 2 / Valid | 40427 | 2 | FLOAT32 | % | R/O | numeric | --- | V3-Hrm N2/N | PERCENT | ECM | None
Voltage Unbal Num Intervals Exceeded 1 / Valid | 40429 | 2 | FLOAT32 | % | R/O | numeric | --- | Vunbal N1/N | PERCENT | ECM | None
V1-Flck N1/N | 40431 | 2 | FLOAT32 | % | R/O | numeric | --- | V1-Flck N1/N | PERCENT | ECM | None
V2-Flck N1/N | 40433 | 2 | FLOAT32 | % | R/O | numeric | --- | V2-Flck N1/N | PERCENT | ECM | None
V3-Flck N1/N | 40435 | 2 | FLOAT32 | % | R/O | numeric | --- | V3-Flck N1/N | PERCENT | ECM | None
V-Swell S1 | 40437 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell S1 | NONE | ECM | BASE_PDMD_V_SWELL_S1
V-Swell T1 | 40438 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell T1 | NONE | ECM | PDMD_V_SWELL_S1
V-Swell S2 | 40439 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell S2 | NONE | ECM | PDMD_V_SWELL_S1
V-Swell T2 | 40440 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell T2 | NONE | ECM | PDMD_V_SWELL_S1
V-Swell S3 | 40441 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell S3 | NONE | ECM | PDMD_V_SWELL_S1
V-Swell T3 | 40442 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell T3 | NONE | ECM | PDMD_V_SWELL_S1
V-Swell S4 | 40443 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell S4 | NONE | ECM | PDMD_V_SWELL_S1
V-Swell T4 | 40444 | 1 | INT16U | --- | R/O | numeric | --- | V-Swell T4 | NONE | ECM | PDMD_V_SWELL_S1
V-Intrpt N1 | 40445 | 1 | INT16U | --- | R/O | numeric | --- | V-Intrpt N1 | NONE | ECM | BASE_PDMD_V_INTRPT_N1
V-Intrpt N2 | 40446 | 1 | INT16U | --- | R/O | numeric | --- | V-Intrpt N2 | NONE | ECM | PDMD_V_INTRPT_N1
V-Intrpt N3 | 40447 | 1 | INT16U | --- | R/O | numeric | --- | V-Intrpt N3 | NONE | ECM | PDMD_V_INTRPT_N1
V-Intrpt tot | 40448 | 1 | INT16U | --- | R/O | numeric | --- | V-Intrpt tot | NONE | ECM | PDMD_V_INTRPT_N1
V1 Mains Signalling Num Intervals Exceed 1 / Valid | 40449 | 2 | FLOAT32 | % | R/O | numeric | --- | V1-MSignal N1/N | PERCENT | ECM | None
V2 Mains Signalling Num Intervals Exceed 1 / Valid | 40451 | 2 | FLOAT32 | % | R/O | numeric | --- | V2-MSignal N1/N | PERCENT | ECM | None
V3 Mains Signalling Num Intervals Exceed 1 / Valid | 40453 | 2 | FLOAT32 | % | R/O | numeric | --- | V3-MSignal N1/N | PERCENT | ECM | None
V1 Interharmonics Num Intervals Exceed 1 / Valid | 40455 | 2 | FLOAT32 | % | R/O | numeric | --- | V1-Inthrm N1/N | PERCENT | ECM | None
V2 Interharmonics Num Intervals Exceed 1 / Valid | 40457 | 2 | FLOAT32 | % | R/O | numeric | --- | V2-Inthrm N1/N | PERCENT | ECM | None
V3 Interharmonics Num Intervals Exceed 1 / Valid | 40459 | 2 | FLOAT32 | % | R/O | numeric | --- | V3-Inthrm N1/N | PERCENT | ECM | None
RVC Count | 40461 | 1 | INT16U | --- | R/O | numeric | --- | RVC Count | NONE | ECM | None
V-Dip A1 | 40462 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip A1 | NONE | ECM | BASE_PDMD_V_DIP_A1
V-Dip B1 | 40463 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip B1 | NONE | ECM | PDMD_V_DIP_A1
V-Dip C1 | 40464 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip C1 | NONE | ECM | PDMD_V_DIP_A1
V-Dip D1 | 40465 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip D1 | NONE | ECM | PDMD_V_DIP_A1
V-Dip A2 | 40466 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip A2 | NONE | ECM | PDMD_V_DIP_A1
V-Dip B2 | 40467 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip B2 | NONE | ECM | PDMD_V_DIP_A1
V-Dip C2 | 40468 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip C2 | NONE | ECM | PDMD_V_DIP_A1
V-Dip D2 | 40469 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip D2 | NONE | ECM | PDMD_V_DIP_A1
V-Dip A3 | 40470 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip A3 | NONE | ECM | PDMD_V_DIP_A1
V-Dip B3 | 40471 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip B3 | NONE | ECM | PDMD_V_DIP_A1
V-Dip C3 | 40472 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip C3 | NONE | ECM | PDMD_V_DIP_A1
V-Dip D3 | 40473 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip D3 | NONE | ECM | PDMD_V_DIP_A1
V-Dip A4 | 40474 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip A4 | NONE | ECM | PDMD_V_DIP_A1
V-Dip B4 | 40475 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip B4 | NONE | ECM | PDMD_V_DIP_A1
V-Dip C4 | 40476 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip C4 | NONE | ECM | PDMD_V_DIP_A1
V-Dip D4 | 40477 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip D4 | NONE | ECM | PDMD_V_DIP_A1
V-Dip A5 | 40478 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip A5 | NONE | ECM | PDMD_V_DIP_A1
V-Dip B5 | 40479 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip B5 | NONE | ECM | PDMD_V_DIP_A1
V-Dip C5 | 40480 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip C5 | NONE | ECM | PDMD_V_DIP_A1
V-Dip D5 | 40481 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip D5 | NONE | ECM | PDMD_V_DIP_A1
V-Dip X1 | 40482 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip X1 | NONE | ECM | PDMD_V_DIP_A1
V-Dip X2 | 40483 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip X2 | NONE | ECM | PDMD_V_DIP_A1
V-Dip X3 | 40484 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip X3 | NONE | ECM | PDMD_V_DIP_A1
V-Dip X4 | 40485 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip X4 | NONE | ECM | PDMD_V_DIP_A1
V-Dip X5 | 40486 | 1 | INT16U | --- | R/O | numeric | --- | V-Dip X5 | NONE | ECM | PDMD_V_DIP_A1
V1 Num Intervals Valid | 40506 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Mag N | NONE | EPM | None
V1 Num Intervals Exceed 1 | 40507 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Mag N1 | NONE | EPM | None
V1 Num Intervals Exceed 2 | 40508 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Mag N2 | NONE | EPM | None
V1 Num Intervals Invalid | 40509 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Mag N invld | NONE | EPM | None
V2 Num Intervals Valid | 40512 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Mag N | NONE | EPM | None
V2 Num Intervals Exceed 1 | 40513 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Mag N1 | NONE | EPM | None
V2 Num Intervals Exceed 2 | 40514 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Mag N2 | NONE | EPM | None
V2 Num Intervals Invalid | 40515 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Mag N invld | NONE | EPM | None
V3 Num Intervals Valid | 40518 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Mag N | NONE | EPM | None
V3 Num Intervals Exceed 1 | 40519 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Mag N1 | NONE | EPM | None
V3 Num Intervals Exceed 2 | 40520 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Mag N2 | NONE | EPM | None
V3 Num Intervals Invalid | 40521 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Mag N invld | NONE | EPM | None
V1 Harm Num Intervals Valid | 40524 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm N | NONE | EPM | None
V1 Harm Num Intervals Exceed 1 | 40525 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm N1 | NONE | EPM | None
V1 Harm Num Intervals Exceed 2 | 40526 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm N2 | NONE | EPM | None
V1 Harm Num Intervals Invalid | 40527 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm N invld | NONE | EPM | None
V2 Harm Num Intervals Valid | 40530 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm N | NONE | EPM | None
V2 Harm Num Intervals Exceed 1 | 40531 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm N1 | NONE | EPM | None
V2 Harm Num Intervals Exceed 2 | 40532 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm N2 | NONE | EPM | None
V2 Harm Num Intervals Invalid | 40533 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm N invld | NONE | EPM | None
V3 Harm Num Intervals Valid | 40536 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm N | NONE | EPM | None
V3 Harm Num Intervals Exceed 1 | 40537 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm N1 | NONE | EPM | None
V3 Harm Num Intervals Exceed 2 | 40538 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm N2 | NONE | EPM | None
V3 Harm Num Intervals Invalid | 40539 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm N invld | NONE | EPM | None
Voltage Unbal Num Intervals Valid | 40542 | 1 | INT16U | --- | R/O | numeric | --- | PO Vunbal N | NONE | EPM | None
Voltage Unbal Num Intervals Exceeded 1 | 40543 | 1 | INT16U | --- | R/O | numeric | --- | PO Vunbal N1 | NONE | EPM | None
Voltage Unbal Num Intervals Invalid | 40544 | 1 | INT16U | --- | R/O | numeric | --- | PO Vunbal N invld | NONE | EPM | None
V1-Dip A1 | 40546 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip A1 | NONE | EPM | None
V1-Dip B1 | 40547 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip B1 | NONE | EPM | None
V1-Dip C1 | 40548 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip C1 | NONE | EPM | None
V1-Dip D1 | 40549 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip D1 | NONE | EPM | None
V1-Dip A2 | 40550 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip A2 | NONE | EPM | None
V1-Dip B2 | 40551 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip B2 | NONE | EPM | None
V1-Dip C2 | 40552 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip C2 | NONE | EPM | None
V1-Dip D2 | 40553 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip D2 | NONE | EPM | None
V1-Dip A3 | 40554 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip A3 | NONE | EPM | None
V1-Dip B3 | 40555 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip B3 | NONE | EPM | None
V1-Dip C3 | 40556 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip C3 | NONE | EPM | None
V1-Dip D3 | 40557 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip D3 | NONE | EPM | None
V1-Dip A4 | 40558 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip A4 | NONE | EPM | None
V1-Dip B4 | 40559 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip B4 | NONE | EPM | None
V1-Dip C4 | 40560 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip C4 | NONE | EPM | None
V1-Dip D4 | 40561 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip D4 | NONE | EPM | None
V1-Dip A5 | 40562 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip A5 | NONE | EPM | None
V1-Dip B5 | 40563 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip B5 | NONE | EPM | None
V1-Dip C5 | 40564 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip C5 | NONE | EPM | None
V1-Dip D5 | 40565 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip D5 | NONE | EPM | None
V1-Dip X1 | 40566 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip X1 | NONE | EPM | None
V1-Dip X2 | 40567 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip X2 | NONE | EPM | None
V1-Dip X3 | 40568 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip X3 | NONE | EPM | None
V1-Dip X4 | 40569 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip X4 | NONE | EPM | None
V1-Dip X5 | 40570 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Dip X5 | NONE | EPM | None
V2-Dip A1 | 40571 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip A1 | NONE | EPM | None
V2-Dip B1 | 40572 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip B1 | NONE | EPM | None
V2-Dip C1 | 40573 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip C1 | NONE | EPM | None
V2-Dip D1 | 40574 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip D1 | NONE | EPM | None
V2-Dip A2 | 40575 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip A2 | NONE | EPM | None
V2-Dip B2 | 40576 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip B2 | NONE | EPM | None
V2-Dip C2 | 40577 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip C2 | NONE | EPM | None
V2-Dip D2 | 40578 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip D2 | NONE | EPM | None
V2-Dip A3 | 40579 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip A3 | NONE | EPM | None
V2-Dip B3 | 40580 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip B3 | NONE | EPM | None
V2-Dip C3 | 40581 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip C3 | NONE | EPM | None
V2-Dip D3 | 40582 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip D3 | NONE | EPM | None
V2-Dip A4 | 40583 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip A4 | NONE | EPM | None
V2-Dip B4 | 40584 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip B4 | NONE | EPM | None
V2-Dip C4 | 40585 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip C4 | NONE | EPM | None
V2-Dip D4 | 40586 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip D4 | NONE | EPM | None
V2-Dip A5 | 40587 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip A5 | NONE | EPM | None
V2-Dip B5 | 40588 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip B5 | NONE | EPM | None
V2-Dip C5 | 40589 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip C5 | NONE | EPM | None
V2-Dip D5 | 40590 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip D5 | NONE | EPM | None
V2-Dip X1 | 40591 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip X1 | NONE | EPM | None
V2-Dip X2 | 40592 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip X2 | NONE | EPM | None
V2-Dip X3 | 40593 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip X3 | NONE | EPM | None
V2-Dip X4 | 40594 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip X4 | NONE | EPM | None
V2-Dip X5 | 40595 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Dip X5 | NONE | EPM | None
V3-Dip A1 | 40596 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip A1 | NONE | EPM | None
V3-Dip B1 | 40597 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip B1 | NONE | EPM | None
V3-Dip C1 | 40598 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip C1 | NONE | EPM | None
V3-Dip D1 | 40599 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip D1 | NONE | EPM | None
V3-Dip A2 | 40600 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip A2 | NONE | EPM | None
V3-Dip B2 | 40601 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip B2 | NONE | EPM | None
V3-Dip C2 | 40602 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip C2 | NONE | EPM | None
V3-Dip D2 | 40603 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip D2 | NONE | EPM | None
V3-Dip A3 | 40604 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip A3 | NONE | EPM | None
V3-Dip B3 | 40605 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip B3 | NONE | EPM | None
V3-Dip C3 | 40606 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip C3 | NONE | EPM | None
V3-Dip D3 | 40607 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip D3 | NONE | EPM | None
V3-Dip A4 | 40608 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip A4 | NONE | EPM | None
V3-Dip B4 | 40609 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip B4 | NONE | EPM | None
V3-Dip C4 | 40610 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip C4 | NONE | EPM | None
V3-Dip D4 | 40611 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip D4 | NONE | EPM | None
V3-Dip A5 | 40612 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip A5 | NONE | EPM | None
V3-Dip B5 | 40613 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip B5 | NONE | EPM | None
V3-Dip C5 | 40614 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip C5 | NONE | EPM | None
V3-Dip D5 | 40615 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip D5 | NONE | EPM | None
V3-Dip X1 | 40616 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip X1 | NONE | EPM | None
V3-Dip X2 | 40617 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip X2 | NONE | EPM | None
V3-Dip X3 | 40618 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip X3 | NONE | EPM | None
V3-Dip X4 | 40619 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip X4 | NONE | EPM | None
V3-Dip X5 | 40620 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Dip X5 | NONE | EPM | None
V1-Ovrvlt S1 | 40621 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt S1 | NONE | EPM | None
V1-Ovrvlt T1 | 40622 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt T1 | NONE | EPM | None
V1-Ovrvlt S2 | 40623 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt S2 | NONE | EPM | None
V1-Ovrvlt T2 | 40624 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt T2 | NONE | EPM | None
V1-Ovrvlt S3 | 40625 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt S3 | NONE | EPM | None
V1-Ovrvlt T3 | 40626 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt T3 | NONE | EPM | None
V1-Ovrvlt S4 | 40627 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt S4 | NONE | EPM | None
V1-Ovrvlt T4 | 40628 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Ovrvlt T4 | NONE | EPM | None
V2-Ovrvlt S1 | 40629 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt S1 | NONE | EPM | None
V2-Ovrvlt T1 | 40630 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt T1 | NONE | EPM | None
V2-Ovrvlt S2 | 40631 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt S2 | NONE | EPM | None
V2-Ovrvlt T2 | 40632 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt T2 | NONE | EPM | None
V2-Ovrvlt S3 | 40633 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt S3 | NONE | EPM | None
V2-Ovrvlt T3 | 40634 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt T3 | NONE | EPM | None
V2-Ovrvlt S4 | 40635 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt S4 | NONE | EPM | None
V2-Ovrvlt T4 | 40636 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Ovrvlt T4 | NONE | EPM | None
V3-Ovrvlt S1 | 40637 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt S1 | NONE | EPM | None
V3-Ovrvlt T1 | 40638 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt T1 | NONE | EPM | None
V3-Ovrvlt S2 | 40639 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt S2 | NONE | EPM | None
V3-Ovrvlt T2 | 40640 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt T2 | NONE | EPM | None
V3-Ovrvlt S3 | 40641 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt S3 | NONE | EPM | None
V3-Ovrvlt T3 | 40642 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt T3 | NONE | EPM | None
V3-Ovrvlt S4 | 40643 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt S4 | NONE | EPM | None
V3-Ovrvlt T4 | 40644 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Ovrvlt T4 | NONE | EPM | None
V1-Intrpt N1 | 40645 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Intrpt N1 | NONE | EPM | None
V1-Intrpt N2 | 40646 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Intrpt N2 | NONE | EPM | None
V1-Intrpt N3 | 40647 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Intrpt N3 | NONE | EPM | None
V2-Intrpt N1 | 40648 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Intrpt N1 | NONE | EPM | None
V2-Intrpt N2 | 40649 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Intrpt N2 | NONE | EPM | None
V2-Intrpt N3 | 40650 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Intrpt N3 | NONE | EPM | None
V3-Intrpt N1 | 40651 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Intrpt N1 | NONE | EPM | None
V3-Intrpt N2 | 40652 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Intrpt N2 | NONE | EPM | None
V3-Intrpt N3 | 40653 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Intrpt N3 | NONE | EPM | None
V1-Flck N | 40654 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Flck N | NONE | EPM | None
V1-Flck N1 | 40655 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Flck N1 | NONE | EPM | None
V1-Flck N invld | 40656 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Flck N invld | NONE | EPM | None
V2-Flck N | 40658 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Flck N | NONE | EPM | None
V2-Flck N1 | 40659 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Flck N1 | NONE | EPM | None
V2-Flck N invld | 40660 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Flck N invld | NONE | EPM | None
V3-Flck N | 40662 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Flck N | NONE | EPM | None
V3-Flck N1 | 40663 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Flck N1 | NONE | EPM | None
V3-Flck N invld | 40664 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Flck N invld | NONE | EPM | None
V1 Interharmonics Num Intervals Valid | 40666 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Inthrm N | NONE | EPM | None
V1 Interharmonics Num Intervals Exceed 1 | 40667 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Inthrm N1 | NONE | EPM | None
V1 Interharmonics Num Intervals Invalid | 40669 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Inthrm N invld | NONE | EPM | None
V2 Interharmonics Num Intervals Valid | 40671 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Inthrm N | NONE | EPM | None
V2 Interharmonics Num Intervals Exceed 1 | 40672 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Inthrm N1 | NONE | EPM | None
V2 Interharmonics Num Intervals Invalid | 40674 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Inthrm N invld | NONE | EPM | None
V3 Interharmonics Num Intervals Valid | 40676 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Inthrm N | NONE | EPM | None
V3 Interharmonics Num Intervals Exceed 1 | 40677 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Inthrm N1 | NONE | EPM | None
V3 Interharmonics Num Intervals Invalid | 40679 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Inthrm N invld | NONE | EPM | None
V1 Mains Signalling Num Intervals Valid | 40681 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-MSignal N | NONE | EPM | None
V1 Mains Signalling Num Intervals Exceed 1 | 40682 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-MSignal N1 | NONE | EPM | None
V1 Mains Signalling Num Intervals Invalid | 40683 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-MSignal N invld | NONE | EPM | None
V2 Mains Signalling Num Intervals Valid | 40685 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-MSignal N | NONE | EPM | None
V2 Mains Signalling Num Intervals Exceed 1 | 40686 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-MSignal N1 | NONE | EPM | None
V2 Mains Signalling Num Intervals Invalid | 40687 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-MSignal N invld | NONE | EPM | None
V3 Mains Signalling Num Intervals Valid | 40689 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-MSignal N | NONE | EPM | None
V3 Mains Signalling Num Intervals Exceed 1 | 40690 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-MSignal N1 | NONE | EPM | None
V3 Mains Signalling Num Intervals Invalid | 40691 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-MSignal N invld | NONE | EPM | None
Freq Num Intervals Valid | 40693 | 2 | INT32U | --- | R/O | numeric | --- | PO Freq N | NONE | EPM | None
Freq Num Intervals Exceed 1 | 40695 | 2 | INT32U | --- | R/O | numeric | --- | PO Freq N1 | NONE | EPM | None
Freq Num Intervals Exceed 2 | 40697 | 2 | INT32U | --- | R/O | numeric | --- | PO Freq N2 | NONE | EPM | None
Freq Num Intervals Invalid | 40699 | 2 | INT32U | --- | R/O | numeric | --- | PO Freq N invld | NONE | EPM | None
Freq Num Intervals Exceed 1 / Valid | 40701 | 2 | FLOAT32 | % | R/O | numeric | --- | PO Freq N1/N | PERCENT | EPM | None
Freq Num Intervals Exceed 2 / Valid | 40703 | 2 | FLOAT32 | % | R/O | numeric | --- | PO Freq N2/N | PERCENT | EPM | None
V1 Num Intervals Exceed 1 / Valid | 40705 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V1-Mag N1/N | PERCENT | EPM | None
V1 Num Intervals Exceed 2 / Valid | 40707 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V1-Mag N2/N | PERCENT | EPM | None
V2 Num Intervals Exceed 1 / Valid | 40709 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V2-Mag N1/N | PERCENT | EPM | None
V2 Num Intervals Exceed 2 / Valid | 40711 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V2-Mag N2/N | PERCENT | EPM | None
V3 Num Intervals Exceed 1 / Valid | 40713 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V3-Mag N1/N | PERCENT | EPM | None
V3 Num Intervals Exceed 2 / Valid | 40715 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V3-Mag N2/N | PERCENT | EPM | None
V1 Harm Num Intervals Exceed 1 / Valid | 40717 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V1-Hrm N1/N | PERCENT | EPM | None
V1 Harm Num Intervals Exceed 2 / Valid | 40719 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V1-Hrm N2/N | PERCENT | EPM | None
V2 Harm Num Intervals Exceed 1 / Valid | 40721 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V2-Hrm N1/N | PERCENT | EPM | None
V2 Harm Num Intervals Exceed 2 / Valid | 40723 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V2-Hrm N2/N | PERCENT | EPM | None
V3 Harm Num Intervals Exceed 1 / Valid | 40725 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V3-Hrm N1/N | PERCENT | EPM | None
V3 Harm Num Intervals Exceed 2 / Valid | 40727 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V3-Hrm N2/N | PERCENT | EPM | None
Voltage Unbal Num Intervals Exceeded 1 / Valid | 40729 | 2 | FLOAT32 | % | R/O | numeric | --- | PO Vunbal N1/N | PERCENT | EPM | None
V1-Flck N1/N | 40731 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V1-Flck N1/N | PERCENT | EPM | None
V2-Flck N1/N | 40733 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V2-Flck N1/N | PERCENT | EPM | None
V3-Flck N1/N | 40735 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V3-Flck N1/N | PERCENT | EPM | None
V-Swell S1 | 40737 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell S1 | NONE | EPM | None
V-Swell T1 | 40738 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell T1 | NONE | EPM | None
V-Swell S2 | 40739 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell S2 | NONE | EPM | None
V-Swell T2 | 40740 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell T2 | NONE | EPM | None
V-Swell S3 | 40741 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell S3 | NONE | EPM | None
V-Swell T3 | 40742 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell T3 | NONE | EPM | None
V-Swell S4 | 40743 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell S4 | NONE | EPM | None
V-Swell T4 | 40744 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Swell T4 | NONE | EPM | None
V-Intrpt N1 | 40745 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Intrpt N1 | NONE | EPM | None
V-Intrpt N2 | 40746 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Intrpt N2 | NONE | EPM | None
V-Intrpt N3 | 40747 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Intrpt N3 | NONE | EPM | None
V-Intrpt tot | 40748 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Intrpt tot | NONE | EPM | None
V1 Mains Signalling Num Intervals Exceed 1 / Valid | 40749 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V1-MSignal N1/N | PERCENT | EPM | None
V2 Mains Signalling Num Intervals Exceed 1 / Valid | 40751 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V2-MSignal N1/N | PERCENT | EPM | None
V3 Mains Signalling Num Intervals Exceed 1 / Valid | 40753 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V3-MSignal N1/N | PERCENT | EPM | None
V1 Interharmonics Num Intervals Exceed 1 / Valid | 40755 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V1-Inthrm N1/N | PERCENT | EPM | None
V2 Interharmonics Num Intervals Exceed 1 / Valid | 40757 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V2-Inthrm N1/N | PERCENT | EPM | None
V3 Interharmonics Num Intervals Exceed 1 / Valid | 40759 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V3-Inthrm N1/N | PERCENT | EPM | None
RVC Count | 40761 | 1 | INT16U | --- | R/O | numeric | --- | PO RVC Count | NONE | EPM | None
V-Dip A1 | 40762 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip A1 | NONE | EPM | None
V-Dip B1 | 40763 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip B1 | NONE | EPM | None
V-Dip C1 | 40764 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip C1 | NONE | EPM | None
V-Dip D1 | 40765 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip D1 | NONE | EPM | None
V-Dip A2 | 40766 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip A2 | NONE | EPM | None
V-Dip B2 | 40767 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip B2 | NONE | EPM | None
V-Dip C2 | 40768 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip C2 | NONE | EPM | None
V-Dip D2 | 40769 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip D2 | NONE | EPM | None
V-Dip A3 | 40770 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip A3 | NONE | EPM | None
V-Dip B3 | 40771 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip B3 | NONE | EPM | None
V-Dip C3 | 40772 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip C3 | NONE | EPM | None
V-Dip D3 | 40773 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip D3 | NONE | EPM | None
V-Dip A4 | 40774 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip A4 | NONE | EPM | None
V-Dip B4 | 40775 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip B4 | NONE | EPM | None
V-Dip C4 | 40776 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip C4 | NONE | EPM | None
V-Dip D4 | 40777 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip D4 | NONE | EPM | None
V-Dip A5 | 40778 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip A5 | NONE | EPM | None
V-Dip B5 | 40779 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip B5 | NONE | EPM | None
V-Dip C5 | 40780 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip C5 | NONE | EPM | None
V-Dip D5 | 40781 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip D5 | NONE | EPM | None
V-Dip X1 | 40782 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip X1 | NONE | EPM | None
V-Dip X2 | 40783 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip X2 | NONE | EPM | None
V-Dip X3 | 40784 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip X3 | NONE | EPM | None
V-Dip X4 | 40785 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip X4 | NONE | EPM | None
V-Dip X5 | 40786 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Dip X5 | NONE | EPM | None
V1-Hrm Z | 43728 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm Z | NONE | IEM | None
V1-Hrm Z1 | 43729 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm Z1 | NONE | IEM | None
V1-Hrm Z2 | 43730 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm Z2 | NONE | IEM | None
V2-Hrm Z | 43731 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm Z | NONE | IEM | None
V2-Hrm Z1 | 43732 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm Z1 | NONE | IEM | None
V2-Hrm Z2 | 43733 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm Z2 | NONE | IEM | None
V3-Hrm Z | 43734 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm Z | NONE | IEM | None
V3-Hrm Z1 | 43735 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm Z1 | NONE | IEM | None
V3-Hrm Z2 | 43736 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm Z2 | NONE | IEM | None
V-Hrm Z1 | 43737 | 1 | INT16U | --- | R/O | numeric | --- | V-Hrm Z1 | NONE | IEM | None
V-Hrm Z2 | 43738 | 1 | INT16U | --- | R/O | numeric | --- | V-Hrm Z2 | NONE | IEM | None
V-Hrm Z Comp | 43739 | 2 | FLOAT32 | % | R/O | numeric | --- | V-Hrm Z Comp | PERCENT | IEM | None
V-THD Z Comp | 43741 | 2 | FLOAT32 | % | R/O | numeric | --- | V-THD Z Comp | PERCENT | IEM | None
I1-Hrm Z | 43743 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm Z | NONE | IEM | None
I1-Hrm Z1 | 43744 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm Z1 | NONE | IEM | None
I1-Hrm Z2 | 43745 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm Z2 | NONE | IEM | None
I2-Hrm Z | 43746 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm Z | NONE | IEM | None
I2-Hrm Z1 | 43747 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm Z1 | NONE | IEM | None
I2-Hrm Z2 | 43748 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm Z2 | NONE | IEM | None
I3-Hrm Z | 43749 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm Z | NONE | IEM | None
I3-Hrm Z1 | 43750 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm Z1 | NONE | IEM | None
I3-Hrm Z2 | 43751 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm Z2 | NONE | IEM | None
I-Hrm Z1 | 43752 | 1 | INT16U | --- | R/O | numeric | --- | I-Hrm Z1 | NONE | IEM | None
I-Hrm Z2 | 43753 | 1 | INT16U | --- | R/O | numeric | --- | I-Hrm Z2 | NONE | IEM | None
I-Hrm Z Comp | 43754 | 2 | FLOAT32 | % | R/O | numeric | --- | I-Hrm Z Comp | PERCENT | IEM | None
I-TDD Z Comp | 43756 | 2 | FLOAT32 | % | R/O | numeric | --- | I-TDD Z Comp | PERCENT | IEM | None
Valid Z | 43758 | 1 | INT16U | --- | R/O | numeric | --- | Valid Z | NONE | IEM | None
Invalid Z | 43759 | 1 | INT16U | --- | R/O | numeric | --- | Invalid Z | NONE | IEM | None
PO V1-Hrm Z | 43760 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm Z | NONE | IEM | None
PO V1-Hrm Z1 | 43761 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm Z1 | NONE | IEM | None
PO V1-Hrm Z2 | 43762 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm Z2 | NONE | IEM | None
PO V2-Hrm Z | 43763 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm Z | NONE | IEM | None
PO V2-Hrm Z1 | 43764 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm Z1 | NONE | IEM | None
PO V2-Hrm Z2 | 43765 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm Z2 | NONE | IEM | None
PO V3-Hrm Z | 43766 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm Z | NONE | IEM | None
PO V3-Hrm Z1 | 43767 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm Z1 | NONE | IEM | None
PO V3-Hrm Z2 | 43768 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm Z2 | NONE | IEM | None
PO V-Hrm Z1 | 43769 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Hrm Z1 | NONE | IEM | None
PO V-Hrm Z2 | 43770 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Hrm Z2 | NONE | IEM | None
PO V-Hrm Z Cmp | 43771 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V-Hrm Z Cmp | PERCENT | IEM | None
PO V-THD Z Cmp | 43773 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V-THD Z Cmp | PERCENT | IEM | None
PO I1-Hrm Z | 43775 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm Z | NONE | IEM | None
PO I1-Hrm Z1 | 43776 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm Z1 | NONE | IEM | None
PO I1-Hrm Z2 | 43777 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm Z2 | NONE | IEM | None
PO I2-Hrm Z | 43778 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm Z | NONE | IEM | None
PO I2-Hrm Z1 | 43779 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm Z1 | NONE | IEM | None
PO I2-Hrm Z2 | 43780 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm Z2 | NONE | IEM | None
PO I3-Hrm Z | 43781 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm Z | NONE | IEM | None
PO I3-Hrm Z1 | 43782 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm Z1 | NONE | IEM | None
PO I3-Hrm Z2 | 43783 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm Z2 | NONE | IEM | None
PO I-Hrm Z1 | 43784 | 1 | INT16U | --- | R/O | numeric | --- | PO I-Hrm Z1 | NONE | IEM | None
PO I-Hrm Z2 | 43785 | 1 | INT16U | --- | R/O | numeric | --- | PO I-Hrm Z2 | NONE | IEM | None
PO I-Hrm Z Cmp | 43786 | 2 | FLOAT32 | % | R/O | numeric | --- | PO I-Hrm Z Cmp | PERCENT | IEM | None
PO I-TDD Z Cmp | 43788 | 2 | FLOAT32 | % | R/O | numeric | --- | PO I-TDD Z Cmp | PERCENT | IEM | None
PO Valid Z | 43790 | 1 | INT16U | --- | R/O | numeric | --- | PO Valid Z | NONE | IEM | None
PO Invalid Z | 43791 | 1 | INT16U | --- | R/O | numeric | --- | PO Invalid Z | NONE | IEM | None
V1-Hrm X | 43792 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm X | NONE | IEM | None
V1-Hrm X1 | 43793 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm X1 | NONE | IEM | None
V1-Hrm X2 | 43794 | 1 | INT16U | --- | R/O | numeric | --- | V1-Hrm X2 | NONE | IEM | None
V2-Hrm X | 43795 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm X | NONE | IEM | None
V2-Hrm X1 | 43796 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm X1 | NONE | IEM | None
V2-Hrm X2 | 43797 | 1 | INT16U | --- | R/O | numeric | --- | V2-Hrm X2 | NONE | IEM | None
V3-Hrm X | 43798 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm X | NONE | IEM | None
V3-Hrm X1 | 43799 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm X1 | NONE | IEM | None
V3-Hrm X2 | 43800 | 1 | INT16U | --- | R/O | numeric | --- | V3-Hrm X2 | NONE | IEM | None
V-Hrm X1 | 43801 | 1 | INT16U | --- | R/O | numeric | --- | V-Hrm X1 | NONE | IEM | None
V-Hrm X2 | 43802 | 1 | INT16U | --- | R/O | numeric | --- | V-Hrm X2 | NONE | IEM | None
V-Hrm X Comp | 43803 | 2 | FLOAT32 | % | R/O | numeric | --- | V-Hrm X Comp | PERCENT | IEM | None
V-THD X Comp | 43805 | 2 | FLOAT32 | % | R/O | numeric | --- | V-THD X Comp | PERCENT | IEM | None
I1-Hrm X | 43807 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm X | NONE | IEM | None
I1-Hrm X1 | 43808 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm X1 | NONE | IEM | None
I1-Hrm X2 | 43809 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm X2 | NONE | IEM | None
I2-Hrm X | 43810 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm X | NONE | IEM | None
I2-Hrm X1 | 43811 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm X1 | NONE | IEM | None
I2-Hrm X2 | 43812 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm X2 | NONE | IEM | None
I3-Hrm X | 43813 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm X | NONE | IEM | None
I3-Hrm X1 | 43814 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm X1 | NONE | IEM | None
I3-Hrm X2 | 43815 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm X2 | NONE | IEM | None
I-Hrm X1 | 43816 | 1 | INT16U | --- | R/O | numeric | --- | I-Hrm X1 | NONE | IEM | None
I-Hrm X2 | 43817 | 1 | INT16U | --- | R/O | numeric | --- | I-Hrm X2 | NONE | IEM | None
I-Hrm X Comp | 43818 | 2 | FLOAT32 | % | R/O | numeric | --- | I-Hrm X Comp | PERCENT | IEM | None
I-TDD X Comp | 43820 | 2 | FLOAT32 | % | R/O | numeric | --- | I-TDD X Comp | PERCENT | IEM | None
I1-Hrm Y | 43822 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm Y | NONE | IEM | None
I1-Hrm Y1 | 43823 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm Y1 | NONE | IEM | None
I1-Hrm Y2 | 43824 | 1 | INT16U | --- | R/O | numeric | --- | I1-Hrm Y2 | NONE | IEM | None
I2-Hrm Y | 43825 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm Y | NONE | IEM | None
I2-Hrm Y1 | 43826 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm Y1 | NONE | IEM | None
I2-Hrm Y2 | 43827 | 1 | INT16U | --- | R/O | numeric | --- | I2-Hrm Y2 | NONE | IEM | None
I3-Hrm Y | 43828 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm Y | NONE | IEM | None
I3-Hrm Y1 | 43829 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm Y1 | NONE | IEM | None
I3-Hrm Y2 | 43830 | 1 | INT16U | --- | R/O | numeric | --- | I3-Hrm Y2 | NONE | IEM | None
I-Hrm Y1 | 43831 | 1 | INT16U | --- | R/O | numeric | --- | I-Hrm Y1 | NONE | IEM | None
I-Hrm Y2 | 43832 | 1 | INT16U | --- | R/O | numeric | --- | I-Hrm Y2 | NONE | IEM | None
I-Hrm Y Comp | 43833 | 2 | FLOAT32 | % | R/O | numeric | --- | I-Hrm Y Comp | PERCENT | IEM | None
I-TDD Y Comp | 43835 | 2 | FLOAT32 | % | R/O | numeric | --- | I-TDD Y Comp | PERCENT | IEM | None
Valid XY | 43837 | 1 | INT16U | --- | R/O | numeric | --- | Valid XY | NONE | IEM | None
Invalid XY | 43838 | 1 | INT16U | --- | R/O | numeric | --- | Invalid XY | NONE | IEM | None
PO V1-Hrm X | 43839 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm X | NONE | IEM | None
PO V1-Hrm X1 | 43840 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm X1 | NONE | IEM | None
PO V1-Hrm X2 | 43841 | 1 | INT16U | --- | R/O | numeric | --- | PO V1-Hrm X2 | NONE | IEM | None
PO V2-Hrm X | 43842 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm X | NONE | IEM | None
PO V2-Hrm X1 | 43843 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm X1 | NONE | IEM | None
PO V2-Hrm X2 | 43844 | 1 | INT16U | --- | R/O | numeric | --- | PO V2-Hrm X2 | NONE | IEM | None
PO V3-Hrm X | 43845 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm X | NONE | IEM | None
PO V3-Hrm X1 | 43846 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm X1 | NONE | IEM | None
PO V3-Hrm X2 | 43847 | 1 | INT16U | --- | R/O | numeric | --- | PO V3-Hrm X2 | NONE | IEM | None
PO V-Hrm X1 | 43848 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Hrm X1 | NONE | IEM | None
PO V-Hrm X2 | 43849 | 1 | INT16U | --- | R/O | numeric | --- | PO V-Hrm X2 | NONE | IEM | None
PO V-Hrm X Cmp | 43850 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V-Hrm X Cmp | PERCENT | IEM | None
PO V-THD X Cmp | 43852 | 2 | FLOAT32 | % | R/O | numeric | --- | PO V-THD X Cmp | PERCENT | IEM | None
PO I1-Hrm X | 43854 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm X | NONE | IEM | None
PO I1-Hrm X1 | 43855 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm X1 | NONE | IEM | None
PO I1-Hrm X2 | 43856 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm X2 | NONE | IEM | None
PO I2-Hrm X | 43857 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm X | NONE | IEM | None
PO I2-Hrm X1 | 43858 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm X1 | NONE | IEM | None
PO I2-Hrm X2 | 43859 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm X2 | NONE | IEM | None
PO I3-Hrm X | 43860 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm X | NONE | IEM | None
PO I3-Hrm X1 | 43861 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm X1 | NONE | IEM | None
PO I3-Hrm X2 | 43862 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm X2 | NONE | IEM | None
PO I-Hrm X1 | 43863 | 1 | INT16U | --- | R/O | numeric | --- | PO I-Hrm X1 | NONE | IEM | None
PO I-Hrm X2 | 43864 | 1 | INT16U | --- | R/O | numeric | --- | PO I-Hrm X2 | NONE | IEM | None
PO I-Hrm X Cmp | 43865 | 2 | FLOAT32 | % | R/O | numeric | --- | PO I-Hrm X Cmp | PERCENT | IEM | None
PO I-TDD X Cmp | 43867 | 2 | FLOAT32 | % | R/O | numeric | --- | PO I-TDD X Cmp | PERCENT | IEM | None
PO I1-Hrm Y | 43869 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm Y | NONE | IEM | None
PO I1-Hrm Y1 | 43870 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm Y1 | NONE | IEM | None
PO I1-Hrm Y2 | 43871 | 1 | INT16U | --- | R/O | numeric | --- | PO I1-Hrm Y2 | NONE | IEM | None
PO I2-Hrm Y | 43872 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm Y | NONE | IEM | None
PO I2-Hrm Y1 | 43873 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm Y1 | NONE | IEM | None
PO I2-Hrm Y2 | 43874 | 1 | INT16U | --- | R/O | numeric | --- | PO I2-Hrm Y2 | NONE | IEM | None
PO I3-Hrm Y | 43875 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm Y | NONE | IEM | None
PO I3-Hrm Y1 | 43876 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm Y1 | NONE | IEM | None
PO I3-Hrm Y2 | 43877 | 1 | INT16U | --- | R/O | numeric | --- | PO I3-Hrm Y2 | NONE | IEM | None
PO I-Hrm Y1 | 43878 | 1 | INT16U | --- | R/O | numeric | --- | PO I-Hrm Y1 | NONE | IEM | None
PO I-Hrm Y2 | 43879 | 1 | INT16U | --- | R/O | numeric | --- | PO I-Hrm Y2 | NONE | IEM | None
PO I-Hrm Y Cmp | 43880 | 2 | FLOAT32 | % | R/O | numeric | --- | PO I-Hrm Y Cmp | PERCENT | IEM | None
PO I-TDD Y Cmp | 43882 | 2 | FLOAT32 | % | R/O | numeric | --- | PO I-TDD Y Cmp | PERCENT | IEM | None
PO Valid XY | 43884 | 1 | INT16U | --- | R/O | numeric | --- | PO Valid XY | NONE | IEM | None
PO Invalid XY | 43885 | 1 | INT16U | --- | R/O | numeric | --- | PO Invalid XY | NONE | IEM | None
519 I_L | 43886 | 2 | FLOAT32 | A | R/O | numeric | --- | 519 I_L | NONE | IEM | None
519 Volt enum | 43888 | 1 | INT16U | --- | R/O | numeric | --- | 519 Volt enum | NONE | IEM | None
519 I_SC | 43889 | 2 | FLOAT32 | A | R/O | numeric | --- | 519 I_SC | NONE | IEM | None
519 Mx Dmd IL | 43891 | 2 | FLOAT32 | A | R/O | numeric | --- | 519 Mx Dmd IL | NONE | IEM | None
External Pulse 1 Trigger | 52001 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 2 Trigger | 52002 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 3 Trigger | 52003 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 4 Trigger | 52004 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 5 Trigger | 52005 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 6 Trigger | 52006 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 7 Trigger | 52007 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 8 Trigger | 52008 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 9 Trigger | 52009 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 10 Trigger | 52010 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 11 Trigger | 52011 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 12 Trigger | 52012 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 13 Trigger | 52013 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 14 Trigger | 52014 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 15 Trigger | 52015 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 16 Trigger | 52016 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 17 Trigger | 52017 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 18 Trigger | 52018 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 19 Trigger | 52019 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 20 Trigger | 52020 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 21 Trigger | 52021 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 22 Trigger | 52022 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 23 Trigger | 52023 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 24 Trigger | 52024 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 25 Trigger | 52025 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 26 Trigger | 52026 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 27 Trigger | 52027 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 28 Trigger | 52028 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 29 Trigger | 52029 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 30 Trigger | 52030 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 31 Trigger | 52031 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 32 Trigger | 52032 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 33 Trigger | 52033 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 34 Trigger | 52034 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 35 Trigger | 52035 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 36 Trigger | 52036 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 37 Trigger | 52037 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 38 Trigger | 52038 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 39 Trigger | 52039 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 40 Trigger | 52040 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 41 Trigger | 52041 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 42 Trigger | 52042 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 43 Trigger | 52043 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 44 Trigger | 52044 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 45 Trigger | 52045 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 46 Trigger | 52046 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 47 Trigger | 52047 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 48 Trigger | 52048 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 49 Trigger | 52049 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 50 Trigger | 52050 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 51 Trigger | 52051 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 52 Trigger | 52052 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 53 Trigger | 52053 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 54 Trigger | 52054 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 55 Trigger | 52055 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 56 Trigger | 52056 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 57 Trigger | 52057 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 58 Trigger | 52058 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 59 Trigger | 52059 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 60 Trigger | 52060 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 61 Trigger | 52061 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 62 Trigger | 52062 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 63 Trigger | 52063 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 64 Trigger | 52064 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 65 Trigger | 52065 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 66 Trigger | 52066 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 67 Trigger | 52067 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 68 Trigger | 52068 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 69 Trigger | 52069 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 70 Trigger | 52070 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 71 Trigger | 52071 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 72 Trigger | 52072 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 73 Trigger | 52073 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 74 Trigger | 52074 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 75 Trigger | 52075 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 76 Trigger | 52076 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 77 Trigger | 52077 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 78 Trigger | 52078 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 79 Trigger | 52079 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 80 Trigger | 52080 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 81 Trigger | 52081 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 82 Trigger | 52082 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 83 Trigger | 52083 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 84 Trigger | 52084 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 85 Trigger | 52085 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 86 Trigger | 52086 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 87 Trigger | 52087 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 88 Trigger | 52088 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 89 Trigger | 52089 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 90 Trigger | 52090 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 91 Trigger | 52091 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 92 Trigger | 52092 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 93 Trigger | 52093 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 94 Trigger | 52094 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 95 Trigger | 52095 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 96 Trigger | 52096 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 97 Trigger | 52097 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 98 Trigger | 52098 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 99 Trigger | 52099 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 100 Trigger | 52100 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 101 Trigger | 52101 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 102 Trigger | 52102 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 103 Trigger | 52103 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 104 Trigger | 52104 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 105 Trigger | 52105 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 106 Trigger | 52106 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 107 Trigger | 52107 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 108 Trigger | 52108 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 109 Trigger | 52109 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 110 Trigger | 52110 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 111 Trigger | 52111 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 112 Trigger | 52112 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 113 Trigger | 52113 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 114 Trigger | 52114 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 115 Trigger | 52115 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 116 Trigger | 52116 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 117 Trigger | 52117 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 118 Trigger | 52118 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 119 Trigger | 52119 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 120 Trigger | 52120 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 121 Trigger | 52121 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 122 Trigger | 52122 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 123 Trigger | 52123 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 124 Trigger | 52124 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 125 Trigger | 52125 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 126 Trigger | 52126 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 127 Trigger | 52127 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Pulse 128 Trigger | 52128 | 1 | INT16U | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Boolean 1 Switch | 52201 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 2 Switch | 52202 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 3 Switch | 52203 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 4 Switch | 52204 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 5 Switch | 52205 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 6 Switch | 52206 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 7 Switch | 52207 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 8 Switch | 52208 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 9 Switch | 52209 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 10 Switch | 52210 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 11 Switch | 52211 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 12 Switch | 52212 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 13 Switch | 52213 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 14 Switch | 52214 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 15 Switch | 52215 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 16 Switch | 52216 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 17 Switch | 52217 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 18 Switch | 52218 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 19 Switch | 52219 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 20 Switch | 52220 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 21 Switch | 52221 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 22 Switch | 52222 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 23 Switch | 52223 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 24 Switch | 52224 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 25 Switch | 52225 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 26 Switch | 52226 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 27 Switch | 52227 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 28 Switch | 52228 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 29 Switch | 52229 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 30 Switch | 52230 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 31 Switch | 52231 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 32 Switch | 52232 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 33 Switch | 52233 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 34 Switch | 52234 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 35 Switch | 52235 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 36 Switch | 52236 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 37 Switch | 52237 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 38 Switch | 52238 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 39 Switch | 52239 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 40 Switch | 52240 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 41 Switch | 52241 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 42 Switch | 52242 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 43 Switch | 52243 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 44 Switch | 52244 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 45 Switch | 52245 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 46 Switch | 52246 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 47 Switch | 52247 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 48 Switch | 52248 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 49 Switch | 52249 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 50 Switch | 52250 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 51 Switch | 52251 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 52 Switch | 52252 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 53 Switch | 52253 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 54 Switch | 52254 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 55 Switch | 52255 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 56 Switch | 52256 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 57 Switch | 52257 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 58 Switch | 52258 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 59 Switch | 52259 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 60 Switch | 52260 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 61 Switch | 52261 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 62 Switch | 52262 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 63 Switch | 52263 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 64 Switch | 52264 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 65 Switch | 52265 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 66 Switch | 52266 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 67 Switch | 52267 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 68 Switch | 52268 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 69 Switch | 52269 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 70 Switch | 52270 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 71 Switch | 52271 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 72 Switch | 52272 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 73 Switch | 52273 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 74 Switch | 52274 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 75 Switch | 52275 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 76 Switch | 52276 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 77 Switch | 52277 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 78 Switch | 52278 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 79 Switch | 52279 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 80 Switch | 52280 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 81 Switch | 52281 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 82 Switch | 52282 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 83 Switch | 52283 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 84 Switch | 52284 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Boolean 85 Switch | 52285 | 1 | INT16U | --- | R/W | boolean | N/A | N/A | N/A | N/A | N/A
External Numeric 1 Value | 52301 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 2 Value | 52303 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 3 Value | 52305 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 4 Value | 52307 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 5 Value | 52309 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 6 Value | 52311 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 7 Value | 52313 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 8 Value | 52315 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 9 Value | 52317 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 10 Value | 52319 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 11 Value | 52321 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 12 Value | 52323 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 13 Value | 52325 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 14 Value | 52327 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 15 Value | 52329 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 16 Value | 52331 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 17 Value | 52333 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 18 Value | 52335 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 19 Value | 52337 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 20 Value | 52339 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 21 Value | 52341 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 22 Value | 52343 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 23 Value | 52345 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 24 Value | 52347 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 25 Value | 52349 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 26 Value | 52351 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 27 Value | 52353 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 28 Value | 52355 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 29 Value | 52357 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 30 Value | 52359 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 31 Value | 52361 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 32 Value | 52363 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 33 Value | 52365 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 34 Value | 52367 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 35 Value | 52369 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 36 Value | 52371 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 37 Value | 52373 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 38 Value | 52375 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 39 Value | 52377 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
External Numeric 40 Value | 52379 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM1 Volts Mode | 54001 | 1 | INT16U | --- | R/W | enum | 0 - 4W-WYE 1 - DELTA 2 - SINGLE 3 - DEMO 4 - 3W-WYE | N/A | N/A | N/A | N/A
PM1 I1Polarity | 54002 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
PM1 I2Polarity | 54003 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
PM1 I3Polarity | 54004 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
COM1 Baud Rate | 54392 | 1 | INT16U | --- | R/W | enum | 0 - 2400 1 - 4800 2 - 9600 3 - 19200 4 - 38400 5 - 57600 6 - 115200 | N/A | N/A | N/A | N/A
FAC1 Nominal Frequency | 54396 | 1 | INT16U | Hz | R/W | enum | 0 - 60Hz; 1 - 50Hz | N/A | N/A | N/A | N/A | Not supported on this device.
PM1 I4Polarity | 54586 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
PM1 V1Polarity | 54587 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
PM1 V2Polarity | 54588 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
PM1 V3Polarity | 54589 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
COM1 Protocol | 54592 | 1 | INT16U | --- | R/W | enum | 0 - ION 1 - Modbus RTU 3 - Factory 4 - DNP V3.00 6 - GPS: TrueTime/Datum 7 - GPS: Arbiter 8 - GPS: Arbiter-Vorne 9 - Modbus Master 13 - DLMS 99 - None (Disabled) 100 - EtherGate 101 - Modbus Gateway | N/A | N/A | N/A | N/A | Not all protocols in list may be supported by this COM port or product
PM V4 Polarity | 55043 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
PM I5 Polarity | 55044 | 1 | INT16U | --- | R/W | enum | 0 - Normal; 1 - Inverted | N/A | N/A | N/A | N/A
CM4 Baud Rate | 55460 | 1 | INT16U | --- | R/W | enum | 0 - 2400 1 - 4800 2 - 9600 3 - 19200 4 - 38400 5 - 57600 6 - 115200 | N/A | N/A | N/A | N/A
CM4 Protocol | 55461 | 1 | INT16U | --- | R/W | enum | 0 - ION 1 - Modbus RTU 3 - Factory 4 - DNP V3.00 6 - GPS: TrueTime/Datum 7 - GPS: Arbiter 8 - GPS: Arbiter-Vorne 9 - Modbus Master 13 - DLMS 99 - None (Disabled) 100 - EtherGate 101 - Modbus Gateway | N/A | N/A | N/A | N/A | Not all protocols in list may be supported by this COM port or product
PM1 PT Primary | 56001 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM1 PT Secondary | 56003 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM1 CT Primary | 56005 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM1 CT Secondary | 56007 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM1 I4 CT Primary | 56009 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM1 I4 CT Secondary | 56011 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
COM1 RTS Delay | 56977 | 2 | INT32 | s | R/W | numeric | N/A | N/A | N/A | N/A | N/A
COM1 Unit ID | 56979 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM V4 PT Primary | 58903 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM V4 PT Secondary | 58905 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM I5 CT Primary | 58907 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
PM I5 CT Secondary | 58909 | 2 | INT32 | --- | R/W | numeric | N/A | N/A | N/A | N/A | N/A
A D1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A D1 State | NONE | IO | None
A D2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A D2 State | NONE | IO | None
A S1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A S1 State | NONE | IO | None
A S2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A S2 State | NONE | IO | None
A S3 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A S3 State | NONE | IO | None
A S4 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A S4 State | NONE | IO | None
A S5 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A S5 State | NONE | IO | None
A S6 State | N/A | N/A | N/A | --- | N/A | boolean | --- | A S6 State | NONE | IO | None
Acquired IPv4 Address | N/A | N/A | N/A | --- | N/A | string | --- | Acquired IPv4 Address | NONE | Config | None
Acquired IPv4 Gateway | N/A | N/A | N/A | --- | N/A | string | --- | Acquired IPv4 Gateway | NONE | Config | None
Acquired IPv4 Subnet Mask | N/A | N/A | N/A | --- | N/A | string | --- | Acquired IPv4 Subnet Mask | NONE | Config | None
Acquired IPv6 Gateway | N/A | N/A | N/A | --- | N/A | string | --- | Acquired IPv6 Gateway | NONE | Config | None
Acquired IPv6 Global Address | N/A | N/A | N/A | --- | N/A | string | --- | Acquired IPv6 Global Addr | NONE | Config | None
ARP Cache Timeout | N/A | N/A | N/A | --- | N/A | numeric | --- | ARP Cache Timeout | NONE | Config | None
B D1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B D1 State | NONE | IO | None
B D2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B D2 State | NONE | IO | None
B S1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B S1 State | NONE | IO | None
B S2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B S2 State | NONE | IO | None
B S3 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B S3 State | NONE | IO | None
B S4 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B S4 State | NONE | IO | None
B S5 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B S5 State | NONE | IO | None
B S6 State | N/A | N/A | N/A | --- | N/A | boolean | --- | B S6 State | NONE | IO | None
Backlight Timeout | N/A | N/A | N/A | --- | N/A | numeric | --- | Backlight Timeout | NONE | Config | None
Bootloader Version | N/A | N/A | N/A | --- | N/A | string | --- | Bootloader Version | NONE | Config | None
C D1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C D1 State | NONE | IO | None
C D2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C D2 State | NONE | IO | None
C S1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C S1 State | NONE | IO | None
C S2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C S2 State | NONE | IO | None
C S3 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C S3 State | NONE | IO | None
C S4 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C S4 State | NONE | IO | None
C S5 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C S5 State | NONE | IO | None
C S6 State | N/A | N/A | N/A | --- | N/A | boolean | --- | C S6 State | NONE | IO | None
Clock Source | N/A | N/A | N/A | --- | N/A | enum | 0 - Internal 1 - Line Freq 2 - COMM | Clock Source | NONE | Config | None
COM1 Baud Rate | N/A | N/A | N/A | --- | N/A | enum | 0 - 2400 1 - 4800 2 - 9600 3 - 19200 4 - 38400 5 - 57600 6 - 115200 | COM1 Baud Rate | NONE | Config | None
COM1 Protocol | N/A | N/A | N/A | --- | N/A | enum | 0 - ION 1 - Modbus RTU 2 - Modbus Master 3 - DNP V3.00 4 - EtherGate 5 - GPS: TrueTime/Datum 6 - GPS: Arbiter 7 - GPS: Arbiter-Vorne 8 - Factory | COM1 Protocol | NONE | Config | None
COM1 RS485 Bias | N/A | N/A | N/A | --- | N/A | enum | 0 - ON; 1 - OFF | COM1 RS485 Bias | NONE | Config | None
COM1 RTS Delay | N/A | N/A | N/A | --- | N/A | numeric | --- | COM1 RTS Delay | S_3D | Config | None
COM1 Rx Timeout | N/A | N/A | N/A | --- | N/A | numeric | --- | COM1 Rx Timeout | S_3D | Config | None
COM1 Serial Port | N/A | N/A | N/A | --- | N/A | enum | 0 - 8N1 1 - 8N2 2 - 8E1 3 - 8E2 4 - 8O1 5 - 8O2 | COM1 Serial Port | NONE | Config | None
COM1 Unit ID | N/A | N/A | N/A | --- | N/A | numeric | --- | COM1 Unit ID | NONE | Config | None
COM4 Baud Rate | N/A | N/A | N/A | --- | N/A | enum | 0 - 2400 1 - 4800 2 - 9600 3 - 19200 4 - 38400 5 - 57600 6 - 115200 | COM4 Baud Rate | NONE | Config | None
COM4 Protocol | N/A | N/A | N/A | --- | N/A | enum | 0 - ION 1 - Modbus RTU 2 - Modbus Master 3 - DNP V3.00 4 - EtherGate 5 - GPS: TrueTime/Datum 6 - GPS: Arbiter 7 - GPS: Arbiter-Vorne 8 - Factory | COM4 Protocol | NONE | Config | None
COM4 RS485 Bias | N/A | N/A | N/A | --- | N/A | enum | 0 - ON; 1 - OFF | COM4 RS485 Bias | NONE | Config | None
COM4 RTS Delay | N/A | N/A | N/A | --- | N/A | numeric | --- | COM4 RTS Delay | S_3D | Config | None
COM4 Rx Timeout | N/A | N/A | N/A | --- | N/A | numeric | --- | COM4 Rx Timeout | S_3D | Config | None
COM4 Serial Port | N/A | N/A | N/A | --- | N/A | enum | 0 - 8N1 1 - 8N2 2 - 8E1 3 - 8E2 4 - 8O1 5 - 8O2 | COM4 Serial Port | NONE | Config | None
COM4 Unit ID | N/A | N/A | N/A | --- | N/A | numeric | --- | COM4 Unit ID | NONE | Config | None
Contingency Fund | N/A | N/A | N/A | --- | N/A | numeric | --- | Contingency Fund | NONE | Config | None
CPU Temp | N/A | N/A | N/A | --- | N/A | numeric | --- | CPU Temp | NONE | Config | None
CT Prim | N/A | N/A | N/A | --- | N/A | numeric | --- | CT Prim | A | Config | None
CT Sec | N/A | N/A | N/A | --- | N/A | numeric | --- | CT Sec | A | Config | None
Current Resolution | N/A | N/A | N/A | --- | N/A | enum | 0 - 1. 1 - 1.X 2 - 1.XX 3 - 1.XXX 4 - 1.XXXX | Current Resolution | NONE | Config | None
Custom Screens Scroll Delay | N/A | N/A | N/A | --- | N/A | numeric | --- | Custom Screens Scroll Delay | NONE | Config | None
D D1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D D1 State | NONE | IO | None
D D2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D D2 State | NONE | IO | None
D S1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D S1 State | NONE | IO | None
D S2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D S2 State | NONE | IO | None
D S3 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D S3 State | NONE | IO | None
D S4 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D S4 State | NONE | IO | None
D S5 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D S5 State | NONE | IO | None
D S6 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D S6 State | NONE | IO | None
D1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D1 State | NONE | IO | None
D2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D2 State | NONE | IO | None
D3 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D3 State | NONE | IO | None
D4 State | N/A | N/A | N/A | --- | N/A | boolean | --- | D4 State | NONE | IO | None
DAN1 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DAN1 Enable | NONE | Config | None
DAN2 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DAN2 Enable | NONE | Config | None
DAN3 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DAN3 Enable | NONE | Config | None
DAN4 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DAN4 Enable | NONE | Config | None
DAN5 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DAN5 Enable | NONE | Config | None
DAN6 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DAN6 Enable | NONE | Config | None
Date Format | N/A | N/A | N/A | --- | N/A | enum | 0 - MM/DD/YYYY 1 - DD/MM/YYYY 2 - YYYY/MM/DD | Date Format | NONE | Config | None
Device Type | N/A | N/A | N/A | --- | N/A | string | --- | DeviceType | NONE | Config | None
DI1 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI1 Enable | NONE | Config | None
DI10 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI10 Enable | NONE | Config | None
DI11 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI11 Enable | NONE | Config | None
DI12 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI12 Enable | NONE | Config | None
DI13 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI13 Enable | NONE | Config | None
DI14 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI14 Enable | NONE | Config | None
DI15 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI15 Enable | NONE | Config | None
DI16 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI16 Enable | NONE | Config | None
DI2 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI2 Enable | NONE | Config | None
DI3 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI3 Enable | NONE | Config | None
DI4 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI4 Enable | NONE | Config | None
DI5 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI5 Enable | NONE | Config | None
DI6 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI6 Enable | NONE | Config | None
DI7 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI7 Enable | NONE | Config | None
DI8 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI8 Enable | NONE | Config | None
DI9 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | DI9 Enable | NONE | Config | None
Digit Grouping | N/A | N/A | N/A | --- | N/A | enum | 0 - 1000.0 1 - 1,000.0 2 - 1 000,0 | Digit Grouping | NONE | Config | None
Digital Input Count Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | Digital Input Count Reset | NONE | IOM | None
Digital Input Count Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Digital Input Count Reset Count | NONE | IOM | None
Disturbance Count Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | Disturbance Count Reset | NONE | IOM | None
Disturbance Count Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Disturbance Count Reset Count | NONE | IOM | None
DLMS Port Number | N/A | N/A | N/A | --- | N/A | numeric | --- | DLMS Port Number | NONE | Config | None
Domain Name | N/A | N/A | N/A | --- | N/A | string | --- | Domain Name | NONE | Config | None
DST Offset | N/A | N/A | N/A | --- | N/A | numeric | --- | DST Offset | NONE | Config | None
EN50160 Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | EN50160 Reset | NONE | IOM | None
EN50160 Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | EN50160 Reset Count | NONE | IOM | None
Enable DLMS | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable DLMS | NONE | Config | None
Enable DNP Over TCP | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable DNP Over TCP | NONE | Config | None
Enable DPWS | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable DPWS | NONE | Config | None
Enable High Priority Alarms | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable High Priority Alarms | NONE | Config | None
Enable ION Over TCP | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable ION Over TCP | NONE | Config | None
Enable IPv6 | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable IPv6 | NONE | Config | None
Enable Low Priority Alarms | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable Low Priority Alarms | NONE | Config | None
Enable Med Priority Alarms | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable Med Priority Alarms | NONE | Config | None
Enable Modbus RTU Over TCP | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable Modbus RTU Over TCP | NONE | Config | None
Enable Modbus TCP | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable Modbus TCP | NONE | Config | None
Enable NTP Time Sync | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable NTP Time Sync | NONE | Config | None
Enable RSTP | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable RSTP | NONE | Config | None
Enable Secure ION Over TCP | N/A | N/A | N/A |  | N/A | enum | 0 - Yes; 1 - No | Enable Secure ION Over TCP | NONE | Config | None
Enable SFTP | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable SFTP | NONE | Config | None
Enable SNMP | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable SNMP | NONE | Config | None
Enable SNMP Traps | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable SNMP Traps | NONE | Config | None
Enable SSH Terminal | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable SSH Terminal | NONE | Config | None
Enable Web Server | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | Enable Web Server | NONE | Config | None
Ethernet Device | N/A | N/A | N/A | --- | N/A | string | --- | Ethernet Device | NONE | Config | None
Ethernet Rx Timeout | N/A | N/A | N/A | --- | N/A | numeric | --- | Ethernet Rx Timeout | S_3D | Config | None
F Nominal | N/A | N/A | N/A | --- | N/A | numeric | --- | F Nominal | HZ | Config | None
Feature Set | N/A | N/A | N/A | --- | N/A | string | --- | Feature Set | NONE | Config | None
Free Buffer Memory | N/A | N/A | N/A | --- | N/A | numeric | --- | Free Buffer Memory | NONE | Config | None
Free Internal Memory | N/A | N/A | N/A | --- | N/A | numeric | --- | Free Internal Memory | NONE | Config | None
Harmonics Min/Max Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | Harmonics Min/Max Reset | NONE | IOM | None
Harmonics Min/Max Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Harmonics Min/Max Reset Count | NONE | IOM | None
HST1 Dur 1/2 Bin Threshold | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Dur 1/2 Bin Threshold | NONE | Config | None
HST1 Dur 2/3 Bin Threshold | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Dur 2/3 Bin Threshold | NONE | Config | None
HST1 Duration Threshold | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Duration Threshold | NONE | Config | None
HST1 Enable | N/A | N/A | N/A |  | N/A | enum | 0 - Enabled; 1 - Disabled | HST1 Enable | NONE | Config | None
HST1 Event Priority | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Event Priority | NONE | Config | None
HST1 Mag 1/2 Bin Threshold | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag 1/2 Bin Threshold | V | Config | None
HST1 Mag 2/3 Bin Threshold | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag 2/3 Bin Threshold | V | Config | None
HST1 Mag1/Dur1 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag1/Dur1 Bin Count | NONE | Config | None
HST1 Mag1/Dur2 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag1/Dur2 Bin Count | NONE | Config | None
HST1 Mag1/Dur3 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag1/Dur3 Bin Count | NONE | Config | None
HST1 Mag2/Dur1 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag2/Dur1 Bin Count | NONE | Config | None
HST1 Mag2/Dur2 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag2/Dur2 Bin Count | NONE | Config | None
HST1 Mag2/Dur3 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag2/Dur3 Bin Count | NONE | Config | None
HST1 Mag3/Dur1 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag3/Dur1 Bin Count | NONE | Config | None
HST1 Mag3/Dur2 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag3/Dur2 Bin Count | NONE | Config | None
HST1 Mag3/Dur3 Bin Count | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Mag3/Dur3 Bin Count | NONE | Config | None
HST1 Magnitude Threshold | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Magnitude Threshold | V | Config | None
HST1 Total Num Events | N/A | N/A | N/A |  | N/A | numeric |  | HST1 Total Num Events | NONE | Config | None
HST1 V1 Num Events | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V1 Num Events | NONE | Config | None
HST1 V1 Stress Accum | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V1 Stress Accum | NONE | Config | None
HST1 V2 Num Events | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V2 Num Events | NONE | Config | None
HST1 V2 Stress Accum | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V2 Stress Accum | NONE | Config | None
HST1 V3 Num Events | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V3 Num Events | NONE | Config | None
HST1 V3 Stress Accum | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V3 Stress Accum | NONE | Config | None
HST1 V4 Num Events | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V4 Num Events | NONE | Config | None
HST1 V4 Stress Accum | N/A | N/A | N/A |  | N/A | numeric |  | HST1 V4 Stress Accum | NONE | Config | None
HST1 Voltage Reference | N/A | N/A | N/A |  | N/A | enum | 0 - Vn; 1 - Ve | HST1 Voltage Reference | NONE | Config | None
I Nominal | N/A | N/A | N/A | --- | N/A | numeric | --- | I Nominal | A | Config | None
I4 CT Prim | N/A | N/A | N/A | --- | N/A | numeric | --- | I4 CT Prim | A | Config | None
I4 CT Sec | N/A | N/A | N/A | --- | N/A | numeric | --- | I4 CT Sec | A | Config | None
I4 Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | I4 Polarity | NONE | Config | None
I5 CT Prim | N/A | N/A | N/A | --- | N/A | numeric | --- | I5 CT Prim | A | Config | None
I5 CT Sec | N/A | N/A | N/A | --- | N/A | numeric | --- | I5 CT Sec | A | Config | None
I5 Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | I5 Polarity | NONE | Config | None
Ia Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | Ia Polarity | NONE | Config | None
Ib Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | Ib Polarity | NONE | Config | None
Ic Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | Ic Polarity | NONE | Config | None
Incremental Energy Interval | N/A | N/A | N/A | --- | N/A | numeric | --- | Incremental Energy Interval | S_3D | ENM | None
Internal Temp | N/A | N/A | N/A | --- | N/A | numeric | --- | Internal Temp | NONE | Config | None
IPv4 Address | N/A | N/A | N/A | --- | N/A | string | --- | IPv4 Address | NONE | Config | None
IPv4 Assignment Mode | N/A | N/A | N/A | --- | N/A | enum | 0 - Stored 1 - Acquired | IPv4 Assignment Mode | NONE | Config | None
IPv6 Assignment Mode | N/A | N/A | N/A | --- | N/A | enum | 0 - Stored 1 - Acquired | IPv6 Assignment Mode | NONE | Config | None
IPv6 Global Address | N/A | N/A | N/A | --- | N/A | string | --- | IPv6 Global Address | NONE | Config | None
IPv6 Link Local Address | N/A | N/A | N/A | --- | N/A | string | --- | IPv6 Link Local Address | NONE | Config | None
Language | N/A | N/A | N/A | --- | N/A | enum | 0 - English 1 - Spanish 2 - French 3 - Russian 4 - German 5 - Italian 6 - Portuguese 7 - Chinese (Simplified) | Language | NONE | Config | None
Local Time | N/A | N/A | N/A | --- | N/A | numeric | --- | Local Time | NONE | Config | None
MAC Address | N/A | N/A | N/A | --- | N/A | string | --- | MAC Address | NONE | Config | None
Master Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | Master Reset | NONE | IOM | None
Master Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Master Reset Count | NONE | IOM | None
Measurement Symbols | N/A | N/A | N/A | --- | N/A | enum | 0 - IEEE; 1 - IEC | Measurement Symbols | NONE | Config | None
Memory Used By Uploaded Files | N/A | N/A | N/A | --- | N/A | numeric | --- | Memory Used By Uploaded Files | NONE | Config | None
Meter Template | N/A | N/A | N/A | --- | N/A | string | --- | Meter Template | NONE | Config | None
Min/Max Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | Min/Max Reset | NONE | IOM | None
Min/Max Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Min/Max Reset Count | NONE | IOM | None
Modbus TCP Idle Timeout | N/A | N/A | N/A | --- | N/A | numeric | --- | Modbus TCP Idle Timeout | NONE | Config | None
Nominal Frequency | N/A | N/A | N/A | --- | N/A | enum | 0 - 60Hz; 1 - 50Hz | Nominal Frequency | NONE | Config | None
Normal Mode Screens Scroll Delay | N/A | N/A | N/A | --- | N/A | numeric | --- | Normal Mode Screens Scroll Delay | NONE | Config | None
NTP Server | N/A | N/A | N/A | --- | N/A | string | --- | NTP Server | NONE | Config | None
NTP Time Sync Interval | N/A | N/A | N/A | --- | N/A | numeric | --- | NTP Time Sync Interval | NONE | Config | None
Option module A FW version | N/A | N/A | N/A | --- | N/A | string | --- | Option module A FW version | NONE | Config | None
Option module A serial number | N/A | N/A | N/A | --- | N/A | string | --- | Option module A serial number | NONE | Config | None
Option module A status | N/A | N/A | N/A | --- | N/A | enum | --- | Option module A status | NONE | Config | None
Option module A type | N/A | N/A | N/A | --- | N/A | numeric | --- | Option module A type | NONE | Config | None
Option module A type string | N/A | N/A | N/A | --- | N/A | string | --- | Option module A type string | NONE | Config | None
Option module B FW version | N/A | N/A | N/A | --- | N/A | string | --- | Option module B FW version | NONE | Config | None
Option module B serial number | N/A | N/A | N/A | --- | N/A | string | --- | Option module B serial number | NONE | Config | None
Option module B status | N/A | N/A | N/A | --- | N/A | enum | --- | Option module B status | NONE | Config | None
Option module B type | N/A | N/A | N/A | --- | N/A | numeric | --- | Option module B type | NONE | Config | None
Option module B type string | N/A | N/A | N/A | --- | N/A | string | --- | Option module B type string | NONE | Config | None
Option module C FW version | N/A | N/A | N/A | --- | N/A | string | --- | Option module C FW version | NONE | Config | None
Option module C serial number | N/A | N/A | N/A | --- | N/A | string | --- | Option module C serial number | NONE | Config | None
Option module C status | N/A | N/A | N/A | --- | N/A | enum | --- | Option module C status | NONE | Config | None
Option module C type | N/A | N/A | N/A | --- | N/A | numeric | --- | Option module C type | NONE | Config | None
Option module C type string | N/A | N/A | N/A | --- | N/A | string | --- | Option module C type string | NONE | Config | None
Option module D FW version | N/A | N/A | N/A | --- | N/A | string | --- | Option module D FW version | NONE | Config | None
Option module D serial number | N/A | N/A | N/A | --- | N/A | string | --- | Option module D serial number | NONE | Config | None
Option module D status | N/A | N/A | N/A | --- | N/A | enum | --- | Option module D status | NONE | Config | None
Option module D type | N/A | N/A | N/A | --- | N/A | numeric | --- | Option module D type | NONE | Config | None
Option module D type string | N/A | N/A | N/A | --- | N/A | string | --- | Option module D type string | NONE | Config | None
Option Modules Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | Option Modules Reset | NONE | IOM | None
Option Modules Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Option Modules Reset Count | NONE | IOM | None
Owner | N/A | N/A | N/A | --- | N/A | string | --- | Owner | NONE | Config | None
Peak Demand Reset | N/A | N/A | N/A | --- | N/A | pulse | --- | Peak Demand Reset | NONE | IOM | None
Peak Demand Reset Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Peak Demand Reset Count | NONE | IOM | None
PF Convention | N/A | N/A | N/A | --- | N/A | enum | 0 - IEEE; 1 - IEC | PF Convention | NONE | Config | None
Phase Lbls | N/A | N/A | N/A | --- | N/A | enum | 0 - ABC; 1 - 123 | Phase Lbls | NONE | Config | None
PhaseOrder | N/A | N/A | N/A | --- | N/A | enum | 0 - ABC; 1 - ACB | PhaseOrder | NONE | Config | None
Power Resolution | N/A | N/A | N/A | --- | N/A | enum | 0 - 1. 1 - 1.X 2 - 1.XX 3 - 1.XXX 4 - 1.XXXX | Power Resolution | NONE | Config | None
Power Ups | N/A | N/A | N/A | --- | N/A | numeric | --- | Power Ups | NONE | Config | None
Primary DNS | N/A | N/A | N/A | --- | N/A | string | --- | Primary DNS | NONE | Config | None
Processing Power Used | N/A | N/A | N/A | --- | N/A | numeric | --- | Processing Power Used | NONE | Config | None
PT Prim | N/A | N/A | N/A | --- | N/A | numeric | --- | PT Prim | V | Config | None
PT Sec | N/A | N/A | N/A | --- | N/A | numeric | --- | PT Sec | V | Config | None
Pulse Constant | N/A | N/A | N/A | --- | N/A | numeric | --- | Pulse Constant | NONE | Config | None
R1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | R1 State | NONE | IO | None
R2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | R2 State | NONE | IO | None
Read-only Community Name | N/A | N/A | N/A | --- | N/A | string | --- | Read-only Community Name | NONE | Config | None
Read-write Community Name | N/A | N/A | N/A | --- | N/A | string | --- | Read-write Community Name | NONE | Config | None
Regulation Tag 1 | N/A | N/A | N/A |  | N/A | string |  | Regulation Tag 1 | NONE | Config | None
Report Buffer Size | N/A | N/A | N/A | --- | N/A | numeric | --- | Report Buffer Size | NONE | Config | None
Report Hold Time | N/A | N/A | N/A | --- | N/A | numeric | --- | Report Hold Time | NONE | Config | None
RMD Revision | N/A | N/A | N/A | --- | N/A | string | --- | RMD Revision | NONE | Config | None
RMD Serial Number | N/A | N/A | N/A | --- | N/A | string | --- | RMD Serial Number | NONE | Config | None
RMD State | N/A | N/A | N/A | --- | N/A | enum | --- | RMD State | NONE | Config | None
RMD Temp | N/A | N/A | N/A | --- | N/A | numeric | --- | RMD Temp | NONE | Config | None
RSP1 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP1 Enable | NONE | Config | None
RSP10 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP10 Enable | NONE | Config | None
RSP11 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP11 Enable | NONE | Config | None
RSP12 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP12 Enable | NONE | Config | None
RSP13 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP13 Enable | NONE | Config | None
RSP14 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP14 Enable | NONE | Config | None
RSP15 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP15 Enable | NONE | Config | None
RSP16 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP16 Enable | NONE | Config | None
RSP17 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP17 Enable | NONE | Config | None
RSP18 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP18 Enable | NONE | Config | None
RSP19 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP19 Enable | NONE | Config | None
RSP2 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP2 Enable | NONE | Config | None
RSP20 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP20 Enable | NONE | Config | None
RSP21 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP21 Enable | NONE | Config | None
RSP22 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP22 Enable | NONE | Config | None
RSP23 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP23 Enable | NONE | Config | None
RSP24 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP24 Enable | NONE | Config | None
RSP25 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP25 Enable | NONE | Config | None
RSP26 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP26 Enable | NONE | Config | None
RSP27 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP27 Enable | NONE | Config | None
RSP28 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP28 Enable | NONE | Config | None
RSP29 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP29 Enable | NONE | Config | None
RSP3 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP3 Enable | NONE | Config | None
RSP30 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP30 Enable | NONE | Config | None
RSP4 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP4 Enable | NONE | Config | None
RSP5 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP5 Enable | NONE | Config | None
RSP6 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP6 Enable | NONE | Config | None
RSP7 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP7 Enable | NONE | Config | None
RSP8 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP8 Enable | NONE | Config | None
RSP9 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | RSP9 Enable | NONE | Config | None
S1 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S1 State | NONE | IO | None
S2 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S2 State | NONE | IO | None
S3 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S3 State | NONE | IO | None
S4 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S4 State | NONE | IO | None
S5 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S5 State | NONE | IO | None
S6 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S6 State | NONE | IO | None
S7 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S7 State | NONE | IO | None
S8 State | N/A | N/A | N/A | --- | N/A | boolean | --- | S8 State | NONE | IO | None
Season 1 | N/A | N/A | N/A | --- | N/A | boolean | --- | Season 1 | NONE | TOM | None
Season 2 | N/A | N/A | N/A | --- | N/A | boolean | --- | Season 2 | NONE | TOM | None
Season 3 | N/A | N/A | N/A | --- | N/A | boolean | --- | Season 3 | NONE | TOM | None
Season 4 | N/A | N/A | N/A | --- | N/A | boolean | --- | Season 4 | NONE | TOM | None
Secondary DNS | N/A | N/A | N/A | --- | N/A | string | --- | Secondary DNS | NONE | Config | None
SFTP/SSH Port Number | N/A | N/A | N/A | --- | N/A | numeric | --- | SFTP/SSH Port Number | NONE | Config | None
SMTP Connection Timeout | N/A | N/A | N/A | --- | N/A | numeric | --- | SMTP Connection Timeout | NONE | Config | None
SMTP Server | N/A | N/A | N/A | --- | N/A | string | --- | SMTP Server | NONE | Config | None
SNMP Port Number | N/A | N/A | N/A | --- | N/A | numeric | --- | SNMP Port Number | NONE | Config | None
SP1 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP1 Enable | NONE | Config | None
SP10 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP10 Enable | NONE | Config | None
SP11 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP11 Enable | NONE | Config | None
SP12 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP12 Enable | NONE | Config | None
SP13 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP13 Enable | NONE | Config | None
SP14 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP14 Enable | NONE | Config | None
SP15 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP15 Enable | NONE | Config | None
SP16 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP16 Enable | NONE | Config | None
SP17 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP17 Enable | NONE | Config | None
SP18 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP18 Enable | NONE | Config | None
SP19 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP19 Enable | NONE | Config | None
SP2 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP2 Enable | NONE | Config | None
SP20 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP20 Enable | NONE | Config | None
SP21 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP21 Enable | NONE | Config | None
SP22 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP22 Enable | NONE | Config | None
SP23 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP23 Enable | NONE | Config | None
SP24 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP24 Enable | NONE | Config | None
SP25 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP25 Enable | NONE | Config | None
SP26 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP26 Enable | NONE | Config | None
SP27 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP27 Enable | NONE | Config | None
SP28 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP28 Enable | NONE | Config | None
SP29 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP29 Enable | NONE | Config | None
SP3 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP3 Enable | NONE | Config | None
SP30 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP30 Enable | NONE | Config | None
SP31 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP31 Enable | NONE | Config | None
SP32 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP32 Enable | NONE | Config | None
SP33 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP33 Enable | NONE | Config | None
SP34 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP34 Enable | NONE | Config | None
SP35 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP35 Enable | NONE | Config | None
SP36 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP36 Enable | NONE | Config | None
SP37 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP37 Enable | NONE | Config | None
SP38 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP38 Enable | NONE | Config | None
SP39 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP39 Enable | NONE | Config | None
SP4 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP4 Enable | NONE | Config | None
SP40 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP40 Enable | NONE | Config | None
SP41 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP41 Enable | NONE | Config | None
SP42 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP42 Enable | NONE | Config | None
SP43 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP43 Enable | NONE | Config | None
SP44 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP44 Enable | NONE | Config | None
SP45 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP45 Enable | NONE | Config | None
SP46 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP46 Enable | NONE | Config | None
SP47 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP47 Enable | NONE | Config | None
SP48 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP48 Enable | NONE | Config | None
SP49 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP49 Enable | NONE | Config | None
SP5 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP5 Enable | NONE | Config | None
SP50 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP50 Enable | NONE | Config | None
SP51 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP51 Enable | NONE | Config | None
SP52 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP52 Enable | NONE | Config | None
SP53 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP53 Enable | NONE | Config | None
SP54 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP54 Enable | NONE | Config | None
SP55 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP55 Enable | NONE | Config | None
SP56 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP56 Enable | NONE | Config | None
SP57 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP57 Enable | NONE | Config | None
SP58 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP58 Enable | NONE | Config | None
SP59 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP59 Enable | NONE | Config | None
SP6 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP6 Enable | NONE | Config | None
SP60 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP60 Enable | NONE | Config | None
SP61 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP61 Enable | NONE | Config | None
SP62 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP62 Enable | NONE | Config | None
SP63 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP63 Enable | NONE | Config | None
SP64 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP64 Enable | NONE | Config | None
SP65 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP65 Enable | NONE | Config | None
SP7 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP7 Enable | NONE | Config | None
SP8 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP8 Enable | NONE | Config | None
SP9 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SP9 Enable | NONE | Config | None
SS1 Enable | N/A | N/A | N/A | --- | N/A | enum | 0 - Yes; 1 - No | SS1 Enable | NONE | Config | None
Stored IPv4 Address | N/A | N/A | N/A | --- | N/A | string | --- | Stored IPv4 Address | NONE | Config | None
Stored IPv4 Gateway | N/A | N/A | N/A | --- | N/A | string | --- | Stored IPv4 Gateway | NONE | Config | None
Stored IPv4 Subnet Mask | N/A | N/A | N/A | --- | N/A | string | --- | Stored IPv4 Subnet Mask | NONE | Config | None
Stored IPv6 Gateway | N/A | N/A | N/A | --- | N/A | string | --- | Stored IPv6 Gateway | NONE | Config | None
Stored IPv6 Global Address | N/A | N/A | N/A | --- | N/A | string | --- | Stored IPv6 Global Addr | NONE | Config | None
System Contact | N/A | N/A | N/A | --- | N/A | string | --- | System Contact | NONE | Config | None
System Location | N/A | N/A | N/A | --- | N/A | string | --- | System Location | NONE | Config | None
System Name | N/A | N/A | N/A | --- | N/A | string | --- | System Name | NONE | Config | None
Tag 1 | N/A | N/A | N/A | --- | N/A | string | --- | Tag 1 | NONE | Config | None
Tag 2 | N/A | N/A | N/A | --- | N/A | string | --- | Tag 2 | NONE | Config | None
TCP Keep Alive Minutes | N/A | N/A | N/A | --- | N/A | numeric | --- | TCP Keep Alive Minutes | NONE | Config | None
Time Format | N/A | N/A | N/A | --- | N/A | enum | 0 - 12H; 1 -24H | Time Format | NONE | Config | None
Time Since Last Time Sync | N/A | N/A | N/A | --- | N/A | numeric | --- | Time Since Last Time Sync | NONE | Config | None
Time Sync Count | N/A | N/A | N/A | --- | N/A | numeric | --- | Time Sync Count | NONE | Config | None
Time Sync Source | N/A | N/A | N/A | --- | N/A | enum | 0 - COM1 1 - ETHERNET 2 - ETHERNET - ION 3 - ETHERNET - DNP 4 - IRIG-B | Time Sync Source | NONE | Config | None
Time Sync Type | N/A | N/A | N/A | --- | N/A | enum | 0 - UTC 1 - LOCAL | Time Sync Type | NONE | Config | None
Total Buffer Memory | N/A | N/A | N/A | --- | N/A | numeric | --- | Total Buffer Memory | NONE | Config | None
Total Internal Memory | N/A | N/A | N/A | --- | N/A | numeric | --- | Total Internal Memory | NONE | Config | None
TOU Rate A | N/A | N/A | N/A | --- | N/A | boolean | --- | TOU Rate A | NONE | TOM | None
TOU Rate B | N/A | N/A | N/A | --- | N/A | boolean | --- | TOU Rate B | NONE | TOM | None
TOU Rate C | N/A | N/A | N/A | --- | N/A | boolean | --- | TOU Rate C | NONE | TOM | None
TOU Rate D | N/A | N/A | N/A | --- | N/A | boolean | --- | TOU Rate D | NONE | TOM | None
Trap Rcvr1 Addr | N/A | N/A | N/A | --- | N/A | string | --- | Trap Rcvr1 Addr | NONE | Config | None
Trap Rcvr2 Addr | N/A | N/A | N/A | --- | N/A | string | --- | Trap Rcvr2 Addr | NONE | Config | None
Trap Rcvr3 Addr | N/A | N/A | N/A | --- | N/A | string | --- | Trap Rcvr3 Addr | NONE | Config | None
Trap Rcvr4 Addr | N/A | N/A | N/A | --- | N/A | string | --- | Trap Rcvr4 Addr | NONE | Config | None
TZ Offset | N/A | N/A | N/A | --- | N/A | numeric | --- | TZ Offset | NONE | Config | None
V Nominal | N/A | N/A | N/A | --- | N/A | numeric | --- | V Nominal | V | Config | None
V4 Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | V4 Polarity | NONE | Config | None
V4 PT Prim | N/A | N/A | N/A | --- | N/A | numeric | --- | V4 PT Prim | V | Config | None
V4 PT Sec | N/A | N/A | N/A | --- | N/A | numeric | --- | V4 PT Sec | V | Config | None
Va Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | Va Polarity | NONE | Config | None
Vb Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | Vb Polarity | NONE | Config | None
Vc Polarity | N/A | N/A | N/A | --- | N/A | enum | 0 - Normal; 1 - Inverted | Vc Polarity | NONE | Config | None
Volts Mode | N/A | N/A | N/A | --- | N/A | enum | 0 - 4W-WYE 1 - DELTA 2 - SINGLE 3 - DEMO 4 - 3W-WYE | Volts Mode | NONE | Config | None
Volts Resolution | N/A | N/A | N/A | --- | N/A | enum | 0 - 1. 1 - 1.X 2 - 1.XX 3 - 1.XXX 4 - 1.XXXX | Volts Resolution | NONE | Config | None
Web Server Port Number | N/A | N/A | N/A | --- | N/A | numeric | --- | Web Server Port Number | NONE | Config | None

## Data Types
Data Type | Description
UTF8 | UTF8 encoded string
INT16 | signed 16-bit integer
INT16U | unsigned 16-bit integer
INT32 | signed 32-bit integer
INT32U | unsigned 32-bit integer
INT64 | signed 64-bit integer
FLOAT32 | 32-bit IEEE-754 floating point number (single precision)
FLOAT64 | 64-bit IEEE-754 floating point number (double precision)
FLOAT32_TS | 6-word value encoded as follows: -words 1-2 - a FLOAT32 value -words 3-6 - a DATETIME value
DATETIME | DateTime coding format using 4 words as per IEC 870-5-4 Word 1 b0-b6: Year (0 - 127) b7-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved Word 3 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 4 b0-b15: Millisecond (0 - 59999)
DATE | Word 1 b0-b7: Year (0 - 99) b8-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved
TIME | Word 1 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 2 b0-b15: Millisecond (0 - 59999)
BITMAP | 16-bit binary register where each bit represents a specific quantity

## Value Types
Value Type | Description
numeric | A number which could be positive or negative, integer or decimal.
string | A UTF8 encoded string.
enum | A enumeration. This value will be represented as a positive integer and every positive integer will correspond with a specific setting for the register.
bitmap | Each bit in this value represents a status for a particular
boolean | A bi-state value. 0 = OFF; 1 = ON.
pulse | This is a special control type. Writing a 1 to this value will perform a pulse operation in ION.

## Data Mapping Modules
Short name | Long name | Description
DEM | Data mapping demand module | This module contains demand related values.
ENM | Data mapping energy module | This module contains energy related values.
ECM | Data mapping EN50160 current interval module | This module contains counters and statistics for the current EN50160 interval.
EPM | Data mapping EN50160 previous interval module | This module contains counters for the previous EN50160 interval.
IEM | Data Mapping IEEE519 module | The module contains counters and data for the IEEE519 monitoring.
IOM | Data mapping IO module | This module contains IO values such as digital input and outputs, resets, and setpoints.
MEM | Data mapping measurements module | This module contains direct measurement values such as voltage, current, power, and frequency.
PQM | Data mapping power quality module | This module contains power quality related values such as harmonics, sag/swell, and symmetric components.
STM | Data mapping statistics module | This module contains statistic related values such as minimums, maximums, and averages.
TOM | Data mapping time of use module | This module contains time of use related values.
Config | N/A | A configuration parameter. Any item marked as "Config" is not remappable through a data mapping module, but can be enabled/disabled in the Modbus map through the MEM module