## Instructions
NHA80944 | V4.5 | ATV900 - Communication Parameters
/!\ WARNING
UNEXPECTED MOVEMENT
Drive systems may perform unexpected movements because of incorrect wiring, incorrect settings, incorrect data or other errors. • Only appropriately trained persons who are familiar with and understand the contents of all pertinent product documentation and who have received safety training to recognize and avoid hazards involved are authorized to work on and with this drive system. Installation, adjustment, repair and maintenance must be performed by qualified personnel. • Carefully install the wiring in accordance with the EMC requirements. • Do not operate the product with unknown or unsuitable settings or data. • Perform a comprehensive commissioning test.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
/!\ WARNING
LOSS OF CONTROL
• The designer of any control scheme must consider the potential failure modes of control paths and, for critical control functions, provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop, overtravel stop, power outage and restart. • Separate or redundant control paths must be provided for critical control functions. • System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. • Observe all accident prevention regulations and local safety guidelines (1). • Each implementation of the product must be individually and thoroughly tested for proper operation before being placed into service.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code:
Language-independent, this allows a rapid search in the programming manual, which includes an index of parameter codes.
Additional information can be found in the Communication Manuals (Modbus, CANopen....etc.....)
Name:
Parameter designation
Logic address:
Addresses for Modbus, Profibus, Profinet and Ethernet TCP
Address for the messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index:
Addresses for CANopen, PowerLink and EtherCAT.
CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
DeviceNet path:
Address for DeviceNet and Ethernet IP.
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link:
- For WORD (listing), a dynamic link opens its description. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
- For WORD (bit register), in the Type column, a dynamic link opens its description.
Category:
Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access:
Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units:
Physical unit and multiplier.
Factory setting:
Value of the parameter set at the factory.
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Range:
Possible values.
Display:
Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order:
Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | CIP path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 |  | Control parameters | R/W | WORD (BitString16) | -
CMD | Command register | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 |  | Control parameters | R/W | WORD (BitString16) | - |  |  | [Cmd Register] (CMD) | [Communication map] (CMM)
RPR | Counter reset | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] NO |  | [Counter Reset] (RPR) | [Counter Management] (ELT) [Maintenance] (CSMA)
LFRD | Speed setpoint | 16#219A = 8602 | 16#2038/3 | 16#8C/01/03 = 140/01/03 |  | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 rpm | -32767 rpm ... 32767 rpm
LFR | Reference frequency | 16#2136 = 8502 | 16#2037/3 | 16#8B/01/67 = 139/01/103 |  | Setpoint parameters | R/W | INT (Signed16) | Refer to programming manual | 0 | -5990 ... 5990 | [Ref Frequency] (LFR) | [Drive parameters] (MPI)
PISP | PIDSet point | 16#2137 = 8503 | 16#2037/4 | 16#8B/01/68 = 139/01/104 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 1000
AIV1 | AIV1 Image input | 16#14A1 = 5281 | 16#2016/52 | 16#7B/01/52 = 123/01/82 |  | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -10000 ... 10000 | [AIV1 Image input] (AIV1) | [Drive parameters] (MPI)
MFR | Multiplying coefficient | 16#2E37 = 11831 | 16#2058/20 | 16#9C/01/20 = 156/01/32 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [Multiplying coeff.] (MFR) | [Drive parameters] (MPI) [Settings] (SET)
ETA | Status Register | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 |  | Status parameters | R | WORD (BitString16) | - |  |  | [Status Register] (ETA) | [Communication map] (CMM)
HMIS | Device state | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HMIS) | [System] (DST)
ETI | Internal State register | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 |  | Status parameters | R | WORD (BitString16) | -
CRC | Channel for reference frequency | 16#20F9 = 8441 | 16#2036/2A | 16#8B/01/2A = 139/01/42 |  | Status parameters | R | WORD (BitString16) | -
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 |  | Status parameters | R | WORD (BitString16) | -
CNFS | Active configuration | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | - |  |  | [Config. active] (CNFS) | [Drive parameters] (MPI)
STUN | Tune selection | 16#2591 = 9617 | 16#2042/12 | 16#91/01/12 = 145/01/18 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] TAB |  | [Tune selection] (STUN) | [Simply start] (SIM) [Motor tune] (MTU)
STUR | Rotation tune selection | 16#2669 = 9833 | 16#2044/22 | 16#92/01/22 = 146/01/34 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] TAB |  | [Rotation Tune Select] (STUR) | [Rotation Tune] (TRAM)
TUNV | Autotuning flux verification value | 16#266B = 9835 | 16#2044/24 | 16#92/01/24 = 146/01/36 |  | Status parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Autotuning flux verif] (TUNV) | [Rotation Tune] (TRAM)
SMOT | Status of motor tune in term of saliency | 16#25AD = 9645 | 16#2042/2E | 16#91/01/2E = 145/01/46 | SMOT | Status parameters | R | WORD (Enumeration) | - |  |  | [Saliency mot. state] (SMOT) | [Motor tune] (MTU)
ECSS | EtherCAT slave status | 16#1A22 = 6690 | 16#2024/5B | 16#82/01/5B = 130/01/91 | ETST | Status parameters | R/W | WORD (Enumeration) | - |  |  | [EthCat slave status] (ECSS) | [EtherCAT Module] (ETC)
ECAA | EtherCAT address | 16#1A24 = 6692 | 16#2024/5D | 16#82/01/5D = 130/01/93 |  | Status parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat addr] (ECAA) | [EtherCAT Module] (ETC)
RFRD | Output velocity | 16#219C = 8604 | 16#2038/5 | 16#8C/01/05 = 140/01/05 |  | Actual values parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
RFR | Motor frequency | 16#0C82 = 3202 | 16#2002/3 | 16#71/01/03 = 113/01/03 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor Frequency] (RFR) | [M/S Local Display] (MSO) [Drive parameters] (MPI)
OTR | Motor torque | 16#0C85 = 3205 | 16#2002/6 | 16#71/01/06 = 113/01/06 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor torque] (OTR) | [Motor parameters] (MMO)
LCR | Motor current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Current] (LCR) | [System] (DST) [Motor parameters] (MMO)
UOP | Motor voltage | 16#0C88 = 3208 | 16#2002/9 | 16#71/01/09 = 113/01/09 |  | Actual values parameters | R | UINT (Unsigned16) | 1 V |  | 0 V ... 65535 V | [Motor voltage] (UOP) | [Motor parameters] (MMO)
OPR | Motor power in % | 16#0C8B = 3211 | 16#2002/C | 16#71/01/0C = 113/01/12 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Mot Mech Power in %] (OPR) | [Motor parameters] (MMO)
FRHD | Speed reference before ramp | 16#219D = 8605 | 16#2038/6 | 16#8C/01/06 = 140/01/06 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FROD | Speed reference after ramp | 16#21C1 = 8641 | 16#2038/2A | 16#8C/01/2A = 140/01/42 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FRH | Reference frequency before ramp | 16#0C83 = 3203 | 16#2002/4 | 16#71/01/04 = 113/01/04 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -599.0 Hz ... 599.0 Hz | [Pre-Ramp Ref Freq] (FRH) | [System] (DST) [Drive parameters] (MPI) [Communication map] (CMM)
FRO | Frequency reference after ramp | 16#233D = 9021 | 16#203C/16 | 16#8E/01/16 = 142/01/22 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
RPC | PID reference | 16#2ECE = 11982 | 16#2059/53 | 16#9C/01/B7 = 156/01/183 |  | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [PID reference] (RPC) | [PID display] (PIC)
RPF | PID feedback | 16#2ECD = 11981 | 16#2059/52 | 16#9C/01/B6 = 156/01/182 |  | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [PID feedback] (RPF) | [PID display] (PIC) [PID Feedback] (FDB) [PID Feedback] (FDB)
RPE | PID error | 16#2ECC = 11980 | 16#2059/51 | 16#9C/01/B5 = 156/01/181 |  | Reference parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [PID Error] (RPE) | [PID display] (PIC)
RPO | PID output | 16#2ECF = 11983 | 16#2059/54 | 16#9C/01/B8 = 156/01/184 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [PID Output] (RPO) | [PID display] (PIC)
ULN | Mains voltage | 16#0C87 = 3207 | 16#2002/8 | 16#71/01/08 = 113/01/08 |  | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULN) | [Drive parameters] (MPI)
THD | Drive thermal state | 16#0C89 = 3209 | 16#2002/A | 16#71/01/0A = 113/01/10 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Drive Therm State] (THD) | [Drive parameters] (MPI)
THR | Motor thermal state | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Motor Therm State] (THR) | [System] (DST) [Motor parameters] (MMO)
RTH | Motor run time | 16#0CAC = 3244 | 16#2002/2D | 16#71/01/2D = 113/01/45 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
PTH | Power-on time | 16#0CAE = 3246 | 16#2002/2F | 16#71/01/2F = 113/01/47 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 |  | I/O parameters | R | WORD (BitString16) | -
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 |  | I/O parameters | R/W | WORD (BitString16) | -
AI1C | Physical value AI1 | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2C | Physical value AI2 | 16#147B = 5243 | 16#2016/2C | 16#7B/01/2C = 123/01/44 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI2R | Analog input 2 standardized value | 16#1471 = 5233 | 16#2016/22 | 16#7B/01/22 = 123/01/34 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3C | Physical value AI3 | 16#147C = 5244 | 16#2016/2D | 16#7B/01/2D = 123/01/45 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI3R | Analog input 3 standardized value | 16#1472 = 5234 | 16#2016/23 | 16#7B/01/23 = 123/01/35 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1C | AQ1 physical value | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
FQS | Pulse input measured frequency | 16#390B = 14603 | 16#2074/4 | 16#AA/01/04 = 170/01/04 |  | I/O parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 30000 Hz | [Measured Freq] (FQS) | [Drive parameters] (MPI)
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 | ERRD | Fault parameters | R | WORD (BitString16) | -
LFT | Last error occurred | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | - |  |  | [Last Error] (LFT) | [Diag. data] (DDT)
DSC | Subcode of the current fault | 16#1BF5 = 7157 | 16#2029/3A | 16#84/01/9E = 132/01/158 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 |  | Fault parameters | R/WS | WORD (BitString16) | -
CNF | Fieldbus module Communication interruption | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Fieldbus Com Interrupt] (CNF) | [DEVICENET DIAG] (DVN) [Profibus diag] (PRB) [Profinet diag] (PRN) [EtherCAT Module Diag] (ETD) [POWERLINK DIAG] (PWL)
ILF1 | Internal communication interruption 1 | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [InternCom Error1] (ILF1) | [Profibus diag] (PRB) [Profinet diag] (PRN) [EtherCAT Module Diag] (ETD) [POWERLINK DIAG] (PWL)
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
ULP0 | DC bus voltage | 16#1C66 = 7270 | 16#202A/47 | 16#85/01/47 = 133/01/71 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
LCP0 | Motor current | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
RFP0 | Output frequency | 16#1C52 = 7250 | 16#202A/33 | 16#85/01/33 = 133/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
THP0 | Motor thermal state | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
EP0 | State word | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 |  | History parameters | R | WORD (BitString16) | -
IP0 | ETI state word | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 |  | History parameters | R | WORD (BitString16) | -
CMP0 | Cmd word | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 |  | History parameters | R | WORD (BitString16) | -
DCC0 | Command channel | 16#FB2C = 64300 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
DRC0 | Channel for reference frequency | 16#FB36 = 64310 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
CRP0 | Channels active on last fault | 16#1C7A = 7290 | 16#202A/5B | 16#85/01/5B = 133/01/91 |  | History parameters | R | WORD (BitString16) | -
RTP0 | Run Elapsed time | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
OTP0 | Motor torque | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP0 | Drive thermal state | 16#1CAC = 7340 | 16#202B/29 | 16#85/01/8D = 133/01/141 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP0 | IGBT junction temp | 16#1CB6 = 7350 | 16#202B/33 | 16#85/01/97 = 133/01/151 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP0 | Switching frequency | 16#1CC0 = 7360 | 16#202B/3D | 16#85/01/A1 = 133/01/161 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
ULP1 | DC bus voltage | 16#1C67 = 7271 | 16#202A/48 | 16#85/01/48 = 133/01/72 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP1) | [None] (DP1)
LCP1 | Motor current | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP1) | [None] (DP1)
RFP1 | Output frequency | 16#1C53 = 7251 | 16#202A/34 | 16#85/01/34 = 133/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP1) | [None] (DP1)
THP1 | Motor thermal state | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP1) | [None] (DP1)
EP1 | Status of last error 1 | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 1 Status] (EP1) | [None] (DP1)
IP1 | ETI state word | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP1) | [None] (DP1)
CMP1 | Cmd word | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP1) | [None] (DP1)
DCC1 | Command channel | 16#FB2D = 64301 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC1) | [None] (DP1)
DRC1 | Channel for reference frequency | 16#FB37 = 64311 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC1) | [None] (DP1)
CRP1 | Active channels on fault n-1 | 16#1C7B = 7291 | 16#202A/5C | 16#85/01/5C = 133/01/92 |  | History parameters | R | WORD (BitString16) | -
RTP1 | Run Elapsed time | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP1) | [None] (DP1)
OTP1 | Motor torque | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP1) | [None] (DP1)
TDP1 | Drive thermal state | 16#1CAD = 7341 | 16#202B/2A | 16#85/01/8E = 133/01/142 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP1) | [None] (DP1)
TJP1 | IGBT junction temp | 16#1CB7 = 7351 | 16#202B/34 | 16#85/01/98 = 133/01/152 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP1) | [None] (DP1)
SFP1 | Switching frequency | 16#1CC1 = 7361 | 16#202B/3E | 16#85/01/A2 = 133/01/162 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP1) | [None] (DP1)
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
ULP2 | DC bus voltage | 16#1C68 = 7272 | 16#202A/49 | 16#85/01/49 = 133/01/73 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP2) | [None] (DP2)
LCP2 | Motor current | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP2) | [None] (DP2)
RFP2 | Output frequency | 16#1C54 = 7252 | 16#202A/35 | 16#85/01/35 = 133/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP2) | [None] (DP2)
THP2 | Motor thermal state | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP2) | [None] (DP2)
EP2 | Status of last error 2 | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 2 Status] (EP2) | [None] (DP2)
IP2 | ETI state word | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP2) | [None] (DP2)
CMP2 | Cmd word | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP2) | [None] (DP2)
DCC2 | Command channel | 16#FB2E = 64302 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC2) | [None] (DP2)
DRC2 | Channel for reference frequency | 16#FB38 = 64312 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC2) | [None] (DP2)
CRP2 | Active channels on fault n-2 | 16#1C7C = 7292 | 16#202A/5D | 16#85/01/5D = 133/01/93 |  | History parameters | R | WORD (BitString16) | -
RTP2 | Run Elapsed time | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP2) | [None] (DP2)
OTP2 | Motor torque | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP2) | [None] (DP2)
TDP2 | Drive thermal state | 16#1CAE = 7342 | 16#202B/2B | 16#85/01/8F = 133/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP2) | [None] (DP2)
TJP2 | IGBT junction temp | 16#1CB8 = 7352 | 16#202B/35 | 16#85/01/99 = 133/01/153 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP2) | [None] (DP2)
SFP2 | Switching frequency | 16#1CC2 = 7362 | 16#202B/3F | 16#85/01/A3 = 133/01/163 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP2) | [None] (DP2)
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
ULP3 | DC bus voltage | 16#1C69 = 7273 | 16#202A/4A | 16#85/01/4A = 133/01/74 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP3) | [None] (DP3)
LCP3 | Motor current | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP3) | [None] (DP3)
RFP3 | Output frequency | 16#1C55 = 7253 | 16#202A/36 | 16#85/01/36 = 133/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP3) | [None] (DP3)
THP3 | Motor thermal state | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP3) | [None] (DP3)
EP3 | Status of last error 3 | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 3 Status] (EP3) | [None] (DP3)
IP3 | ETI state word | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP3) | [None] (DP3)
CMP3 | Cmd word | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP3) | [None] (DP3)
DCC3 | Command channel | 16#FB2F = 64303 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC3) | [None] (DP3)
DRC3 | Channel for reference frequency | 16#FB39 = 64313 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC3) | [None] (DP3)
CRP3 | Active channels on fault n-3 | 16#1C7D = 7293 | 16#202A/5E | 16#85/01/5E = 133/01/94 |  | History parameters | R | WORD (BitString16) | -
RTP3 | Run Elapsed time | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP3) | [None] (DP3)
OTP3 | Motor torque | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP3) | [None] (DP3)
TDP3 | Drive thermal state | 16#1CAF = 7343 | 16#202B/2C | 16#85/01/90 = 133/01/144 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP3) | [None] (DP3)
TJP3 | IGBT junction temp | 16#1CB9 = 7353 | 16#202B/36 | 16#85/01/9A = 133/01/154 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP3) | [None] (DP3)
SFP3 | Switching frequency | 16#1CC3 = 7363 | 16#202B/40 | 16#85/01/A4 = 133/01/164 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP3) | [None] (DP3)
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
ULP4 | DC bus voltage | 16#1C6A = 7274 | 16#202A/4B | 16#85/01/4B = 133/01/75 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP4) | [None] (DP4)
LCP4 | Motor current | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP4) | [None] (DP4)
RFP4 | Output frequency | 16#1C56 = 7254 | 16#202A/37 | 16#85/01/37 = 133/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP4) | [None] (DP4)
THP4 | Motor thermal state | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP4) | [None] (DP4)
EP4 | Status of last error 4 | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 4 Status] (EP4) | [None] (DP4)
IP4 | ETI state word | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP4) | [None] (DP4)
CMP4 | Cmd word | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP4) | [None] (DP4)
DCC4 | Command channel | 16#FB30 = 64304 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC4) | [None] (DP4)
DRC4 | Channel for reference frequency | 16#FB3A = 64314 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC4) | [None] (DP4)
CRP4 | Active channels on fault n-4 | 16#1C7E = 7294 | 16#202A/5F | 16#85/01/5F = 133/01/95 |  | History parameters | R | WORD (BitString16) | -
RTP4 | Run Elapsed time | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP4) | [None] (DP4)
OTP4 | Motor torque | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP4) | [None] (DP4)
TDP4 | Drive thermal state | 16#1CB0 = 7344 | 16#202B/2D | 16#85/01/91 = 133/01/145 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP4) | [None] (DP4)
TJP4 | IGBT junction temp | 16#1CBA = 7354 | 16#202B/37 | 16#85/01/9B = 133/01/155 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP4) | [None] (DP4)
SFP4 | Switching frequency | 16#1CC4 = 7364 | 16#202B/41 | 16#85/01/A5 = 133/01/165 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP4) | [None] (DP4)
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
ULP5 | DC bus voltage | 16#1C6B = 7275 | 16#202A/4C | 16#85/01/4C = 133/01/76 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP5) | [None] (DP5)
LCP5 | Motor current | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP5) | [None] (DP5)
RFP5 | Output frequency | 16#1C57 = 7255 | 16#202A/38 | 16#85/01/38 = 133/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP5) | [None] (DP5)
THP5 | Motor thermal state | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP5) | [None] (DP5)
EP5 | State word | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP5) | [None] (DP5)
IP5 | ETI state word | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP5) | [None] (DP5)
CMP5 | Cmd word | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP5) | [None] (DP5)
DCC5 | Command channel | 16#FB31 = 64305 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC5) | [None] (DP5)
DRC5 | Channel for reference frequency | 16#FB3B = 64315 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC5) | [None] (DP5)
CRP5 | Active channels on fault n-5 | 16#1C7F = 7295 | 16#202A/60 | 16#85/01/60 = 133/01/96 |  | History parameters | R | WORD (BitString16) | -
RTP5 | Run Elapsed time | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP5) | [None] (DP5)
OTP5 | Motor torque | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP5) | [None] (DP5)
TDP5 | Drive thermal state | 16#1CB1 = 7345 | 16#202B/2E | 16#85/01/92 = 133/01/146 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP5) | [None] (DP5)
TJP5 | IGBT junction temp | 16#1CBB = 7355 | 16#202B/38 | 16#85/01/9C = 133/01/156 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP5) | [None] (DP5)
SFP5 | Switching frequency | 16#1CC5 = 7365 | 16#202B/42 | 16#85/01/A6 = 133/01/166 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP5) | [None] (DP5)
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | -
ULP6 | DC bus voltage | 16#1C6C = 7276 | 16#202A/4D | 16#85/01/4D = 133/01/77 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP6) | [None] (DP6)
LCP6 | Motor current | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP6) | [None] (DP6)
RFP6 | Output frequency | 16#1C58 = 7256 | 16#202A/39 | 16#85/01/39 = 133/01/57 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP6) | [None] (DP6)
THP6 | Motor thermal state | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP6) | [None] (DP6)
EP6 | State word | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP6) | [None] (DP6)
IP6 | ETI state word | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP6) | [None] (DP6)
CMP6 | Cmd word | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP6) | [None] (DP6)
DCC6 | Command channel | 16#FB32 = 64306 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC6) | [None] (DP6)
DRC6 | Channel for reference frequency | 16#FB3C = 64316 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC6) | [None] (DP6)
CRP6 | Active channels on fault n-6 | 16#1C80 = 7296 | 16#202A/61 | 16#85/01/61 = 133/01/97 |  | History parameters | R | WORD (BitString16) | -
RTP6 | Run Elapsed time | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP6) | [None] (DP6)
OTP6 | Motor torque | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP6) | [None] (DP6)
TDP6 | Drive thermal state | 16#1CB2 = 7346 | 16#202B/2F | 16#85/01/93 = 133/01/147 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP6) | [None] (DP6)
TJP6 | IGBT junction temp | 16#1CBC = 7356 | 16#202B/39 | 16#85/01/9D = 133/01/157 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP6) | [None] (DP6)
SFP6 | Switching frequency | 16#1CC6 = 7366 | 16#202B/43 | 16#85/01/A7 = 133/01/167 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP6) | [None] (DP6)
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | -
ULP7 | DC bus voltage | 16#1C6D = 7277 | 16#202A/4E | 16#85/01/4E = 133/01/78 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP7) | [None] (DP7)
LCP7 | Motor current | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP7) | [None] (DP7)
RFP7 | Output frequency | 16#1C59 = 7257 | 16#202A/3A | 16#85/01/3A = 133/01/58 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP7) | [None] (DP7)
THP7 | Motor thermal state | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP7) | [None] (DP7)
EP7 | State word | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP7) | [None] (DP7)
IP7 | ETI state word | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP7) | [None] (DP7)
CMP7 | Cmd word | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP7) | [None] (DP7)
DCC7 | Command channel | 16#FB33 = 64307 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC7) | [None] (DP7)
DRC7 | Channel for reference frequency | 16#FB3D = 64317 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC7) | [None] (DP7)
CRP7 | Active channels on fault n-7 | 16#1C81 = 7297 | 16#202A/62 | 16#85/01/62 = 133/01/98 |  | History parameters | R | WORD (BitString16) | -
RTP7 | Run Elapsed time | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP7) | [None] (DP7)
OTP7 | Motor torque | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP7) | [None] (DP7)
TDP7 | Drive thermal state | 16#1CB3 = 7347 | 16#202B/30 | 16#85/01/94 = 133/01/148 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP7) | [None] (DP7)
TJP7 | IGBT junction temp | 16#1CBD = 7357 | 16#202B/3A | 16#85/01/9E = 133/01/158 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP7) | [None] (DP7)
SFP7 | Switching frequency | 16#1CC7 = 7367 | 16#202B/44 | 16#85/01/A8 = 133/01/168 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP7) | [None] (DP7)
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | -
ULP8 | DC bus voltage | 16#1C6E = 7278 | 16#202A/4F | 16#85/01/4F = 133/01/79 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP8) | [None] (DP8)
LCP8 | Motor current | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP8) | [None] (DP8)
RFP8 | Output frequency | 16#1C5A = 7258 | 16#202A/3B | 16#85/01/3B = 133/01/59 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP8) | [None] (DP8)
THP8 | Motor thermal state | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP8) | [None] (DP8)
EP8 | State word | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP8) | [None] (DP8)
IP8 | ETI state word | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP8) | [None] (DP8)
CMP8 | Cmd word | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP8) | [None] (DP8)
DCC8 | Command channel | 16#FB34 = 64308 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC8) | [None] (DP8)
DRC8 | Channel for reference frequency | 16#FB3E = 64318 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC8) | [None] (DP8)
CRP8 | Active channels on fault n-8 | 16#1C82 = 7298 | 16#202A/63 | 16#85/01/63 = 133/01/99 |  | History parameters | R | WORD (BitString16) | -
RTP8 | Run Elapsed time | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP8) | [None] (DP8)
OTP8 | Motor torque | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP8) | [None] (DP8)
TDP8 | Drive thermal state | 16#1CB4 = 7348 | 16#202B/31 | 16#85/01/95 = 133/01/149 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP8) | [None] (DP8)
TJP8 | IGBT junction temp | 16#1CBE = 7358 | 16#202B/3B | 16#85/01/9F = 133/01/159 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP8) | [None] (DP8)
SFP8 | Switching frequency | 16#1CC8 = 7368 | 16#202B/45 | 16#85/01/A9 = 133/01/169 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP8) | [None] (DP8)
NCV | Drive nominal rating | 16#0BC3 = 3011 | 16#2000/C | 16#70/01/0C = 112/01/12 | NCV | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] NO
VCAL | Drive mains voltage | 16#0BC4 = 3012 | 16#2000/D | 16#70/01/0D = 112/01/13 | VCAL | Identification parameters | R | WORD (Enumeration) | - | [Unkown voltage] NO
INV | Nominal Drive current | 16#0BC9 = 3017 | 16#2000/12 | 16#70/01/12 = 112/01/18 |  | Identification parameters | R | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535
VDP | Device software version | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
PAN0 | Device name (char 1 and 2) | 16#0D0C = 3340 | 16#2003/29 | 16#71/01/8D = 113/01/141 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN1 | Device name (char 3 and 4) | 16#0D0D = 3341 | 16#2003/2A | 16#71/01/8E = 113/01/142 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN2 | Device name (char 5 and 6) | 16#0D0E = 3342 | 16#2003/2B | 16#71/01/8F = 113/01/143 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN3 | Device name (char 7 and 8) | 16#0D0F = 3343 | 16#2003/2C | 16#71/01/90 = 113/01/144 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN4 | Device name (char 9 and 10) | 16#0D10 = 3344 | 16#2003/2D | 16#71/01/91 = 113/01/145 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN5 | Device name (char 11 and 12) | 16#0D11 = 3345 | 16#2003/2E | 16#71/01/92 = 113/01/146 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN6 | Device name (char 13 and 14) | 16#0D12 = 3346 | 16#2003/2F | 16#71/01/93 = 113/01/147 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN7 | Device name (char 15 and 16) | 16#0D13 = 3347 | 16#2003/30 | 16#71/01/94 = 113/01/148 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PWRC | MCE : Configure the number rectifier brick b0-b11 for 12 rectifier bricks | 16#99E9 = 39401 |  |  |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
BAFC | AFE : Configure the number AFE brick b0-b11 for 12 bricks | 16#9A4C = 39500 |  |  |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
BBUC | BU : Configure the number BU brick b0-b11 for 12 bricks | 16#9AB0 = 39600 |  |  |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NC1 | Com scan output 1 value | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (NC1) | [Com scan output map] (OSA)
NC2 | Com scan output 2 value | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (NC2) | [Com scan output map] (OSA)
NC3 | Com scan output 3 value | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (NC3) | [Com scan output map] (OSA)
NC4 | Com scan output 4 value | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (NC4) | [Com scan output map] (OSA)
NC5 | Com scan output 5 value | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (NC5) | [Com scan output map] (OSA)
NC6 | Com scan output 6 value | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (NC6) | [Com scan output map] (OSA)
NC7 | Com scan output 7 value | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (NC7) | [Com scan output map] (OSA)
NC8 | Com scan output 8 value | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (NC8) | [Com scan output map] (OSA)
NM1 | Com scan input 1 value | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (NM1) | [Com. scanner input map] (ISA)
NM2 | Com scan input 2 value | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (NM2) | [Com. scanner input map] (ISA)
NM3 | Com scan input 3 value | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (NM3) | [Com. scanner input map] (ISA)
NM4 | Com scan input 4 value | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (NM4) | [Com. scanner input map] (ISA)
NM5 | Com scan input 5 value | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (NM5) | [Com. scanner input map] (ISA)
NM6 | Com scan input 6 value | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (NM6) | [Com. scanner input map] (ISA)
NM7 | Com scan input 7 value | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (NM7) | [Com. scanner input map] (ISA)
NM8 | Com scan input 8 value | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (NM8) | [Com. scanner input map] (ISA)
SMAL | Velocity max amount | 16#21A1 = 8609 | 16#2038/A | 16#8C/01/0A = 140/01/10 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 0 rpm ... 65535 rpm
SMIL | Velocity min amount | 16#219F = 8607 | 16#2038/8 | 16#8C/01/08 = 140/01/08 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 0 rpm ... 65535 rpm
SPAL | Acceleration delta speed | 16#21A3 = 8611 | 16#2038/C | 16#8C/01/0C = 140/01/12 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 1 rpm ... 4294967295 rpm
SPAT | Acceleration delta time | 16#21A5 = 8613 | 16#2038/E | 16#8C/01/0E = 140/01/14 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s
SPDL | Deceleration delta speed | 16#21A6 = 8614 | 16#2038/F | 16#8C/01/0F = 140/01/15 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 1 rpm ... 4294967295 rpm
SPFN | Setpoint factor numerator | 16#21C2 = 8642 | 16#2038/2B | 16#8C/01/2B = 140/01/43 |  | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767
SPFD | Setpoint factor denominator | 16#21C3 = 8643 | 16#2038/2C | 16#8C/01/2C = 140/01/44 |  | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767
DOTD | Type of switchOn Disable Stop | 16#21CC = 8652 | 16#2038/35 | 16#8C/01/35 = 140/01/53 | DOTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [SwitchOnDisable Stp] (DOTD) | [Stop configuration] (STT)
QSTD | Quick stop option code | 16#21CB = 8651 | 16#2038/34 | 16#8C/01/34 = 140/01/52 | QSTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Fast stop then disable voltage] FST2
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 |  | Configuration management | R/WS | WORD (BitString16) | - | BIT1
CHA1 | Parameter set sel 1 | 16#3266 = 12902 | 16#2063/3 | 16#A1/01/67 = 161/01/103 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Parameter sets] (CHA1) | [Parameters switching] (MLP)
CHA2 | Parameter set sel 2 | 16#3267 = 12903 | 16#2063/4 | 16#A1/01/68 = 161/01/104 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Parameter sets] (CHA2) | [Parameters switching] (MLP)
CFPS | Used parameter set | 16#3264 = 12900 | 16#2063/1 | 16#A1/01/65 = 161/01/101 | CFPS | Parameter set switching | R | WORD (Enumeration) | - |  |  | [Used param. set] (CFPS) | [Drive parameters] (MPI)
VAL | Load parameter set command | 16#3265 = 12901 | 16#2063/2 | 16#A1/01/66 = 161/01/102 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 1
AD01 | Parameter set address 1 | 16#326F = 12911 | 16#2063/C | 16#A1/01/70 = 161/01/112 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD02 | Parameter set address 2 | 16#3270 = 12912 | 16#2063/D | 16#A1/01/71 = 161/01/113 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD03 | Parameter set address 3 | 16#3271 = 12913 | 16#2063/E | 16#A1/01/72 = 161/01/114 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD04 | Parameter set address 4 | 16#3272 = 12914 | 16#2063/F | 16#A1/01/73 = 161/01/115 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD05 | Parameter set address 5 | 16#3273 = 12915 | 16#2063/10 | 16#A1/01/74 = 161/01/116 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD06 | Parameter set address 6 | 16#3274 = 12916 | 16#2063/11 | 16#A1/01/75 = 161/01/117 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD07 | Parameter set address 7 | 16#3275 = 12917 | 16#2063/12 | 16#A1/01/76 = 161/01/118 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD08 | Parameter set address 8 | 16#3276 = 12918 | 16#2063/13 | 16#A1/01/77 = 161/01/119 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD09 | Parameter set address 9 | 16#3277 = 12919 | 16#2063/14 | 16#A1/01/78 = 161/01/120 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD10 | Parameter set address 10 | 16#3278 = 12920 | 16#2063/15 | 16#A1/01/79 = 161/01/121 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD11 | Parameter set address 11 | 16#3279 = 12921 | 16#2063/16 | 16#A1/01/7A = 161/01/122 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD12 | Parameter set address 12 | 16#327A = 12922 | 16#2063/17 | 16#A1/01/7B = 161/01/123 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD13 | Parameter set address 13 | 16#327B = 12923 | 16#2063/18 | 16#A1/01/7C = 161/01/124 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD14 | Parameter set address 14 | 16#327C = 12924 | 16#2063/19 | 16#A1/01/7D = 161/01/125 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD15 | Parameter set address 15 | 16#327D = 12925 | 16#2063/1A | 16#A1/01/7E = 161/01/126 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
S101 | Parameter set 1 value 1 | 16#3283 = 12931 | 16#2063/20 | 16#A1/01/84 = 161/01/132 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 1] (S101) | [Set 1] (PS1)
S102 | Parameter set 1 value 2 | 16#3284 = 12932 | 16#2063/21 | 16#A1/01/85 = 161/01/133 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 2] (S102) | [Set 1] (PS1)
S103 | Parameter set 1 value 3 | 16#3285 = 12933 | 16#2063/22 | 16#A1/01/86 = 161/01/134 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 3] (S103) | [Set 1] (PS1)
S104 | Parameter set 1 value 4 | 16#3286 = 12934 | 16#2063/23 | 16#A1/01/87 = 161/01/135 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 4] (S104) | [Set 1] (PS1)
S105 | Parameter set 1 value 5 | 16#3287 = 12935 | 16#2063/24 | 16#A1/01/88 = 161/01/136 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 5] (S105) | [Set 1] (PS1)
S106 | Parameter set 1 value 6 | 16#3288 = 12936 | 16#2063/25 | 16#A1/01/89 = 161/01/137 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 6] (S106) | [Set 1] (PS1)
S107 | Parameter set 1 value 7 | 16#3289 = 12937 | 16#2063/26 | 16#A1/01/8A = 161/01/138 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 7] (S107) | [Set 1] (PS1)
S108 | Parameter set 1 value 8 | 16#328A = 12938 | 16#2063/27 | 16#A1/01/8B = 161/01/139 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 8] (S108) | [Set 1] (PS1)
S109 | Parameter set 1 value 9 | 16#328B = 12939 | 16#2063/28 | 16#A1/01/8C = 161/01/140 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 9] (S109) | [Set 1] (PS1)
S110 | Parameter set 1 value 10 | 16#328C = 12940 | 16#2063/29 | 16#A1/01/8D = 161/01/141 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 10] (S110) | [Set 1] (PS1)
S111 | Parameter set 1 value 11 | 16#328D = 12941 | 16#2063/2A | 16#A1/01/8E = 161/01/142 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 11] (S111) | [Set 1] (PS1)
S112 | Parameter set 1 value 12 | 16#328E = 12942 | 16#2063/2B | 16#A1/01/8F = 161/01/143 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 12] (S112) | [Set 1] (PS1)
S113 | Parameter set 1 value 13 | 16#328F = 12943 | 16#2063/2C | 16#A1/01/90 = 161/01/144 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 13] (S113) | [Set 1] (PS1)
S114 | Parameter set 1 value 14 | 16#3290 = 12944 | 16#2063/2D | 16#A1/01/91 = 161/01/145 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 14] (S114) | [Set 1] (PS1)
S115 | Parameter set 1 value 15 | 16#3291 = 12945 | 16#2063/2E | 16#A1/01/92 = 161/01/146 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 1 Value 15] (S115) | [Set 1] (PS1)
S201 | Parameter set 2 value 1 | 16#3297 = 12951 | 16#2063/34 | 16#A1/01/98 = 161/01/152 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 1] (S201) | [Set 2] (PS2)
S202 | Parameter set 2 value 2 | 16#3298 = 12952 | 16#2063/35 | 16#A1/01/99 = 161/01/153 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 2] (S202) | [Set 2] (PS2)
S203 | Parameter set 2 value 3 | 16#3299 = 12953 | 16#2063/36 | 16#A1/01/9A = 161/01/154 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 3] (S203) | [Set 2] (PS2)
S204 | Parameter set 2 value 4 | 16#329A = 12954 | 16#2063/37 | 16#A1/01/9B = 161/01/155 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 4] (S204) | [Set 2] (PS2)
S205 | Parameter set 2 value 5 | 16#329B = 12955 | 16#2063/38 | 16#A1/01/9C = 161/01/156 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 5] (S205) | [Set 2] (PS2)
S206 | Parameter set 2 value 6 | 16#329C = 12956 | 16#2063/39 | 16#A1/01/9D = 161/01/157 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 6] (S206) | [Set 2] (PS2)
S207 | Parameter set 2 value 7 | 16#329D = 12957 | 16#2063/3A | 16#A1/01/9E = 161/01/158 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 7] (S207) | [Set 2] (PS2)
S208 | Parameter set 2 value 8 | 16#329E = 12958 | 16#2063/3B | 16#A1/01/9F = 161/01/159 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 8] (S208) | [Set 2] (PS2)
S209 | Parameter set 2 value 9 | 16#329F = 12959 | 16#2063/3C | 16#A1/01/A0 = 161/01/160 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 9] (S209) | [Set 2] (PS2)
S210 | Parameter set 2 value 10 | 16#32A0 = 12960 | 16#2063/3D | 16#A1/01/A1 = 161/01/161 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 10] (S210) | [Set 2] (PS2)
S211 | Parameter set 2 value 11 | 16#32A1 = 12961 | 16#2063/3E | 16#A1/01/A2 = 161/01/162 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 11] (S211) | [Set 2] (PS2)
S212 | Parameter set 2 value 12 | 16#32A2 = 12962 | 16#2063/3F | 16#A1/01/A3 = 161/01/163 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 12] (S212) | [Set 2] (PS2)
S213 | Parameter set 2 value 13 | 16#32A3 = 12963 | 16#2063/40 | 16#A1/01/A4 = 161/01/164 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 13] (S213) | [Set 2] (PS2)
S214 | Parameter set 2 value 14 | 16#32A4 = 12964 | 16#2063/41 | 16#A1/01/A5 = 161/01/165 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 14] (S214) | [Set 2] (PS2)
S215 | Parameter set 2 value 15 | 16#32A5 = 12965 | 16#2063/42 | 16#A1/01/A6 = 161/01/166 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 2 Value 15] (S215) | [Set 2] (PS2)
S301 | Parameter set 3 value 1 | 16#32AB = 12971 | 16#2063/48 | 16#A1/01/AC = 161/01/172 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 1] (S301) | [Set 3] (PS3)
S302 | Parameter set 3 value 2 | 16#32AC = 12972 | 16#2063/49 | 16#A1/01/AD = 161/01/173 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 2] (S302) | [Set 3] (PS3)
S303 | Parameter set 3 value 3 | 16#32AD = 12973 | 16#2063/4A | 16#A1/01/AE = 161/01/174 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 3] (S303) | [Set 3] (PS3)
S304 | Parameter set 3 value 4 | 16#32AE = 12974 | 16#2063/4B | 16#A1/01/AF = 161/01/175 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 4] (S304) | [Set 3] (PS3)
S305 | Parameter set 3 value 5 | 16#32AF = 12975 | 16#2063/4C | 16#A1/01/B0 = 161/01/176 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 5] (S305) | [Set 3] (PS3)
S306 | Parameter set 3 value 6 | 16#32B0 = 12976 | 16#2063/4D | 16#A1/01/B1 = 161/01/177 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 6] (S306) | [Set 3] (PS3)
S307 | Parameter set 3 value 7 | 16#32B1 = 12977 | 16#2063/4E | 16#A1/01/B2 = 161/01/178 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 7] (S307) | [Set 3] (PS3)
S308 | Parameter set 3 value 8 | 16#32B2 = 12978 | 16#2063/4F | 16#A1/01/B3 = 161/01/179 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 8] (S308) | [Set 3] (PS3)
S309 | Parameter set 3 value 9 | 16#32B3 = 12979 | 16#2063/50 | 16#A1/01/B4 = 161/01/180 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 9] (S309) | [Set 3] (PS3)
S310 | Parameter set 3 value 10 | 16#32B4 = 12980 | 16#2063/51 | 16#A1/01/B5 = 161/01/181 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 10] (S310) | [Set 3] (PS3)
S311 | Parameter set 3 value 11 | 16#32B5 = 12981 | 16#2063/52 | 16#A1/01/B6 = 161/01/182 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 11] (S311) | [Set 3] (PS3)
S312 | Parameter set 3 value 12 | 16#32B6 = 12982 | 16#2063/53 | 16#A1/01/B7 = 161/01/183 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 12] (S312) | [Set 3] (PS3)
S313 | Parameter set 3 value 13 | 16#32B7 = 12983 | 16#2063/54 | 16#A1/01/B8 = 161/01/184 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 13] (S313) | [Set 3] (PS3)
S314 | Parameter set 3 value 14 | 16#32B8 = 12984 | 16#2063/55 | 16#A1/01/B9 = 161/01/185 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 14] (S314) | [Set 3] (PS3)
S315 | Parameter set 3 value 15 | 16#32B9 = 12985 | 16#2063/56 | 16#A1/01/BA = 161/01/186 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter Set 3 Value 15] (S315) | [Set 3] (PS3)
LSP | Low speed | 16#0C21 = 3105 | 16#2001/6 | 16#70/01/6A = 112/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Low Speed] (LSP) | [Simply start] (SIM) [Speed Limits] (SLM) [Settings] (SET)
HSP | High speed | 16#0C20 = 3104 | 16#2001/5 | 16#70/01/69 = 112/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High Speed] (HSP) | [Simply start] (SIM) [Speed Limits] (SLM) [High Speed Switching] (CHS) [Settings] (SET)
HSP2 | High speed 2 | 16#3B06 = 15110 | 16#2079/B | 16#AC/01/6F = 172/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 2] (HSP2) | [High Speed Switching] (CHS) [Settings] (SET)
HSP3 | High speed 3 | 16#3B07 = 15111 | 16#2079/C | 16#AC/01/70 = 172/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 3] (HSP3) | [High Speed Switching] (CHS) [Settings] (SET)
HSP4 | High speed 4 | 16#3B08 = 15112 | 16#2079/D | 16#AC/01/71 = 172/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 4] (HSP4) | [High Speed Switching] (CHS) [Settings] (SET)
SH2 | 2 high speed assign. | 16#3AFD = 15101 | 16#2079/2 | 16#AC/01/66 = 172/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 High speed] (SH2) | [High Speed Switching] (CHS)
SH4 | 4 high speed assign. | 16#3AFE = 15102 | 16#2079/3 | 16#AC/01/67 = 172/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [4 High speed] (SH4) | [High Speed Switching] (CHS)
ITH | Motor Thermal current | 16#2596 = 9622 | 16#2042/17 | 16#91/01/17 = 145/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Motor Th Current] (ITH) | [Simply start] (SIM) [Motor monitoring] (MOP) [Settings] (SET) [Motor thermal monit] (THT)
SPGU | Inertia factor | 16#259D = 9629 | 16#2042/1E | 16#91/01/1E = 145/01/30 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Inertia Factor] (SPGU) | [Motor control] (DRC) [Settings] (SET)
SPG | Speed proportional gain | 16#238F = 9103 | 16#203D/4 | 16#8E/01/68 = 142/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Speed prop. gain] (SPG) | [Spd Loop Optimization] (MCL) [Settings] (SET)
SIT | Speed time integral | 16#2390 = 9104 | 16#203D/5 | 16#8E/01/69 = 142/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | Refer to programming manual | 1 ms ... 65535 ms | [Speed time integral] (SIT) | [Spd Loop Optimization] (MCL) [Settings] (SET)
SFC | K speed loop filter | 16#2391 = 9105 | 16#203D/6 | 16#8E/01/6A = 142/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 100 | [K speed loop filter] (SFC) | [Spd Loop Optimization] (MCL) [Settings] (SET)
JACO | Inertia Coefficient of the application | 16#2398 = 9112 | 16#203D/D | 16#8E/01/71 = 142/01/113 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | 1.00 | 0.10 ... 100.00 | [App. Inertia Coef.] (JACO) | [Spd Loop Optimization] (MCL)
SSL | Speed loop type | 16#2392 = 9106 | 16#203D/7 | 16#8E/01/6B = 142/01/107 | SSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] STD |  | [Speed loop type] (SSL) | [Spd Loop Optimization] (MCL)
JEST | Estimated application inertia | 16#2393 = 9107 | 16#203D/8 | 16#8E/01/6C = 142/01/108 |  | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Estim. app. inertia] (JEST) | [Spd Loop Optimization] (MCL)
JAPL | Application Inertia | 16#2394 = 9108 | 16#203D/9 | 16#8E/01/6D = 142/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Application Inertia] (JAPL) | [Spd Loop Optimization] (MCL)
JMUL | Inertia Multiplying Coefficient | 16#2395 = 9109 | 16#203D/A | 16#8E/01/6E = 142/01/110 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 g.m² |  | 0.0 g.m² ... 6553.5 g.m² | [Inertia Mult. Coef.] (JMUL) | [Spd Loop Optimization] (MCL)
FFP | Feed forward value | 16#2396 = 9110 | 16#203D/B | 16#8E/01/6F = 142/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 200 % | [Feed forward] (FFP) | [Spd Loop Optimization] (MCL)
FFV | Feed forward bandwidth | 16#2397 = 9111 | 16#203D/C | 16#8E/01/70 = 142/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 20 % ... 500 % | [FeedFwd Bandwidth] (FFV) | [Spd Loop Optimization] (MCL)
FFH | Filter time of the estimated speed | 16#239B = 9115 | 16#203D/10 | 16#8E/01/74 = 142/01/116 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | Refer to programming manual | 0.0 ms ... 100.0 ms | [Spd est. filter time] (FFH) | [Spd Loop Optimization] (MCL)
CRTF | Filter time of the current | 16#239C = 9116 | 16#203D/11 | 16#8E/01/75 = 142/01/117 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 0.0 ms | 0.0 ms ... 100.0 ms | [Current Filter Time] (CRTF) | [data] (MTD)
NFA | Notch Filter Activation | 16#23A0 = 9120 | 16#203D/15 | 16#8E/01/79 = 142/01/121 | NFL | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Notch Filter Activation] (NFA) | [Spd Loop Optimization] (MCL)
NFF1 | Notch Filter 1 - frequency | 16#23A1 = 9121 | 16#203D/16 | 16#8E/01/7A = 142/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 10.0 Hz ... 150.0 Hz | [Notch Filter Freq 1] (NFF1) | [Spd Loop Optimization] (MCL)
NFB1 | Notch Filter 1 - Bandwidth | 16#23A2 = 9122 | 16#203D/17 | 16#8E/01/7B = 142/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 10 % ... 400 % | [Notch Filter Bdw 1] (NFB1) | [Spd Loop Optimization] (MCL)
NFD1 | Notch Filter 1 - Depth | 16#23A3 = 9123 | 16#203D/18 | 16#8E/01/7C = 142/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 99 % | [Notch Filter Depth 1] (NFD1) | [Spd Loop Optimization] (MCL)
NFF2 | Notch Filter 2 - frequency | 16#23A4 = 9124 | 16#203D/19 | 16#8E/01/7D = 142/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 85.0 Hz | 10.0 Hz ... 150.0 Hz | [Notch Filter Freq 2] (NFF2) | [Spd Loop Optimization] (MCL)
NFB2 | Notch Filter 2 - Bandwidth | 16#23A5 = 9125 | 16#203D/1A | 16#8E/01/7E = 142/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 10 % ... 400 % | [Notch Filter Bdw 2] (NFB2) | [Spd Loop Optimization] (MCL)
NFD2 | Notch Filter 2 - Depth | 16#23A6 = 9126 | 16#203D/1B | 16#8E/01/7F = 142/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 25 % | 0 % ... 99 % | [Notch Filter Depth 2] (NFD2) | [Spd Loop Optimization] (MCL)
CTD | High current threshold | 16#2AF9 = 11001 | 16#2050/2 | 16#98/01/02 = 152/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [High Current Thd] (CTD) | [Threshold reached] (THRE) [Settings] (SET)
TTH | High torque threshold | 16#2B08 = 11016 | 16#2050/11 | 16#98/01/11 = 152/01/17 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | -300 % ... 300 % | [High torque thd.] (TTH) | [Threshold reached] (THRE) [Settings] (SET)
TTL | Low torque threshold | 16#2B07 = 11015 | 16#2050/10 | 16#98/01/10 = 152/01/16 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 50 % | -300 % ... 300 % | [Low torque thd.] (TTL) | [Threshold reached] (THRE) [Settings] (SET)
FQL | Pulse warning threshold | 16#3911 = 14609 | 16#2074/A | 16#AA/01/0A = 170/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 30000 Hz | [Pulse warning thd.] (FQL) | [Frequency meter] (FQF)
FTD | Motor frequency threshold | 16#2AFB = 11003 | 16#2050/4 | 16#98/01/04 = 152/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Motor Freq Thd] (FTD) | [Threshold reached] (THRE) [Settings] (SET)
F2D | Frequency threshold 2 | 16#2AFC = 11004 | 16#2050/5 | 16#98/01/05 = 152/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Freq. threshold 2] (F2D) | [Threshold reached] (THRE) [Settings] (SET)
JF2 | Skip frequency 2 | 16#2C26 = 11302 | 16#2053/3 | 16#99/01/67 = 153/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency 2] (JF2) | [Jump frequency] (JUF) [Settings] (SET)
JPF | Skip frequency | 16#2C25 = 11301 | 16#2053/2 | 16#99/01/66 = 153/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency] (JPF) | [Jump frequency] (JUF) [Settings] (SET)
JFH | Skip Freq. hysteresis | 16#2C2F = 11311 | 16#2053/C | 16#99/01/70 = 153/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.1 Hz ... 10.0 Hz | [Skip Freq.Hysteresis] (JFH) | [Jump frequency] (JUF) [Settings] (SET)
JF3 | 3rd Skip frequency | 16#2C27 = 11303 | 16#2053/4 | 16#99/01/68 = 153/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [3rd Skip Frequency] (JF3) | [Jump frequency] (JUF) [Settings] (SET)
BFR | Motor Standard | 16#0BC7 = 3015 | 16#2000/10 | 16#70/01/10 = 112/01/16 | BFR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Motor Standard] (BFR) | [Simply start] (SIM) [data] (MTD)
NPR | Nominal motor power | 16#258D = 9613 | 16#2042/E | 16#91/01/0E = 145/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Nominal Motor Power] (NPR) | [Simply start] (SIM) [data] (MTD)
COS | Motor 1 Cosinus Phi | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | Refer to programming manual | 0.50 ... 1.00 | [Motor 1 Cosinus Phi] (COS) | [Simply start] (SIM) [data] (MTD)
UNS | Nominal motor voltage | 16#2581 = 9601 | 16#2042/2 | 16#91/01/02 = 145/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 690 V | [Nom Motor Voltage] (UNS) | [Simply start] (SIM) [data] (MTD)
NCR | Nominal motor current | 16#2583 = 9603 | 16#2042/4 | 16#91/01/04 = 145/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Nom Motor Current] (NCR) | [Simply start] (SIM) [data] (MTD)
FRS | Nominal motor frequency | 16#2582 = 9602 | 16#2042/3 | 16#91/01/03 = 145/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 599.0 Hz | [Nominal Motor Freq] (FRS) | [Simply start] (SIM) [data] (MTD)
NSP | Nominal motor speed | 16#2584 = 9604 | 16#2042/5 | 16#91/01/05 = 145/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nominal Motor Speed] (NSP) | [Simply start] (SIM) [data] (MTD)
TFR | Max frequency | 16#0C1F = 3103 | 16#2001/4 | 16#70/01/68 = 112/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 599.0 Hz | [Max Frequency] (TFR) | [Simply start] (SIM) [data] (MTD)
TUN | Autotuning | 16#2588 = 9608 | 16#2042/9 | 16#91/01/09 = 145/01/09 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] NO |  | [Autotuning] (TUN) | [Simply start] (SIM) [Motor tune] (MTU)
TUNR | Rotation tune enable | 16#2668 = 9832 | 16#2044/21 | 16#92/01/21 = 146/01/33 | ACTION | Configuration and settings | R/WS | WORD (Enumeration) | - | [No action] NO |  | [Rotation Tune Enable] (TUNR) | [Rotation Tune] (TRAM)
IDL1 | First Id min current level in rotation | 16#266C = 9836 | 16#2044/25 | 16#92/01/25 = 146/01/37 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 300 % | [1st Id min current] (IDL1) | [Rotation Tune] (TRAM)
IDH1 | First Id max current level in rotation | 16#266D = 9837 | 16#2044/26 | 16#92/01/26 = 146/01/38 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 300 % | [1st Id max current] (IDH1) | [Rotation Tune] (TRAM)
IDL2 | Second Id min current level in rotation | 16#266E = 9838 | 16#2044/27 | 16#92/01/27 = 146/01/39 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 300 % | [2nd Id min current] (IDL2) | [Rotation Tune] (TRAM)
IDH2 | Second Id max current level in rotation | 16#266F = 9839 | 16#2044/28 | 16#92/01/28 = 146/01/40 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 120 % | 0 % ... 300 % | [2nd Id max current] (IDH2) | [Rotation Tune] (TRAM)
EFAP | Rotation tune type | 16#2670 = 9840 | 16#2044/29 | 16#92/01/29 = 146/01/41 | EFAP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] LINF1 |  | [Rotation Tune Type] (EFAP) | [Rotation Tune] (TRAM)
TNBR | Number of autotuning sequence repetitions | 16#2667 = 9831 | 16#2044/20 | 16#92/01/20 = 146/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 3 | [Nb Of Repetitions] (TNBR) | [Rotation Tune] (TRAM)
L0A | Tangential main inductance | 16#2671 = 9841 | 16#2044/2A | 16#92/01/2A = 146/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Tangential Main Inductance] (L0A) | [data] (MTD) [Rotation Tune] (TRAM)
ALFA | Flux saturation curve coefficient A | 16#2672 = 9842 | 16#2044/2B | 16#92/01/2B = 146/01/43 |  | Configuration and settings | R/WS | INT (Signed16) | 0.01 % | 0.00 % | -327.67 % ... 327.67 % | [Flux curve coeff A] (ALFA) | [data] (MTD) [Rotation Tune] (TRAM)
BET0 | Flux saturation curve coefficient B | 16#2673 = 9843 | 16#2044/2C | 16#92/01/2C = 146/01/44 |  | Configuration and settings | R/WS | INT (Signed16) | 0.01 % | 0.00 % | -327.67 % ... 327.67 % | [Flux curve coeff B] (BET0) | [data] (MTD) [Rotation Tune] (TRAM)
PHIA | Rotor nominal flux | 16#2674 = 9844 | 16#2044/2D | 16#92/01/2D = 146/01/45 |  | Actual values parameters | R | UINT (Unsigned16) | 0.01 Wb |  | 0.00 Wb ... 655.35 Wb | [Rotor Nominal Flux] (PHIA) | [data] (MTD) [Rotation Tune] (TRAM)
LA | Main inductance | 16#2675 = 9845 | 16#2044/2E | 16#92/01/2E = 146/01/46 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Main Inductance] (LA) | [data] (MTD) [Rotation Tune] (TRAM)
AUT | Automatic autotune | 16#258F = 9615 | 16#2042/10 | 16#91/01/10 = 145/01/16 | AUT | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Automatic autotune] (AUT) | [Motor tune] (MTU)
TUS | Autotuning status | 16#2589 = 9609 | 16#2042/A | 16#91/01/0A = 145/01/10 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Not done] TAB |  | [Autotuning Status] (TUS) | [Simply start] (SIM) [Motor tune] (MTU) [Rotation Tune] (TRAM)
TURS | Rotation tune status | 16#266A = 9834 | 16#2044/23 | 16#92/01/23 = 146/01/35 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Not done] TAB |  | [Rotation Tune Status] (TURS) | [Rotation Tune] (TRAM)
CTT | Motor control type | 16#2587 = 9607 | 16#2042/8 | 16#91/01/08 = 145/01/08 | CTT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Sensorless flux vector V] VVC |  | [Motor control type] (CTT) | [Motor parameters] (MPA)
U1 | Volt point 1 on 5pt V/F | 16#3073 = 12403 | 16#205E/4 | 16#9F/01/04 = 159/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U1] (U1) | [Motor control] (DRC)
F1 | Freq point 1on 5pt V/F | 16#3074 = 12404 | 16#205E/5 | 16#9F/01/05 = 159/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F1] (F1) | [Motor control] (DRC)
U2 | Volt point 2 on 5pt V/F | 16#3075 = 12405 | 16#205E/6 | 16#9F/01/06 = 159/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U2] (U2) | [Motor control] (DRC)
F2 | Freq point 2 on 5pt V/F | 16#3076 = 12406 | 16#205E/7 | 16#9F/01/07 = 159/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F2] (F2) | [Motor control] (DRC)
U3 | Volt point 3 on 5pt V/F | 16#3077 = 12407 | 16#205E/8 | 16#9F/01/08 = 159/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U3] (U3) | [Motor control] (DRC)
F3 | Freq point 3 on 5pt V/F | 16#3078 = 12408 | 16#205E/9 | 16#9F/01/09 = 159/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F3] (F3) | [Motor control] (DRC)
U4 | Volt point 4 on 5pt V/F | 16#3079 = 12409 | 16#205E/A | 16#9F/01/0A = 159/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U4] (U4) | [Motor control] (DRC)
F4 | Freq point 4 on 5pt V/F | 16#307A = 12410 | 16#205E/B | 16#9F/01/0B = 159/01/11 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F4] (F4) | [Motor control] (DRC)
U5 | Volt point 5 on 5pt V/F | 16#307B = 12411 | 16#205E/C | 16#9F/01/0C = 159/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U5] (U5) | [Motor control] (DRC)
F5 | Freq point 5 on 5pt V/F | 16#307C = 12412 | 16#205E/D | 16#9F/01/0D = 159/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F5] (F5) | [Motor control] (DRC)
NCRS | Sync motor nominal current | 16#25C6 = 9670 | 16#2042/47 | 16#91/01/47 = 145/01/71 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Sync Nominal I] (NCRS) | [data] (MTD)
NSPS | Nominal synchronous motor speed | 16#25C7 = 9671 | 16#2042/48 | 16#91/01/48 = 145/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nom SyncMotor Speed] (NSPS) | [data] (MTD)
PPNS | Pole pairs number (sync) | 16#25C8 = 9672 | 16#2042/49 | 16#91/01/49 = 145/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 240 | [Pole pairs] (PPNS) | [data] (MTD)
TQS | Nominal motor torque | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 1 ... 65535 | [Nom Motor torque] (TQS) | [data] (MTD)
PHS | Sync. EMF constant | 16#25C9 = 9673 | 16#2042/4A | 16#91/01/4A = 145/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mV/rpm | 0.0 mV/rpm | 0.0 mV/rpm ... 6553.5 mV/rpm | [Syn. EMF constant] (PHS) | [data] (MTD)
LDS | Sync motor d inductance | 16#25CA = 9674 | 16#2042/4B | 16#91/01/4B = 145/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Autotune L d-axis] (LDS) | [data] (MTD)
LQS | Sync motor q inductance | 16#25CB = 9675 | 16#2042/4C | 16#91/01/4C = 145/01/76 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Autotune L q-axis] (LQS) | [data] (MTD)
RSAS | Calculated SyncMotor Stator R | 16#25D2 = 9682 | 16#2042/53 | 16#91/01/53 = 145/01/83 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [SyncMotor Stator R] (RSAS) | [data] (MTD)
UFR | IR compensation | 16#2597 = 9623 | 16#2042/18 | 16#91/01/18 = 145/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [IR compensation] (UFR) | [Motor control] (DRC) [Settings] (SET)
SLP | Slip Compensation | 16#2599 = 9625 | 16#2042/1A | 16#91/01/1A = 145/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 300 % | [Slip compensation] (SLP) | [Motor control] (DRC) [Settings] (SET)
PPN | Number of pairs of poles calculated | 16#2592 = 9618 | 16#2042/13 | 16#91/01/13 = 145/01/19 |  | Configuration and settings | R | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 100
FLG | Frequency loop gain | 16#2594 = 9620 | 16#2042/15 | 16#91/01/15 = 145/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [FreqLoopGain] (FLG) | [Spd Loop Optimization] (MCL)
STA | Frequency loop stability | 16#2595 = 9621 | 16#2042/16 | 16#91/01/16 = 145/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [FreqLoop Stab] (STA) | [Spd Loop Optimization] (MCL)
RSA | AsyncMotor Stator resistance | 16#25AA = 9642 | 16#2042/2B | 16#91/01/2B = 145/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [AsyncMotor R Stator] (RSA) | [data] (MTD)
IDA | Magnetizing current | 16#25B4 = 9652 | 16#2042/35 | 16#91/01/35 = 145/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Magnetizing Current] (IDA) | [data] (MTD)
LFA | AsyncMotor Leakage inductance | 16#25BE = 9662 | 16#2042/3F | 16#91/01/3F = 145/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [AsyncMotor Lf Induct] (LFA) | [data] (MTD)
TRA | Rotor time constant | 16#25C3 = 9667 | 16#2042/44 | 16#91/01/44 = 145/01/68 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Rotor Time Const] (TRA) | [data] (MTD)
FRSS | Synchronous motor nominal freq | 16#25CF = 9679 | 16#2042/50 | 16#91/01/50 = 145/01/80 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 599.0 Hz | [Sync Nominal Freq] (FRSS) | [data] (MTD)
SFR | Switching frequency | 16#0C1E = 3102 | 16#2001/3 | 16#70/01/67 = 112/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 kHz | Refer to programming manual | 2.0 kHz ... 16.0 kHz | [Switching frequency] (SFR) | [Switching frequency] (SWF) [Settings] (SET)
CLI | Current limitation | 16#23F1 = 9201 | 16#203E/2 | 16#8F/01/02 = 143/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Current Limitation] (CLI) | [Motor monitoring] (MOP) [Settings] (SET) [2nd current limit.] (CLI)
SFT | Switching frequency type | 16#0C1D = 3101 | 16#2001/2 | 16#70/01/66 = 112/01/102 | SFT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Switch.frequency type 1] HF1 |  | [Switch Freq Type] (SFT) | [Switching frequency] (SWF)
NRD | Motor Noise Reduction | 16#0C23 = 3107 | 16#2001/8 | 16#70/01/6C = 112/01/108 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Noise Reduction] (NRD) | [Switching frequency] (SWF)
BOA | Boost activation | 16#3656 = 13910 | 16#206D/B | 16#A6/01/6F = 166/01/111 | BOA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Boost activation] (BOA) | [Motor control] (DRC)
SVL | Motor surge limitation | 16#3139 = 12601 | 16#2060/2 | 16#A0/01/02 = 160/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Motor surge limit.] (SVL) | [Switching frequency] (SWF)
SOP | Attenuation time | 16#313A = 12602 | 16#2060/3 | 16#A0/01/03 = 160/01/03 | SOP | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Attenuation Time] (SOP) | [Motor monitoring] (MOP) [Switching frequency] (SWF)
VBR | Braking level | 16#3715 = 14101 | 16#206F/2 | 16#A7/01/66 = 167/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 V | Refer to programming manual | 335 V ... 1130 V | [Braking level] (VBR) | [Motor control] (DRC)
BRO | Braking resistor monitoring | 16#371F = 14111 | 16#206F/C | 16#A7/01/70 = 167/01/112 | BRO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore monitoring] NO |  | [Braking Resistor Monit] (BRO) | [Braking Resistor monit] (BRP)
BRP | Braking resistor power | 16#3720 = 14112 | 16#206F/D | 16#A7/01/71 = 167/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 kW | 0.1 kW | 0.1 kW ... 3000.0 kW | [Braking Resistor Power] (BRP) | [Braking Resistor monit] (BRP)
BRV | Braking resistor value | 16#3721 = 14113 | 16#206F/E | 16#A7/01/72 = 167/01/114 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Ohm | 0.1 Ohm | 0.1 Ohm ... 200.0 Ohm | [Braking Resistor Value] (BRV) | [Braking Resistor monit] (BRP)
BRTC | Braking resistor time constant | 16#3723 = 14115 | 16#206F/10 | 16#A7/01/74 = 167/01/116 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | Refer to programming manual | 0 s ... 200 s | [Braking Resist T Constant] (BRTC) | [Braking Resistor monit] (BRP)
LBA | Load sharing | 16#37DD = 14301 | 16#2071/2 | 16#A8/01/66 = 168/01/102 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Load sharing] (LBA) | [Load Sharing] (LDS) [Load Sharing] (LDS) [Load Sharing M/S] (MSB)
LBC | Load correction | 16#37DE = 14302 | 16#2071/3 | 16#A8/01/67 = 168/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 1000.0 Hz | [Load correction] (LBC) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS) [Settings] (SET)
LBC1 | Correction min speed | 16#37DF = 14303 | 16#2071/4 | 16#A8/01/68 = 168/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 999.9 Hz | [Correction min spd] (LBC1) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
LBC2 | Correction max speed | 16#37E0 = 14304 | 16#2071/5 | 16#A8/01/69 = 168/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 1000.0 Hz | [Correction max spd] (LBC2) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
LBC3 | Torque offset | 16#37E1 = 14305 | 16#2071/6 | 16#A8/01/6A = 168/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Torque offset] (LBC3) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
LBF | Sharing filter | 16#37E2 = 14306 | 16#2071/7 | 16#A8/01/6B = 168/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 100 ms | 100 ms ... 20000 ms | [Sharing filter] (LBF) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
FFM | Fan mode | 16#0C3A = 3130 | 16#2001/1F | 16#70/01/83 = 112/01/131 | FFM | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard] STD |  | [Fan mode] (FFM) | [Settings] (SET) [Fan management] (FAMA)
TCC | 2/3-wire control | 16#2B5D = 11101 | 16#2051/2 | 16#98/01/66 = 152/01/102 | TCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [2-wire control] 2C |  | [2/3-Wire Control] (TCC) | [Simply start] (SIM) [Command and Reference] (CRP)
TCT | Type of 2-wire control | 16#2B5E = 11102 | 16#2051/3 | 16#98/01/67 = 152/01/103 | TCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Transition] TRN |  | [2-wire type] (TCT) | [Command and Reference] (CRP)
RRS | Reverse assignment | 16#2B61 = 11105 | 16#2051/6 | 16#98/01/6A = 152/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Reverse Assign] (RRS) | [Command and Reference] (CRP)
BSP | Reference frequency template selection | 16#0C22 = 3106 | 16#2001/7 | 16#70/01/6B = 112/01/107 | BSP | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard ref template] BSD |  | [Ref Freq template] (BSP) | [Speed Limits] (SLM) [Input/Output] (IO)
AI1T | Configuration of AI1 | 16#1132 = 4402 | 16#200E/3 | 16#77/01/03 = 119/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI1 Type] (AI1T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
UIL1 | AI1 voltage scaling parameter of 0% | 16#113C = 4412 | 16#200E/D | 16#77/01/0D = 119/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI1 Min. Value] (UIL1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
UIH1 | AI1 voltage scaling parameter of 100% | 16#1146 = 4422 | 16#200E/17 | 16#77/01/17 = 119/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI1 Max Value] (UIH1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [AI1] (AI1C) [AI1 configuration] (AI1)
AI1E | AI1 intermediate point X | 16#116E = 4462 | 16#200E/3F | 16#77/01/3F = 119/01/63 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 X Interm. Point] (AI1E) | [AI1 configuration] (AI1)
AI1S | AI1 intermediate point Y | 16#1178 = 4472 | 16#200E/49 | 16#77/01/49 = 119/01/73 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point Y] (AI1S) | [AI1 configuration] (AI1)
AI2T | Configuration of AI2 | 16#1133 = 4403 | 16#200E/4 | 16#77/01/04 = 119/01/04 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [AI bipolar volts selected] N10U |  | [AI2 Type] (AI2T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI2 Config.] (MSR2) [Torque Ref AI2 Config.] (MTR2) [AI2 configuration] (AI2)
UIL2 | AI2 voltage scaling parameter of 0% | 16#113D = 4413 | 16#200E/E | 16#77/01/0E = 119/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI2 Min. Value] (UIL2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [Speed Ref AI2 Config.] (MSR2) [Torque Ref AI2 Config.] (MTR2) [AI2 configuration] (AI2)
UIH2 | AI2 voltage scaling parameter of 100% | 16#1147 = 4423 | 16#200E/18 | 16#77/01/18 = 119/01/24 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI2 Max value] (UIH2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [Speed Ref AI2 Config.] (MSR2) [Torque Ref AI2 Config.] (MTR2) [AI2 configuration] (AI2)
AI2F | AI2 filter | 16#1165 = 4453 | 16#200E/36 | 16#77/01/36 = 119/01/54 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI2 filter] (AI2F) | [AI2] (AI2C) [AI2 configuration] (AI2)
AI2E | AI2 intermediate point X | 16#116F = 4463 | 16#200E/40 | 16#77/01/40 = 119/01/64 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 X Interm. Point] (AI2E) | [AI2 configuration] (AI2)
AI2S | AI2 intermediate point Y | 16#1179 = 4473 | 16#200E/4A | 16#77/01/4A = 119/01/74 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point Y] (AI2S) | [AI2 configuration] (AI2)
AI3T | Configuration of AI3 | 16#1134 = 4404 | 16#200E/5 | 16#77/01/05 = 119/01/05 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AI3 Type] (AI3T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
CRL3 | AI3 current scaling parameter of 0% | 16#1152 = 4434 | 16#200E/23 | 16#77/01/23 = 119/01/35 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI3 Min. Value] (CRL3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
CRH3 | AI3 current scaling parameter of 100% | 16#115C = 4444 | 16#200E/2D | 16#77/01/2D = 119/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI3 Max Value] (CRH3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
AI3F | AI3 filter | 16#1166 = 4454 | 16#200E/37 | 16#77/01/37 = 119/01/55 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI3 filter] (AI3F) | [AI3] (AI3C) [AI3 configuration] (AI3)
AI3E | AI3 intermediate point X | 16#1170 = 4464 | 16#200E/41 | 16#77/01/41 = 119/01/65 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 X Interm. point] (AI3E) | [AI3 configuration] (AI3)
AI3S | AI3 intermediate point Y | 16#117A = 4474 | 16#200E/4B | 16#77/01/4B = 119/01/75 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Y Interm. point] (AI3S) | [AI3 configuration] (AI3)
AO1 | AQ1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor frequency] OFR |  | [AQ1 assignment] (AO1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1T | AQ1 Type | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AQ1 Type] (AO1T) | [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
AOL1 | AQ1 min output value | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ1 min output] (AOL1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
AOH1 | AQ1 max output value | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ1 max output] (AOH1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
UOL1 | AQ1 minimum output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ1 min Output] (UOL1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
UOH1 | AQ1 maximum output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ1 max Output] (UOH1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
ASL1 | Scaling AQ1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 Min] (ASL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
ASH1 | Scaling AQ1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 Max] (ASH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1F | AQ1 filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ1 Filter] (AO1F) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
FR1 | Configuration reference frequency 1 | 16#20DD = 8413 | 16#2036/E | 16#8B/01/0E = 139/01/14 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 1 Config] (FR1) | [Command and Reference] (CRP) [PID Reference] (RF) [PID Reference] (RF)
RIN | Reverse direction disable | 16#0C24 = 3108 | 16#2001/9 | 16#70/01/6D = 112/01/109 | RIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Reverse Disable] (RIN) | [Command and Reference] (CRP) [Reverse disable] (REIN)
PST | Stop key enable | 16#FA02 = 64002 |  |  | PST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop key priority] YES |  | [Stop Key Enable] (PST) | [Command and Reference] (CRP)
CHCF | Control mode configuration | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Combined channel mode] SIM |  | [Control Mode] (CHCF) | [Command and Reference] (CRP)
CCS | Command switching | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Command channel 1] CD1 |  | [Command Switching] (CCS) | [Command and Reference] (CRP)
CD1 | Command channel 1 assign | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminal block] TER |  | [Cmd channel 1] (CD1) | [Command and Reference] (CRP)
CD2 | Command channel 2 assign | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus communication] MDB |  | [Cmd channel 2] (CD2) | [Command and Reference] (CRP)
RFC | Freq switching assignment | 16#20DB = 8411 | 16#2036/C | 16#8B/01/0C = 139/01/12 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Freq Switch Assign] (RFC) | [Command and Reference] (CRP)
FR2 | Configuration reference frequency 2 | 16#20DE = 8414 | 16#2036/F | 16#8B/01/0F = 139/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 2 Config] (FR2) | [Command and Reference] (CRP)
COP | Copy Ch.1-Ch.2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No copy] NO |  | [Copy Ch1-Ch2] (COP) | [Command and Reference] (CRP)
FN1 | F1 key assignment | 16#34BD = 13501 | 16#2069/2 | 16#A4/01/66 = 164/01/102 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F1 key assignment] (FN1) | [Functions key mgnt] (FKG)
FN2 | F2 key assignment | 16#34BE = 13502 | 16#2069/3 | 16#A4/01/67 = 164/01/103 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F2 key assignment] (FN2) | [Functions key mgnt] (FKG)
FN3 | F3 key assignment | 16#34BF = 13503 | 16#2069/4 | 16#A4/01/68 = 164/01/104 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F3 key assignment] (FN3) | [Functions key mgnt] (FKG)
FN4 | F4 key assignment | 16#34C0 = 13504 | 16#2069/5 | 16#A4/01/69 = 164/01/105 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F4 key assignment] (FN4) | [Functions key mgnt] (FKG)
BMP | HMI local/remote command | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] DIS |  | [HMI L/R cmd] (BMP) | [Command and Reference] (CRP)
RCB | Select switching (1 to 1B) | 16#20DC = 8412 | 16#2036/D | 16#8B/01/0D = 139/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Reference frequency channel 1] FR1 |  | [Ref 1B switching] (RCB) | [Command and Reference] (CRP)
FR1B | Configuration ref. 1B | 16#20DF = 8415 | 16#2036/10 | 16#8B/01/10 = 139/01/16 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref.1B channel] (FR1B) | [Command and Reference] (CRP)
SA2 | Summing input 2 | 16#2E19 = 11801 | 16#2058/2 | 16#9C/01/02 = 156/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Summing Input 2] (SA2) | [Ref. operations] (OAI)
SA3 | Summing input 3 | 16#2E1A = 11802 | 16#2058/3 | 16#9C/01/03 = 156/01/03 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Summing Input 3] (SA3) | [Ref. operations] (OAI)
DA2 | Subtract reference frequency 2 | 16#2E23 = 11811 | 16#2058/C | 16#9C/01/0C = 156/01/12 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 2] (DA2) | [Ref. operations] (OAI)
DA3 | Subtract reference frequency 3 | 16#2E24 = 11812 | 16#2058/D | 16#9C/01/0D = 156/01/13 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 3] (DA3) | [Ref. operations] (OAI)
MA2 | Reference frequency 2 multiply | 16#2E2D = 11821 | 16#2058/16 | 16#9C/01/16 = 156/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 2 Multiply] (MA2) | [Ref. operations] (OAI)
MA3 | Reference frequency 3 multiply | 16#2E2E = 11822 | 16#2058/17 | 16#9C/01/17 = 156/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 3 Multiply] (MA3) | [Ref. operations] (OAI)
RPT | Type of ramp | 16#232C = 9004 | 16#203C/5 | 16#8E/01/05 = 142/01/05 | RPT | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Ramp Type] (RPT) | [Ramp] (RAMP)
INR | Ramp increment | 16#233C = 9020 | 16#203C/15 | 16#8E/01/15 = 142/01/21 | INR | Configuration and settings | R/W | WORD (Enumeration) | - | [Tenths of seconds] 01 |  | [Ramp increment] (INR) | [Ramp] (RAMP) [Settings] (SET)
ACC | Acceleration ramp time | 16#2329 = 9001 | 16#203C/2 | 16#8E/01/02 = 142/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 9999 | [Acceleration] (ACC) | [Simply start] (SIM) [Ramp] (RAMP) [Settings] (SET)
DEC | Deceleration ramp time | 16#232A = 9002 | 16#203C/3 | 16#8E/01/03 = 142/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 9999 | [Deceleration] (DEC) | [Simply start] (SIM) [Ramp] (RAMP) [Settings] (SET)
TA1 | Start ACC ramp rounding | 16#232D = 9005 | 16#203C/6 | 16#8E/01/06 = 142/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 100 % | [Begin Acc round] (TA1) | [Ramp] (RAMP) [Settings] (SET)
TA2 | End ACC ramp rounding | 16#232E = 9006 | 16#203C/7 | 16#8E/01/07 = 142/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 100 % | [End Acc round] (TA2) | [Ramp] (RAMP) [Settings] (SET)
TA3 | Start DEC ramp rounding | 16#232F = 9007 | 16#203C/8 | 16#8E/01/08 = 142/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 100 % | [Begin Dec round] (TA3) | [Ramp] (RAMP) [Settings] (SET)
TA4 | End DEC ramp rounding | 16#2330 = 9008 | 16#203C/9 | 16#8E/01/09 = 142/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 100 % | [End Dec round] (TA4) | [Ramp] (RAMP) [Settings] (SET)
FRT | Ramp 2 frequency threshold | 16#2333 = 9011 | 16#203C/C | 16#8E/01/0C = 142/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Ramp 2 Thd] (FRT) | [Ramp switching] (RPT)
RPS | Ramp switching assignment | 16#2332 = 9010 | 16#203C/B | 16#8E/01/0B = 142/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ramp Switch Assign] (RPS) | [Ramp switching] (RPT)
AC2 | Acceleration 2 ramp time | 16#2334 = 9012 | 16#203C/D | 16#8E/01/0D = 142/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Acceleration 2] (AC2) | [Ramp switching] (RPT) [Settings] (SET) [+/- speed around ref] (SRE)
DE2 | Deceleration 2 | 16#2335 = 9013 | 16#203C/E | 16#8E/01/0E = 142/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Deceleration 2] (DE2) | [Ramp switching] (RPT) [Settings] (SET) [+/- speed around ref] (SRE)
BRA | Decel ramp adaptation | 16#232B = 9003 | 16#203C/4 | 16#8E/01/04 = 142/01/04 | BRA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Dec.Ramp Adapt] (BRA) | [Ramp] (RAMP)
BBA | Braking balance | 16#3716 = 14102 | 16#206F/3 | 16#A7/01/67 = 167/01/103 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Braking balance] (BBA) | [Ramp] (RAMP)
STT | Type of stop | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Type of stop] (STT) | [Stop configuration] (STT)
FFT | Freewheel stop threshold | 16#2BD4 = 11220 | 16#2052/15 | 16#99/01/15 = 153/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.2 Hz ... 599.0 Hz | [Freewheel stop Thd] (FFT) | [Stop configuration] (STT) [Settings] (SET)
NST | Freewheel stop | 16#2BC2 = 11202 | 16#2052/3 | 16#99/01/03 = 153/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Freewheel Stop] (NST) | [Stop configuration] (STT)
FST | Fast stop assignment | 16#2BC4 = 11204 | 16#2052/5 | 16#99/01/05 = 153/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fast Stop Assign] (FST) | [Stop configuration] (STT)
DCF | Fast Stop ramp Divider | 16#2BDE = 11230 | 16#2052/1F | 16#99/01/1F = 153/01/31 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 4 | 0 ... 10 | [Ramp Divider] (DCF) | [Stop configuration] (STT) [Settings] (SET)
DCI | DC injection assignment | 16#2BC3 = 11203 | 16#2052/4 | 16#99/01/04 = 153/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DC Injection Assign] (DCI) | [Stop configuration] (STT)
IDC | DC injection level 1 | 16#2BCA = 11210 | 16#2052/B | 16#99/01/0B = 153/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [DC Inj Level 1] (IDC) | [Stop configuration] (STT) [Settings] (SET)
TDI | DC injection time 1 | 16#2BCD = 11213 | 16#2052/E | 16#99/01/0E = 153/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 1] (TDI) | [Stop configuration] (STT) [Settings] (SET)
IDC2 | DC injection level 2 | 16#2BCC = 11212 | 16#2052/D | 16#99/01/0D = 153/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [DC Inj Level 2] (IDC2) | [Stop configuration] (STT) [Settings] (SET)
TDC | DC injection time 2 | 16#2BCB = 11211 | 16#2052/C | 16#99/01/0C = 153/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 2] (TDC) | [Stop configuration] (STT) [Settings] (SET)
ADC | Automatic DC injection | 16#28A1 = 10401 | 16#204A/2 | 16#95/01/02 = 149/01/02 | ADC | Configuration and settings | R/W | WORD (Enumeration) | - | [No DC injection] NO |  | [Auto DC Injection] (ADC) | [Auto DC injection] (ADC)
SDC1 | Auto DC injection level 1 | 16#28A3 = 10403 | 16#204A/4 | 16#95/01/04 = 149/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Auto DC inj Level 1] (SDC1) | [Auto DC injection] (ADC) [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
TDC1 | Auto DC injection time 1 | 16#28A2 = 10402 | 16#204A/3 | 16#95/01/03 = 149/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [Auto DC Inj Time 1] (TDC1) | [Auto DC injection] (ADC) [Settings] (SET)
SDC2 | Auto DC injection level 2 | 16#28A5 = 10405 | 16#204A/6 | 16#95/01/06 = 149/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Auto DC inj Level 2] (SDC2) | [Auto DC injection] (ADC) [Settings] (SET)
TDC2 | Auto DC injection time 2 | 16#28A4 = 10404 | 16#204A/5 | 16#95/01/05 = 149/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 30.0 s | [Auto DC Inj Time 2] (TDC2) | [Auto DC injection] (ADC) [Settings] (SET)
JOG | Jog assignment | 16#2B66 = 11110 | 16#2051/B | 16#98/01/6F = 152/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Jog Assign] (JOG) | [Jog] (JOG)
JGF | Jog frequency | 16#2B67 = 11111 | 16#2051/C | 16#98/01/70 = 152/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 10.0 Hz | [Jog Frequency] (JGF) | [Jog] (JOG) [Settings] (SET)
JGT | Jog delay | 16#2B68 = 11112 | 16#2051/D | 16#98/01/71 = 152/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 2.0 s | [Jog Delay] (JGT) | [Jog] (JOG) [Settings] (SET)
PS2 | 2 Preset Freq assignment | 16#2C89 = 11401 | 16#2054/2 | 16#9A/01/02 = 154/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 Preset Freq] (PS2) | [Preset speeds] (PSS)
PS4 | 4 Preset Freq assignment | 16#2C8A = 11402 | 16#2054/3 | 16#9A/01/03 = 154/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 Preset Freq] (PS4) | [Preset speeds] (PSS)
PS8 | 8 Preset Freq assignment | 16#2C8B = 11403 | 16#2054/4 | 16#9A/01/04 = 154/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [8 Preset Freq] (PS8) | [Preset speeds] (PSS)
PS16 | 16 Preset Freq assignment | 16#2C8C = 11404 | 16#2054/5 | 16#9A/01/05 = 154/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [16 Preset Freq] (PS16) | [Preset speeds] (PSS)
SP2 | Preset speed 2 | 16#2C92 = 11410 | 16#2054/B | 16#9A/01/0B = 154/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 2] (SP2) | [Preset speeds] (PSS) [Settings] (SET)
SP3 | Preset speed 3 | 16#2C93 = 11411 | 16#2054/C | 16#9A/01/0C = 154/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 3] (SP3) | [Preset speeds] (PSS) [Settings] (SET)
SP4 | Preset speed 4 | 16#2C94 = 11412 | 16#2054/D | 16#9A/01/0D = 154/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 4] (SP4) | [Preset speeds] (PSS) [Settings] (SET)
SP5 | Preset speed 5 | 16#2C95 = 11413 | 16#2054/E | 16#9A/01/0E = 154/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 5] (SP5) | [Preset speeds] (PSS) [Settings] (SET)
SP6 | Preset speed 6 | 16#2C96 = 11414 | 16#2054/F | 16#9A/01/0F = 154/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 30.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 6] (SP6) | [Preset speeds] (PSS) [Settings] (SET)
SP7 | Preset speed 7 | 16#2C97 = 11415 | 16#2054/10 | 16#9A/01/10 = 154/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 7] (SP7) | [Preset speeds] (PSS) [Settings] (SET)
SP8 | Preset speed 8 | 16#2C98 = 11416 | 16#2054/11 | 16#9A/01/11 = 154/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 8] (SP8) | [Preset speeds] (PSS) [Settings] (SET)
SP9 | Preset speed 9 | 16#2C99 = 11417 | 16#2054/12 | 16#9A/01/12 = 154/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 45.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 9] (SP9) | [Preset speeds] (PSS) [Settings] (SET)
SP10 | Preset speed 10 | 16#2C9A = 11418 | 16#2054/13 | 16#9A/01/13 = 154/01/19 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 50.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 10] (SP10) | [Preset speeds] (PSS) [Settings] (SET)
SP11 | Preset speed 11 | 16#2C9B = 11419 | 16#2054/14 | 16#9A/01/14 = 154/01/20 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 55.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 11] (SP11) | [Preset speeds] (PSS) [Settings] (SET)
SP12 | Preset speed 12 | 16#2C9C = 11420 | 16#2054/15 | 16#9A/01/15 = 154/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 12] (SP12) | [Preset speeds] (PSS) [Settings] (SET)
SP13 | Preset speed 13 | 16#2C9D = 11421 | 16#2054/16 | 16#9A/01/16 = 154/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 70.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 13] (SP13) | [Preset speeds] (PSS) [Settings] (SET)
SP14 | Preset speed 14 | 16#2C9E = 11422 | 16#2054/17 | 16#9A/01/17 = 154/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 80.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 14] (SP14) | [Preset speeds] (PSS) [Settings] (SET)
SP15 | Preset speed 15 | 16#2C9F = 11423 | 16#2054/18 | 16#9A/01/18 = 154/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 90.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 15] (SP15) | [Preset speeds] (PSS) [Settings] (SET)
SP16 | Preset speed 16 | 16#2CA0 = 11424 | 16#2054/19 | 16#9A/01/19 = 154/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 100.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 16] (SP16) | [Preset speeds] (PSS) [Settings] (SET)
USP | + speed assignment | 16#2CED = 11501 | 16#2055/2 | 16#9A/01/66 = 154/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ Speed Assign] (USP) | [+/- speed] (UPD)
DSP | - speed assignment | 16#2CEE = 11502 | 16#2055/3 | 16#9A/01/67 = 154/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [- Speed Assign] (DSP) | [+/- speed] (UPD)
STR | Reference frequency save | 16#2CEF = 11503 | 16#2055/4 | 16#9A/01/68 = 154/01/104 | STR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No save] NO |  | [Ref Frequency Save] (STR) | [+/- speed] (UPD)
USI | + speed assignment | 16#2D00 = 11520 | 16#2055/15 | 16#9A/01/79 = 154/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ Speed Assign] (USI) | [+/- speed around ref] (SRE)
DSI | - speed assignment | 16#2D01 = 11521 | 16#2055/16 | 16#9A/01/7A = 154/01/122 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [- Speed Assign] (DSI) | [+/- speed around ref] (SRE)
LAF | Stop forward limit assignment | 16#2D51 = 11601 | 16#2056/2 | 16#9B/01/02 = 155/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop FW assign] (LAF) | [Limit switches] (LST)
LAR | Stop reverse limit assignment | 16#2D52 = 11602 | 16#2056/3 | 16#9B/01/03 = 155/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop RV assign] (LAR) | [Limit switches] (LST)
LAS | Stop type on limit switch | 16#2D53 = 11603 | 16#2056/4 | 16#9B/01/04 = 155/01/04 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] NST |  | [Stop type] (LAS) | [Limit switches] (LST)
SRP | +/- speed limitation | 16#2CF1 = 11505 | 16#2055/6 | 16#9A/01/6A = 154/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 50 % | [+/- Speed limitation] (SRP) | [+/- speed around ref] (SRE) [Settings] (SET)
SPM | Reference frequency memory assignment | 16#212B = 8491 | 16#2036/5C | 16#8B/01/5C = 139/01/92 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ref Freq Memo assign] (SPM) | [Memo reference frequency] (SPM)
FLU | Motor fluxing configure | 16#364E = 13902 | 16#206D/3 | 16#A6/01/67 = 166/01/103 | FLU | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Motor fluxing] (FLU) | [Fluxing by DI] (FLI) [Settings] (SET)
FLI | Fluxing input assignment | 16#364D = 13901 | 16#206D/2 | 16#A6/01/66 = 166/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fluxing assignment] (FLI) | [Fluxing by DI] (FLI)
AST | Auto angle setting type | 16#3665 = 13925 | 16#206D/1A | 16#A6/01/7E = 166/01/126 | AST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pulse Signal injection - Optimized] PSIO |  | [Angle setting type] (AST) | [data] (MTD) [Angle test setting] (ASA) [Motor tune] (MTU) [Fluxing by DI] (FLI)
ASA | Angle auto-test | 16#3661 = 13921 | 16#206D/16 | 16#A6/01/7A = 166/01/122 | ASA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Angle auto-test] (ASA) | [Angle test setting] (ASA)
ASL | Angle Test assignment | 16#3663 = 13923 | 16#206D/18 | 16#A6/01/7C = 166/01/124 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Angle Test Assign] (ASL) | [Angle test setting] (ASA)
ATA | Angle setting activation mode | 16#3664 = 13924 | 16#206D/19 | 16#A6/01/7D = 166/01/125 | ATA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Run command] AUTO |  | [Angle setting Mode] (ATA) | [Angle test setting] (ASA)
ASTS | Auto angle setting status | 16#3666 = 13926 | 16#206D/1B | 16#A6/01/7F = 166/01/127 | ASTS | Status parameters | R | WORD (Enumeration) | - | [Not done] TAB |  | [Angle setting status] (ASTS) | [Angle test setting] (ASA)
HFI | Activation of HF injection | 16#3CF0 = 15600 | 16#207E/1 | 16#AF/01/01 = 175/01/01 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [HF inj. activation] (HFI) | [Motor control] (DRC)
SPB | Bandwidth of the HF PLL | 16#3CF3 = 15603 | 16#207E/4 | 16#AF/01/04 = 175/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 400 % | [HF pll bandwidth] (SPB) | [Motor control] (DRC)
ILR | Current level of the HF alignment | 16#3CF5 = 15605 | 16#207E/6 | 16#AF/01/06 = 175/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 200 % | [Current Level Align] (ILR) | [Motor control] (DRC)
SIR | Boost level for IPMA alignment | 16#3CF6 = 15606 | 16#207E/7 | 16#AF/01/07 = 175/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [Boost level align.] (SIR) | [Motor control] (DRC)
MCR | Maximum current of PSI alignment | 16#3CF7 = 15607 | 16#207E/8 | 16#AF/01/08 = 175/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [PSI Align Curr Max] (MCR) | [data] (MTD) [Motor tune] (MTU)
PEC | Angle position error compensation | 16#3CF8 = 15608 | 16#207E/9 | 16#AF/01/09 = 175/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 500 % | [Angle error Comp.] (PEC) | [Motor control] (DRC)
BLC | Brake assignment | 16#2711 = 10001 | 16#2046/2 | 16#93/01/02 = 147/01/02 | BLC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Brake assignment] (BLC) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BST | Motion type selection | 16#2718 = 10008 | 16#2046/9 | 16#93/01/09 = 147/01/09 | BST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Hoisting motion] VER |  | [Movement type] (BST) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BCI | Brake contact input | 16#2719 = 10009 | 16#2046/A | 16#93/01/0A = 147/01/10 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Brake Contact] (BCI) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BIP | Brake release pulse | 16#2717 = 10007 | 16#2046/8 | 16#93/01/08 = 147/01/08 | BIP | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Brake Release Pulse] (BIP) | [Brake logic control] (BLC) [Brake logic control] (BLC)
IBR | Brake Release current | 16#2716 = 10006 | 16#2046/7 | 16#93/01/07 = 147/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Brk Release Current] (IBR) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
IRD | Rev. brake release curr. | 16#271B = 10011 | 16#2046/C | 16#93/01/0C = 147/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Brake release I Rev] (IRD) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BRT | Brake release time | 16#2714 = 10004 | 16#2046/5 | 16#93/01/05 = 147/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | Refer to programming manual | 0.00 s ... 5.00 s | [Brake Release time] (BRT) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BIR | Brake release frequency | 16#271C = 10012 | 16#2046/D | 16#93/01/0D = 147/01/13 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Brake release freq] (BIR) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BEN | Brake engage frequency | 16#2713 = 10003 | 16#2046/4 | 16#93/01/04 = 147/01/04 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Brake engage freq] (BEN) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
TBE | Brake engage delay | 16#271A = 10010 | 16#2046/B | 16#93/01/0B = 147/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage delay] (TBE) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BET | Brake engage time | 16#2715 = 10005 | 16#2046/6 | 16#93/01/06 = 147/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | Refer to programming manual | 0.00 s ... 5.00 s | [Brake engage time] (BET) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BED | Brake engage at reversal | 16#2724 = 10020 | 16#2046/15 | 16#93/01/15 = 147/01/21 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Engage at reversal] (BED) | [Brake logic control] (BLC) [Brake logic control] (BLC)
JDC | Jump at reversal | 16#271D = 10013 | 16#2046/E | 16#93/01/0E = 147/01/14 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Jump at reversal] (JDC) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BECD | Brake engage at 0 speed | 16#271E = 10014 | 16#2046/F | 16#93/01/0F = 147/01/15 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 s | -0.1 s | -0.1 s ... 30.0 s | [Brake engage at 0] (BECD) | [Brake logic control] (BLC) [Brake logic control] (BLC)
TTR | Time to restart | 16#2726 = 10022 | 16#2046/17 | 16#93/01/17 = 147/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 15.00 s | [Time to restart] (TTR) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
FBCI | Brake feedback filter | 16#2729 = 10025 | 16#2046/1A | 16#93/01/1A = 147/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 100 ms | 0 ms ... 5000 ms | [Brake Fdbk Filter] (FBCI) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BRH | Brake hidden | 16#2742 = 10050 | 16#2046/33 | 16#93/01/33 = 147/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
BFTD | BRH_b4 frequency threshold detection | 16#2743 = 10051 | 16#2046/34 | 16#93/01/34 = 147/01/52 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 10.0 Hz | [BRH_b4_freq] (BFTD) | [Brake logic control] (BLC) [Brake logic control] (BLC) [Settings] (SET)
MDFT | Load maintain time | 16#2746 = 10054 | 16#2046/37 | 16#93/01/37 = 147/01/55 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 60 min | [Load Maintain Time] (MDFT) | [Brake logic control] (BLC) [Brake logic control] (BLC)
MTBF | Load maintain remaining time | 16#2747 = 10055 | 16#2046/38 | 16#93/01/38 = 147/01/56 |  | Actual values parameters | R | INT (Signed16) | 1 s |  | -1 s ... 3600 s | [Load Maintain Delay] (MTBF) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BRR | Current ramp time | 16#271F = 10015 | 16#2046/10 | 16#93/01/10 = 147/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Current ramp time] (BRR) | [Brake logic control] (BLC) [Brake logic control] (BLC)
ENA | ENA activation | 16#2F45 = 12101 | 16#205B/2 | 16#9D/01/66 = 157/01/102 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [ENA activation] (ENA) | [ENA System] (ENA)
GPE | ENA proportional gain | 16#2F47 = 12103 | 16#205B/4 | 16#9D/01/68 = 157/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 250 | 1 ... 9999 | [ENA prop gain] (GPE) | [ENA System] (ENA) [Settings] (SET)
GIE | ENA integral gain | 16#2F48 = 12104 | 16#205B/5 | 16#9D/01/69 = 157/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 9999 | [ENA integral gain] (GIE) | [ENA System] (ENA) [Settings] (SET)
RAP | Reduction ratio | 16#2F49 = 12105 | 16#205B/6 | 16#9D/01/6A = 157/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 10.0 | 10.0 ... 999.9 | [Reduction ratio] (RAP) | [ENA System] (ENA)
HSO | High speed hoisting | 16#300D = 12301 | 16#205D/2 | 16#9E/01/66 = 158/01/102 | HSO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [High speed hoisting] (HSO) | [High speed hoisting] (HSH)
COF | Motor speed coefficient | 16#300F = 12303 | 16#205D/4 | 16#9E/01/68 = 158/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [Motor speed coeff.] (COF) | [High speed hoisting] (HSH)
COR | Generator speed coefficient | 16#3010 = 12304 | 16#205D/5 | 16#9E/01/69 = 158/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 200 % | [Gen. speed coeff] (COR) | [High speed hoisting] (HSH)
TOS | Load measuring time | 16#3013 = 12307 | 16#205D/8 | 16#9E/01/6C = 158/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.50 s | 0.10 s ... 65.00 s | [Load measuring tm.] (TOS) | [High speed hoisting] (HSH)
OSP | Measurement speed | 16#3011 = 12305 | 16#205D/6 | 16#9E/01/6A = 158/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Measurement spd] (OSP) | [High speed hoisting] (HSH)
CLO | High speed I limit | 16#300E = 12302 | 16#205D/3 | 16#9E/01/67 = 158/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [High speed I Limit] (CLO) | [High speed hoisting] (HSH)
SCL | Current limit. frequency | 16#3012 = 12306 | 16#205D/7 | 16#9E/01/6B = 158/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [I Limit. frequency] (SCL) | [High speed hoisting] (HSH)
RSTL | Rope slack torque level | 16#3022 = 12322 | 16#205D/17 | 16#9E/01/7B = 158/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Rope slack trq level] (RSTL) | [High speed hoisting] (HSH) [Rope Slack Handling] (SDR)
RSD | Rope slack configuration | 16#3021 = 12321 | 16#205D/16 | 16#9E/01/7A = 158/01/122 | RSD | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Rope slack config.] (RSD) | [High speed hoisting] (HSH) [Rope Slack Handling] (SDR)
PIF | PID controller feedback | 16#2E7D = 11901 | 16#2059/2 | 16#9C/01/66 = 156/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID feedback Assign] (PIF) | [PID Feedback] (FDB) [PID Feedback] (FDB)
PIF1 | Minimum PID feedback | 16#2E80 = 11904 | 16#2059/5 | 16#9C/01/69 = 156/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 32767 | [Min PID feedback] (PIF1) | [PID Feedback] (FDB) [PID Feedback] (FDB)
PIF2 | Maximum PID feedback | 16#2E81 = 11905 | 16#2059/6 | 16#9C/01/6A = 156/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 1000 | 0 ... 32767 | [Max PID feedback] (PIF2) | [PID Feedback] (FDB) [PID Feedback] (FDB)
PIP1 | Minimum PID process | 16#2E82 = 11906 | 16#2059/7 | 16#9C/01/6B = 156/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 150 | 0 ... 32767 | [Min PID Process] (PIP1) | [PID Reference] (RF) [PID Reference] (RF)
PIP2 | Maximum PID process | 16#2E83 = 11907 | 16#2059/8 | 16#9C/01/6C = 156/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 900 | 0 ... 32767 | [Max PID Process] (PIP2) | [PID Reference] (RF) [PID Reference] (RF)
PII | Internal PID reference | 16#2E84 = 11908 | 16#2059/9 | 16#9C/01/6D = 156/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Intern PID Ref] (PII) | [PID Reference] (RF) [PID Reference] (RF)
RPI | Internal PID reference | 16#2E90 = 11920 | 16#2059/15 | 16#9C/01/79 = 156/01/121 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 150 | 0 ... 32767 | [Internal PID ref] (RPI) | [PID display] (PIC) [PID Reference] (RF) [PID Reference] (RF)
RPG | PID Proportional gain | 16#2EA5 = 11941 | 16#2059/2A | 16#9C/01/8E = 156/01/142 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Prop.Gain] (RPG) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
RIG | PID controller integral gain | 16#2EA6 = 11942 | 16#2059/2B | 16#9C/01/8F = 156/01/143 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Intgl.Gain] (RIG) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
RDG | PID derivative gain | 16#2EA7 = 11943 | 16#2059/2C | 16#9C/01/90 = 156/01/144 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 0.00 | 0.00 ... 100.00 | [PID derivative gain] (RDG) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PRP | PID ramp | 16#2ED0 = 11984 | 16#2059/55 | 16#9C/01/B9 = 156/01/185 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [PID ramp] (PRP) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PIC | PID inversion | 16#2EA4 = 11940 | 16#2059/29 | 16#9C/01/8D = 156/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID Inversion] (PIC) | [Settings] (ST) [Settings] (ST)
POL | PID controller min. output | 16#2EB0 = 11952 | 16#2059/35 | 16#9C/01/99 = 156/01/153 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -599.0 Hz ... 599.0 Hz | [PID Min Output] (POL) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
POH | PID controller max. output | 16#2EB1 = 11953 | 16#2059/36 | 16#9C/01/9A = 156/01/154 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [PID Max Output] (POH) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PAL | Minimum feedback level warning | 16#2EB9 = 11961 | 16#2059/3E | 16#9C/01/A2 = 156/01/162 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 65535 | [Min fbk Warning] (PAL) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Settings] (SET)
PAH | Maximum feedback level warning | 16#2EBA = 11962 | 16#2059/3F | 16#9C/01/A3 = 156/01/163 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 1000 | 0 ... 65535 | [Max fbk Warning] (PAH) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Settings] (SET)
PER | PID error warning | 16#2EBB = 11963 | 16#2059/40 | 16#9C/01/A4 = 156/01/164 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 65535 | [PID error Warning] (PER) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PIS | PID integral disabled | 16#2EA8 = 11944 | 16#2059/2D | 16#9C/01/91 = 156/01/145 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID Integral OFF] (PIS) | [Settings] (ST) [Settings] (ST)
FPI | Predictive speed reference | 16#2EAE = 11950 | 16#2059/33 | 16#9C/01/97 = 156/01/151 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Predictive Speed Ref] (FPI) | [PID Reference] (RF) [PID Reference] (RF)
PSR | PID speed input % ref | 16#2EAF = 11951 | 16#2059/34 | 16#9C/01/98 = 156/01/152 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Speed input %] (PSR) | [PID Reference] (RF) [PID Reference] (RF) [Settings] (SET)
PAU | Auto/Manual select input | 16#2EC2 = 11970 | 16#2059/47 | 16#9C/01/AB = 156/01/171 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Auto/Manual assign.] (PAU) | [PID Reference] (RF) [PID Reference] (RF)
PIM | Manual PID reference | 16#2EB2 = 11954 | 16#2059/37 | 16#9C/01/9B = 156/01/155 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Manual PID reference] (PIM) | [PID Reference] (RF) [PID Reference] (RF)
TLS | Low speed timeout | 16#2DB5 = 11701 | 16#2057/2 | 16#9B/01/66 = 155/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Low Speed Timeout] (TLS) | [Settings] (SET) [Stop after speed timeout] (PRSP)
PR2 | 2 PID Preset assignment | 16#2E85 = 11909 | 16#2059/A | 16#9C/01/6E = 156/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 PID Preset Assign] (PR2) | [PID preset references] (PRI) [PID preset references] (PRI)
PR4 | 4 PID Preset assignment | 16#2E86 = 11910 | 16#2059/B | 16#9C/01/6F = 156/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 PID Preset Assign] (PR4) | [PID preset references] (PRI) [PID preset references] (PRI)
RP2 | 2nd PID preset reference | 16#2E91 = 11921 | 16#2059/16 | 16#9C/01/7A = 156/01/122 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 300 | 0 ... 32767 | [Ref PID Preset 2] (RP2) | [Settings] (SET) [PID preset references] (PRI) [PID preset references] (PRI)
RP3 | 3rd PID preset reference | 16#2E92 = 11922 | 16#2059/17 | 16#9C/01/7B = 156/01/123 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 0 ... 32767 | [Ref PID Preset 3] (RP3) | [Settings] (SET) [PID preset references] (PRI) [PID preset references] (PRI)
RP4 | 4th PID preset reference | 16#2E93 = 11923 | 16#2059/18 | 16#9C/01/7C = 156/01/124 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 900 | 0 ... 32767 | [Ref PID Preset 4] (RP4) | [PID preset references] (PRI) [PID preset references] (PRI) [Settings] (SET)
TLA | Torque limit. activation | 16#23FA = 9210 | 16#203E/B | 16#8F/01/0B = 143/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque limit activ.] (TLA) | [Torque limitation] (TOL)
INTP | Torque increment | 16#23FF = 9215 | 16#203E/10 | 16#8F/01/10 = 143/01/16 | INCPER | Configuration and settings | R/WS | WORD (Enumeration) | - | [1%] 1 |  | [Torque increment] (INTP) | [Torque limitation] (TOL)
TLIM | Motoring torque limit | 16#23FB = 9211 | 16#203E/C | 16#8F/01/0C = 143/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 3000 | [Motor torque limit] (TLIM) | [Torque limitation] (TOL) [Settings] (SET)
TLIG | Generator torque limit | 16#23FC = 9212 | 16#203E/D | 16#8F/01/0D = 143/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 3000 | [Gen. torque limit] (TLIG) | [Torque limitation] (TOL) [Settings] (SET)
TAA | Reference torque assignment | 16#23FE = 9214 | 16#203E/F | 16#8F/01/0F = 143/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Torque Assign] (TAA) | [Torque limitation] (TOL)
TLC | Torque analog limit. activ | 16#23FD = 9213 | 16#203E/E | 16#8F/01/0E = 143/01/14 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Analog limit activ.] (TLC) | [Torque limitation] (TOL)
TSS | Torque/Speed switching control mode | 16#2404 = 9220 | 16#203E/15 | 16#8F/01/15 = 143/01/21 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Trq/spd switching] (TSS) | [Torque control] (TOR)
TR1 | Channel for torque reference | 16#2405 = 9221 | 16#203E/16 | 16#8F/01/16 = 143/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque ref. channel] (TR1) | [Torque control] (TOR)
TSD | Torque reference sign switching | 16#2406 = 9222 | 16#203E/17 | 16#8F/01/17 = 143/01/23 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Torque ref. sign] (TSD) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
DBN | Torque regulation negative deadband | 16#2407 = 9223 | 16#203E/18 | 16#8F/01/18 = 143/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 2000.0 Hz | [Negative deadband] (DBN) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
DBP | Torque regulation positive deadband | 16#2408 = 9224 | 16#203E/19 | 16#8F/01/19 = 143/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 2000.0 Hz | [Positive deadband] (DBP) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TRT | Torque ratio | 16#2409 = 9225 | 16#203E/1A | 16#8F/01/1A = 143/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 1000.0 % | [Torque ratio] (TRT) | [Torque control] (TOR) [Settings] (SET) [M/S Torque Control] (MSQ)
TRP | Torque ramp time | 16#240A = 9226 | 16#203E/1B | 16#8F/01/1B = 143/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 3.00 s | 0.00 s ... 99.99 s | [Torque ramp time] (TRP) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TST | Torque control stop type | 16#240B = 9227 | 16#203E/1C | 16#8F/01/1C = 143/01/28 | TST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] NST |  | [Torque control stop] (TST) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TOB | Response to torque control error | 16#240C = 9228 | 16#203E/1D | 16#8F/01/1D = 143/01/29 | TOB | Configuration and settings | R/WS | WORD (Enumeration) | - | [warning] ALRM |  | [Torque Ctrl ErrorResp] (TOB) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
RTO | Torque control time out | 16#240D = 9229 | 16#203E/1E | 16#8F/01/1E = 143/01/30 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 999.9 s | [Torque ctrl time out] (RTO) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
SPT | Spin time | 16#240E = 9230 | 16#203E/1F | 16#8F/01/1F = 143/01/31 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 0.0 s ... 3600.0 s | [Spin time] (SPT) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TQR | Torque ratio assignment | 16#2411 = 9233 | 16#203E/22 | 16#8F/01/22 = 143/01/34 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Torque Ratio Assign] (TQR) | [Torque control] (TOR)
TQO | Torque offset assignment | 16#2413 = 9235 | 16#203E/24 | 16#8F/01/24 = 143/01/36 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Torque Offset Assign] (TQO) | [Torque control] (TOR)
TRI | Torque reference assignment | 16#2416 = 9238 | 16#203E/27 | 16#8F/01/27 = 143/01/39 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Torque reference channel] TR1 |  | [Torque Ref Assign] (TRI) | [Torque control] (TOR)
TR2 | Torque reference 2 channel | 16#2417 = 9239 | 16#203E/28 | 16#8F/01/28 = 143/01/40 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque Ref 2 Channel] (TR2) | [Torque control] (TOR)
LC2 | Current limitation 2 | 16#23F2 = 9202 | 16#203E/3 | 16#8F/01/03 = 143/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Current Limitation2] (LC2) | [2nd current limit.] (CLI)
CL2 | Current limitation 2 value | 16#23F3 = 9203 | 16#203E/4 | 16#8F/01/04 = 143/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Current Limit2 Value] (CL2) | [2nd current limit.] (CLI) [Settings] (SET)
TASU | Reference torque switch assignment | 16#23F8 = 9208 | 16#203E/9 | 16#8F/01/09 = 143/01/09 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ref Torque Switch Assign] (TASU) | [Torque limitation] (TOL)
TAA2 | Reference torque 2 assignment | 16#23F9 = 9209 | 16#203E/A | 16#8F/01/0A = 143/01/10 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Torque 2 Assign] (TAA2) | [Torque limitation] (TOL)
LLC | Mains contactor control | 16#3522 = 13602 | 16#206A/3 | 16#A5/01/03 = 165/01/03 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Mains Contactor] (LLC) | [Mains contactor command] (LLC)
LES | Device lock assignment | 16#3521 = 13601 | 16#206A/2 | 16#A5/01/02 = 165/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Device Lock] (LES) | [Mains contactor command] (LLC) [Circuit breaker] (CCBK)
LCT | Mains V. time out | 16#3523 = 13603 | 16#206A/4 | 16#A5/01/04 = 165/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 5 s | 1 s ... 999 s | [Mains V. time out] (LCT) | [Mains contactor command] (LLC) [Circuit breaker] (CCBK)
SAF | Fwd stop limit input assig | 16#30D5 = 12501 | 16#205F/2 | 16#9F/01/66 = 159/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop FW limit sw.] (SAF) | [Positioning by sensors] (LPO)
SAR | RV stop limit input assign | 16#30D6 = 12502 | 16#205F/3 | 16#9F/01/67 = 159/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop RV limit sw.] (SAR) | [Positioning by sensors] (LPO)
DAF | Forward slowdown limit | 16#30D7 = 12503 | 16#205F/4 | 16#9F/01/68 = 159/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forward Slowdown] (DAF) | [Positioning by sensors] (LPO)
DAR | Reverse slowdown limit | 16#30D8 = 12504 | 16#205F/5 | 16#9F/01/69 = 159/01/105 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Reverse Slowdown] (DAR) | [Positioning by sensors] (LPO)
CLS | Disable limit switch | 16#30DB = 12507 | 16#205F/8 | 16#9F/01/6C = 159/01/108 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Disable limit sw.] (CLS) | [Positioning by sensors] (LPO)
PAS | Stop type | 16#30DA = 12506 | 16#205F/7 | 16#9F/01/6B = 159/01/107 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [On ramp] RMP |  | [Stop type] (PAS) | [Positioning by sensors] (LPO)
DSF | Deceleration type | 16#30D9 = 12505 | 16#205F/6 | 16#9F/01/6A = 159/01/106 | DSF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] STD |  | [Deceleration type] (DSF) | [Positioning by sensors] (LPO)
STD | Stop distance | 16#30E9 = 12521 | 16#205F/16 | 16#9F/01/7A = 159/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m | 0.00 m | 0.00 m ... 10.00 m | [Stop distance] (STD) | [Positioning by sensors] (LPO)
NLS | Rated linear speed | 16#30DF = 12511 | 16#205F/C | 16#9F/01/70 = 159/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m/s | 1.00 m/s | 0.20 m/s ... 5.00 m/s | [Nom linear speed] (NLS) | [Positioning by sensors] (LPO)
SFD | Distance stop corrector | 16#30EA = 12522 | 16#205F/17 | 16#9F/01/7B = 159/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 50 % ... 200 % | [Stop corrector] (SFD) | [Positioning by sensors] (LPO)
CHM | Multimotors selection | 16#1F59 = 8025 | 16#2032/1A | 16#89/01/1A = 137/01/26 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Multimotors] (CHM) | [Multimotors config] (MMC)
CNF1 | 2 configurations assignt. | 16#1F55 = 8021 | 16#2032/16 | 16#89/01/16 = 137/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Configurations] (CNF1) | [Multimotors config] (MMC)
CNF2 | 3 configurations assignt. | 16#1F56 = 8022 | 16#2032/17 | 16#89/01/17 = 137/01/23 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Configurations] (CNF2) | [Multimotors config] (MMC)
TUL | Autotuning input assignment | 16#258A = 9610 | 16#2042/B | 16#91/01/0B = 145/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Autotuning Assign] (TUL) | [Motor tune] (MTU)
RSF | Fault reset input assignment | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Fault Reset Assign] (RSF) | [Fault reset] (RST)
RP | Product restart | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Product restart] (RP) | [Fault reset] (RST)
RPA | Product restart assignment | 16#1BD9 = 7129 | 16#2029/1E | 16#84/01/82 = 132/01/130 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Prod Restart Assign] (RPA) | [Fault reset] (RST)
ATR | Automatic fault reset | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Auto Fault Reset] (ATR) | [Auto Fault Reset] (ATR)
TAR | Fault Reset time | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] 5 |  | [Fault Reset Time] (TAR) | [Auto Fault Reset] (ATR)
FLR | Catch on fly | 16#0C26 = 3110 | 16#2001/B | 16#70/01/6F = 112/01/111 | FLR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Catch On Fly] (FLR) | [Catch on the fly] (FLR)
THT | Motor thermal monitoring mode | 16#258C = 9612 | 16#2042/D | 16#91/01/0D = 145/01/13 | THT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Self cooled motor] ACL |  | [Motor Thermal Mode] (THT) | [Motor monitoring] (MOP) [Motor thermal monit] (THT)
TTD | Motor thermal threshold | 16#2AFA = 11002 | 16#2050/3 | 16#98/01/03 = 152/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor Therm Thd] (TTD) | [Motor monitoring] (MOP) [Threshold reached] (THRE) [Settings] (SET)
TTD2 | Motor 2 thermal threshold | 16#2AFE = 11006 | 16#2050/7 | 16#98/01/07 = 152/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor2 Therm Thd] (TTD2) | [Motor monitoring] (MOP) [Threshold reached] (THRE)
TTD3 | Motor 3 thermal threshold | 16#2AFF = 11007 | 16#2050/8 | 16#98/01/08 = 152/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor3 Therm Thd] (TTD3) | [Motor monitoring] (MOP) [Threshold reached] (THRE)
TTD4 | Motor 4 thermal threshold | 16#2B00 = 11008 | 16#2050/9 | 16#98/01/09 = 152/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor4 Therm Thd] (TTD4) | [Motor monitoring] (MOP) [Threshold reached] (THRE)
OLL | Motor overtemp error response | 16#1B61 = 7009 | 16#2028/A | 16#84/01/0A = 132/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorTemp ErrorResp] (OLL) | [Motor monitoring] (MOP)
OPL | Output Phase Loss assignment | 16#258B = 9611 | 16#2042/C | 16#91/01/0C = 145/01/12 | OPL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [OutPhaseLoss Assign] (OPL) | [Output phase loss] (OPL)
ODT | Output Phase Loss delay | 16#1BA9 = 7081 | 16#2028/52 | 16#84/01/52 = 132/01/82 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.5 s ... 10.0 s | [OutPhaseLoss Delay] (ODT) | [Output phase loss] (OPL)
IPL | Input Phase Loss assignment | 16#1B5A = 7002 | 16#2028/3 | 16#84/01/03 = 132/01/03 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [InPhaseLoss Assign] (IPL) | [Input phase loss] (IPL)
OHL | Drive overtemp error response | 16#1B60 = 7008 | 16#2028/9 | 16#84/01/09 = 132/01/09 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [DriveTemp ErrorResp] (OHL) | [Drive overload monit] (OBR)
THA | Device thermal state warning | 16#2B01 = 11009 | 16#2050/A | 16#98/01/0A = 152/01/10 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Dev Thermal Warning] (THA) | [Drive overload monit] (OBR)
ETF | External error assignment | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ext Error assign] (ETF) | [External error] (ETF)
EPL | Device response to external error | 16#1B5E = 7006 | 16#2028/7 | 16#84/01/07 = 132/01/07 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Ext Error Resp] (EPL) | [External error] (ETF)
USB | Response to undervoltage | 16#35EB = 13803 | 16#206C/4 | 16#A6/01/04 = 166/01/04 | USB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error triggered] 0 |  | [Undervoltage Resp] (USB) | [Undervoltage handling] (USB)
URES | Evacuation mains voltage | 16#35E9 = 13801 | 16#206C/2 | 16#A6/01/02 = 166/01/02 | URES | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Mains voltage] (URES) | [Undervoltage handling] (USB)
USL | Undervoltage level | 16#35EA = 13802 | 16#206C/3 | 16#A6/01/03 = 166/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 435 V | [Undervoltage level] (USL) | [Undervoltage handling] (USB)
UST | Undervoltage timeout | 16#35EC = 13804 | 16#206C/5 | 16#A6/01/05 = 166/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.2 s | 0.2 s ... 999.9 s | [UnderVolt timeout] (UST) | [Undervoltage handling] (USB)
STP | Stop type on power loss | 16#1B5C = 7004 | 16#2028/5 | 16#84/01/05 = 132/01/05 | STP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [Stop Type PLoss] (STP) | [Undervoltage handling] (USB)
TSM | Undervolt. restart time | 16#35F5 = 13813 | 16#206C/E | 16#A6/01/0E = 166/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 1.0 s ... 999.9 s | [UnderV. restart tm] (TSM) | [Undervoltage handling] (USB)
UPL | Under V prevention level | 16#35F3 = 13811 | 16#206C/C | 16#A6/01/0C = 166/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 141 V ... 495 V | [Prevention level] (UPL) | [Undervoltage handling] (USB)
SDD | Load slip detection | 16#1B5D = 7005 | 16#2028/6 | 16#84/01/06 = 132/01/06 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Load slip detection] (SDD) | [Encoder monitoring] (SDD)
STM | Maximum stop time | 16#35F6 = 13814 | 16#206C/F | 16#A6/01/0F = 166/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.01 s ... 60.00 s | [Max stop time] (STM) | [Undervoltage handling] (USB)
DCO | DC Bus charge assignment | 16#3611 = 13841 | 16#206C/2A | 16#A6/01/2A = 166/01/42 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [DC Charging Assign] (DCO) | [DC bus supply] (DCO)
DCT | DC Bus charge opt. time | 16#3612 = 13842 | 16#206C/2B | 16#A6/01/2B = 166/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [DC Bus Charge Time] (DCT) | [DC bus supply] (DCO) [DC-Bus Ref Link] (DBS)
TBS | DC bus maintain time | 16#35F4 = 13812 | 16#206C/D | 16#A6/01/0D = 166/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 9999 s | 1 s ... 9999 s | [DC bus maintain time] (TBS) | [Undervoltage handling] (USB)
STRT | Output short circuit test | 16#0C28 = 3112 | 16#2001/D | 16#70/01/71 = 112/01/113 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Output Short Circuit Test] (STRT) | [Motor monitoring] (MOP)
COFM | Catch on fly mode | 16#0C29 = 3113 | 16#2001/E | 16#70/01/72 = 112/01/114 | COFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Measured] HWCOF |  | [Catch On Fly Mode] (COFM) | [Catch on the fly] (FLR)
LFL3 | Response to 4-20mA loss on AI3 | 16#1B65 = 7013 | 16#2028/E | 16#84/01/0E = 132/01/14 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI3 4-20mA loss] (LFL3) | [4-20 mA loss] (LFL)
INH | Disable error detection | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Disable Error Detect] (INH) | [Error detect disabling] (INH)
INHS | Forced Run | 16#1BD6 = 7126 | 16#2029/1B | 16#84/01/7F = 132/01/127 | INHS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] NO |  | [Forced Run] (INHS) | [Error detect disabling] (INH)
INHR | Forced Run reference frequency | 16#1BD7 = 7127 | 16#2029/1C | 16#84/01/80 = 132/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 6553.5 Hz | [Forced Run Ref] (INHR) | [Error detect disabling] (INH)
CLL | Response to Fieldbus module communication interruption | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Fieldbus Interrupt Resp] (CLL) | [Communication Module] (COMO)
COL | Response to CANopen error | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CANopen Error Resp] (COL) | [Communication Module] (COMO)
SLL | Response to Modbus interruption | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Modbus Error Resp] (SLL) | [Fieldbus monitoring] (CLL)
SSB | Stop type - torque/I limit | 16#2418 = 9240 | 16#203E/29 | 16#8F/01/29 = 143/01/41 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [Trq/I limit. stop] (SSB) | [Torque limitation] (TOL) [Torque or I limit detect] (TID)
STO | Torque/I limit. timeout | 16#2419 = 9241 | 16#203E/2A | 16#8F/01/2A = 143/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 1000 ms | 0 ms ... 9999 ms | [Trq/I Limit Timeout] (STO) | [Torque limitation] (TOL) [Torque or I limit detect] (TID)
TNL | Response to Autotuning error | 16#1B64 = 7012 | 16#2028/D | 16#84/01/0D = 132/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Tuning Error Resp] (TNL) | [Motor tune] (MTU)
PPI | Pairing password | 16#36B1 = 14001 | 16#206E/2 | 16#A7/01/02 = 167/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [Pairing password] (PPI) | [My preferences] (MYP)
LFF | Fall back speed | 16#1BA8 = 7080 | 16#2028/51 | 16#84/01/51 = 132/01/81 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [FallbackSpeed] (LFF) | [4-20 mA loss] (LFL) [External error] (ETF) [Communication Module] (COMO) [Fieldbus monitoring] (CLL) [Fallback speed] (LFF) [Embedded modbus TCP] (EMTC) [Pumpcycle monitoring] (CSP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [M/S System Architecture] (MSA)
FQF | Frequency meter | 16#3909 = 14601 | 16#2074/2 | 16#AA/01/02 = 170/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Frequency meter] (FQF) | [Frequency meter] (FQF)
FQC | Pulse scaling divisor | 16#390A = 14602 | 16#2074/3 | 16#AA/01/03 = 170/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 1.0 | 1.0 ... 100.0 | [Pulse scal. divider] (FQC) | [Frequency meter] (FQF)
FQA | Overspd. pulse threshold | 16#390C = 14604 | 16#2074/5 | 16#AA/01/05 = 170/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 30000 Hz | [Overspd. pulse thd.] (FQA) | [Frequency meter] (FQF)
TDS | Pulse Overspeed delay | 16#390D = 14605 | 16#2074/6 | 16#AA/01/06 = 170/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse overspd delay] (TDS) | [Frequency meter] (FQF)
FDT | Level freq. pulse ctrl | 16#390E = 14606 | 16#2074/7 | 16#AA/01/07 = 170/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Level fr. pulse ctrl] (FDT) | [Frequency meter] (FQF)
FQT | Pulse threshold wo Run | 16#390F = 14607 | 16#2074/8 | 16#AA/01/08 = 170/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 1000 Hz | [Pulse thd. wo Run] (FQT) | [Frequency meter] (FQF)
TLD | Dynamic load time | 16#3018 = 12312 | 16#205D/D | 16#9E/01/71 = 158/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 0.01 s | -0.01 s | -0.01 s ... 10.00 s | [Dynamic load time] (TLD) | [Dynamic load detect.] (DLD)
DLD | Dynamic load threshold | 16#3017 = 12311 | 16#205D/C | 16#9E/01/70 = 158/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Dyn. load threshold] (DLD) | [Dynamic load detect.] (DLD)
DLB | Dynamic load Mgt. | 16#3019 = 12313 | 16#205D/E | 16#9E/01/72 = 158/01/114 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Dyn. load Mgt.] (DLB) | [Dynamic load detect.] (DLD)
NCA1 | Scan output 1 address | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
NCA2 | Scan output 2 address | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535
NCA3 | Scan output 3 address | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA4 | Scan output 4 address | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA5 | Scan output 5 address | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA6 | Scan output 6 address | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA7 | Scan output 7 address | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA8 | Scan output 8 address | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA1 | Scan input 1 address | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
NMA2 | Scan input 2 address | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535
NMA3 | Scan input 3 address | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA4 | Scan input 4 address | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA5 | Scan input 5 address | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA6 | Scan input 6 address | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA7 | Scan input 7 address | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA8 | Scan input 8 address | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA1 | Scan input 1 address | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 | [Scan. IN1 address] (OMA1) | [DeviceNet] (DNC)
OMA2 | Scan input 2 address | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 | [Scan. IN2 address] (OMA2) | [DeviceNet] (DNC)
OMA3 | Scan input 3 address | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan. IN3 address] (OMA3) | [DeviceNet] (DNC)
OMA4 | Scan input 4 address | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan. IN4 address] (OMA4) | [DeviceNet] (DNC)
OMA5 | Scan input 5 address | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA6 | Scan input 6 address | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA1 | Scan output 1 address | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 | [Scan.Out1 address] (OCA1) | [DeviceNet] (DNC)
OCA2 | Scan output 2 address | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 | [Scan.Out2 address] (OCA2) | [DeviceNet] (DNC)
OCA3 | Scan output 3 address | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan.Out3 address] (OCA3) | [DeviceNet] (DNC)
OCA4 | Scan output 4 address | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan.Out4 address] (OCA4) | [DeviceNet] (DNC)
OCA5 | Scan output 5 address | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA6 | Scan output 6 address | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ADD | Device modbus address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus Address] (ADD) | [Modbus Fieldbus] (MD1)
AMOC | Mdb add comm. module | 16#19FB = 6651 | 16#2024/34 | 16#82/01/34 = 130/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus add Com.C.] (AMOC) | [Modbus Fieldbus] (MD1)
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [Modbus Baud Rate] (TBR) | [Modbus Fieldbus] (MD1)
TFO | Modbus format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [Modbus Format] (TFO) | [Modbus Fieldbus] (MD1)
TTO | Modbus timeout | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [ModbusTimeout] (TTO) | [Modbus Fieldbus] (MD1)
ADCO | Device CANopen address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 127 | [CANopen Address] (ADCO) | [CANopen] (CNO)
BDCO | CANopen baudrate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Baud rate 250kbps] 250K |  | [CANopen Baudrate] (BDCO) | [CANopen] (CNO)
ERCO | CANopen error | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [CANopen Error] (ERCO) | [CANopen map] (CNM) [CANopen] (CNO)
FLO | Forced local assignment | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forced Local Assign] (FLO) | [Command and Reference] (CRP)
FLOC | Forced Local channel assignment | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Forced Local Chan] (FLOC) | [Command and Reference] (CRP)
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOT) | [Command and Reference] (CRP)
ADRC | Device address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (ADRC) | [DeviceNet] (DNC) [Profibus] (PBC) [Powerlink] (EPL)
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [PPO profile used] (PRFL) | [Profibus diag] (PRB) [Profinet diag] (PRN)
DPMA | DP Master active | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | R/W | WORD (Enumeration) | - | [Master 1] 1 |  | [DP Master Active] (DPMA) | [Profibus diag] (PRB) [Profinet diag] (PRN)
ECSA | EtherCAT second address | 16#1A23 = 6691 | 16#2024/5C | 16#82/01/5C = 130/01/92 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat 2nd addr] (ECSA) | [EtherCAT Module] (ETC)
CIOA | Configured assembly | 16#1A0B = 6667 | 16#2024/44 | 16#82/01/44 = 130/01/68 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] 21 |  | [Conf. Assembly] (CIOA) | [DeviceNet] (DNC)
BDR | Comm. option baudrate | 16#19CB = 6603 | 16#2024/4 | 16#82/01/04 = 130/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [Automatic] AUTO |  | [Baudrate] (BDR) | [DeviceNet] (DNC)
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | R/W | WORD (Enumeration) | - | [Automatic] AUTO |  | [Data rate used] (BDRU) | [DEVICENET DIAG] (DVN) [Profibus diag] (PRB)
RDS | Rate and duplex setting | 16#FAFB = 64251 |  |  | RDS | Configuration and settings | R/W | WORD (Enumeration) | - | [Auto detected] AUTO
ARD | Actual rate and duplex | 16#FB0A = 64266 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Actual rate] (ARD) | [Ethernet Module Diag] (MTE)
L1D | DI1 delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI1 Delay] (L1D) | [DI1 Configuration] (DI1)
R1 | R1 assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Device in operating state "Fault"] FLT |  | [R1 Assignment] (R1) | [R1 configuration] (R1)
R2 | R2 assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [R2 Assignment] (R2) | [R2 configuration] (R2)
L2D | DI2 delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI2 Delay] (L2D) | [DI2 Configuration] (DI2)
R1D | R1 delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Delay time] (R1D) | [R1 configuration] (R1)
R2D | R2 delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Delay time] (R2D) | [R2 configuration] (R2)
L3D | DI3 delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI3 Delay] (L3D) | [DI3 Configuration] (DI3)
R1S | R1 active level | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R1 Active at] (R1S) | [R1 configuration] (R1)
R2S | R2 active level | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R2 Active at] (R2S) | [R2 configuration] (R2)
L4D | DI4 delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI4 Delay] (L4D) | [DI4 Configuration] (DI4)
R1H | R1 holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Holding time] (R1H) | [R1 configuration] (R1)
R2H | R2 holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Holding time] (R2H) | [R2 configuration] (R2)
L5D | DI5 delay | 16#0FA5 = 4005 | 16#200A/6 | 16#75/01/06 = 117/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI5 Delay] (L5D) | [DI5 Configuration] (DI5)
L6D | DI6 delay | 16#0FA6 = 4006 | 16#200A/7 | 16#75/01/07 = 117/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI6 Delay] (L6D) | [DI6 Configuration] (DI6)
L7D | DI7 delay | 16#0FA7 = 4007 | 16#200A/8 | 16#75/01/08 = 117/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI7 Delay] (L7D) | [DI7 Configuration] (DI7)
L8D | DI8 delay | 16#0FA8 = 4008 | 16#200A/9 | 16#75/01/09 = 117/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI8 Delay] (L8D) | [DI8 Configuration] (DI8)
DO1 | DQ1 assignment | 16#13A7 = 5031 | 16#2014/20 | 16#7A/01/20 = 122/01/32 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ1 Assignment] (DO1) | [DQ1 configuration] (DO1)
DO1D | DQ1 delay time | 16#10B9 = 4281 | 16#200C/52 | 16#76/01/52 = 118/01/82 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ1 Delay time] (DO1D) | [DQ1 configuration] (DO1)
DO1H | DQ1 holding time | 16#10AF = 4271 | 16#200C/48 | 16#76/01/48 = 118/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ1 Holding time] (DO1H) | [DQ1 configuration] (DO1)
DO1S | DQ1 active level | 16#10A5 = 4261 | 16#200C/3E | 16#76/01/3E = 118/01/62 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [DQ1 Active at] (DO1S) | [DQ1 configuration] (DO1)
FRHT | FRH high resolution | 16#0C96 = 3222 | 16#2002/17 | 16#71/01/17 = 113/01/23 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SLCR | LCR without filter | 16#0C98 = 3224 | 16#2002/19 | 16#71/01/19 = 113/01/25 |  | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535
SRFR | RFR without filter | 16#0C99 = 3225 | 16#2002/1A | 16#71/01/1A = 113/01/26 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
MMF | Measured output freq. | 16#0C93 = 3219 | 16#2002/14 | 16#71/01/14 = 113/01/20 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Measured output fr.] (MMF) | [Drive parameters] (MPI)
SOTR | Motor torque (% of Cn motor in Q12) without filter | 16#0C9A = 3226 | 16#2002/1B | 16#71/01/1B = 113/01/27 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SULN | ULN without filter | 16#0C9D = 3229 | 16#2002/1E | 16#71/01/1E = 113/01/30 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
SOPR | OPR without filter | 16#0CDA = 3290 | 16#2002/5B | 16#71/01/5B = 113/01/91 |  | Configuration and settings | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 %
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI2 | AI2 physical value without filter | 16#14AC = 5292 | 16#2016/5D | 16#7B/01/5D = 123/01/93 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI3 | AI3 physical value without filter | 16#14AD = 5293 | 16#2016/5E | 16#7B/01/5E = 123/01/94 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAO1 | AO1 physical value without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
PGI | Number of pulses | 16#15E4 = 5604 | 16#201A/5 | 16#7D/01/05 = 125/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1024 | 100 ... 10000 | [Number of pulses] (PGI) | [Encoder configuration] (IEN)
ENS | AB Encoder type configuration | 16#15E8 = 5608 | 16#201A/9 | 16#7D/01/09 = 125/01/09 | ENS | Configuration and settings | R/WS | WORD (Enumeration) | - | [For signals A/A-/B/B-] AABB |  | [AB Encoder type] (ENS) | [Encoder configuration] (IEN)
ENU | Encoder usage | 16#15E6 = 5606 | 16#201A/7 | 16#7D/01/07 = 125/01/07 | ENU | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Encoder usage] (ENU) | [Encoder configuration] (IEN)
ENC | Encoder check | 16#15E5 = 5605 | 16#201A/6 | 16#7D/01/06 = 125/01/06 | ENC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Encoder check not done] NO |  | [Encoder check] (ENC) | [Encoder configuration] (IEN)
ECC | Encoder coupling monitoring | 16#15E7 = 5607 | 16#201A/8 | 16#7D/01/08 = 125/01/08 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Encoder Coupling Monit] (ECC) | [Encoder monitoring] (SDD)
ECT | Encoder check time | 16#15E9 = 5609 | 16#201A/A | 16#7D/01/0A = 125/01/10 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 2.0 s | 2.0 s ... 10.0 s | [Encoder check time] (ECT) | [Encoder monitoring] (SDD)
RPPN | Resolver poles nbr | 16#15ED = 5613 | 16#201A/E | 16#7D/01/0E = 125/01/14 | RPPN | Configuration and settings | R/WS | WORD (Enumeration) | - | [2 poles] 2P |  | [Resolver poles nbr] (RPPN) | [Encoder configuration] (IEN)
FRES | Resolver excitation frequency | 16#15EE = 5614 | 16#201A/F | 16#7D/01/0F = 125/01/15 | FRES | Configuration and settings | R/WS | WORD (Enumeration) | - | [8kHz] 8K
UECP | Encoder type | 16#15EF = 5615 | 16#201A/10 | 16#7D/01/10 = 125/01/16 | UECP | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Encoder Type] (UECP) | [Encoder configuration] (IEN)
UECV | Encoder supply voltage | 16#15F0 = 5616 | 16#201A/11 | 16#7D/01/11 = 125/01/17 | UECV | Configuration and settings | R/WS | WORD (Enumeration) | - | [Undefined] UND |  | [Encoder supply volt.] (UECV) | [Encoder configuration] (IEN)
ENRI | Inversion of encoder rotation direction | 16#15F2 = 5618 | 16#201A/13 | 16#7D/01/13 = 125/01/19 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Encoder rotation inv.] (ENRI) | [Encoder configuration] (IEN)
FFA | Encoder feeback filter activation | 16#15FE = 5630 | 16#201A/1F | 16#7D/01/1F = 125/01/31 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Encoder filter activ.] (FFA) | [Spd Loop Optimization] (MCL) [Encoder configuration] (IEN)
FFR | Encoder feedback filter value | 16#15FF = 5631 | 16#201A/20 | 16#7D/01/20 = 125/01/32 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 ms | Refer to programming manual | 0.0 ms ... 40.0 ms | [Encoder filter value] (FFR) | [Spd Loop Optimization] (MCL) [Encoder configuration] (IEN)
ULT | Underload detection delay | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Unld Detect Delay] (ULT) | [Process underload] (ULD)
SRB | Hysteresis frequency | 16#3841 = 14401 | 16#2072/2 | 16#A9/01/02 = 169/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.3 Hz ... 599.0 Hz | [Hysteresis Freq] (SRB) | [Settings] (SET) [Process underload] (ULD) [Process overload] (OLD)
UDL | Response to underload error | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Underload ErrorResp] (UDL) | [Process underload] (ULD)
RMUD | Unld. Freq.Thr. Detection | 16#384E = 14414 | 16#2072/F | 16#A9/01/0F = 169/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Unld. FreqThr. Det.] (RMUD) | [Settings] (SET) [Process underload] (ULD)
LUL | Unld.Thr. at O speed | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Unld.Thr.0.Speed] (LUL) | [Settings] (SET) [Process underload] (ULD)
LUN | Unld.Thr. at Nom. speed | 16#3850 = 14416 | 16#2072/11 | 16#A9/01/11 = 169/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 60 % | 20 % ... 100 % | [Unld.Thr.Nom.Speed] (LUN) | [Settings] (SET) [Process underload] (ULD)
TOL | Overload detection delay | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Ovld Detection Delay] (TOL) | [Process overload] (OLD)
ODL | Response to overload error | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Overload ErrorResp] (ODL) | [Process overload] (OLD)
STOS | Safe torque Off function Status | 16#3BDA = 15322 | 16#207B/17 | 16#AD/01/7B = 173/01/123 | STOS | Safety function | R | WORD (Enumeration) | -
ACCP | PID acceleration time | 16#2ED1 = 11985 | 16#2059/56 | 16#9C/01/BA = 156/01/186 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [PID acceleration time] (ACCP) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
AI1I | AI1 input physical image (MAX = 8192) | 16#1466 = 5222 | 16#2016/17 | 16#7B/01/17 = 123/01/23 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2I | AI2 input physical image (MAX = 8192) | 16#1467 = 5223 | 16#2016/18 | 16#7B/01/18 = 123/01/24 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3I | AI3 input physical image (MAX = 8192) | 16#1468 = 5224 | 16#2016/19 | 16#7B/01/19 = 123/01/25 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI4C | Physical value AI4 | 16#147D = 5245 | 16#2016/2E | 16#7B/01/2E = 123/01/46 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI4E | AI4 intermediate point X | 16#1171 = 4465 | 16#200E/42 | 16#77/01/42 = 119/01/66 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 X Interm. point] (AI4E) | [AI4 configuration] (AI4)
AI4F | AI4 filter | 16#1167 = 4455 | 16#200E/38 | 16#77/01/38 = 119/01/56 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI4 filter] (AI4F) | [AI4] (AI4C) [AI4 configuration] (AI4)
AI4I | AI4 input physical image (MAX = 8192) | 16#1469 = 5225 | 16#2016/1A | 16#7B/01/1A = 123/01/26 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI4R | Analog input 4 standardized value | 16#1473 = 5235 | 16#2016/24 | 16#7B/01/24 = 123/01/36 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI4S | AI4 intermediate point Y | 16#117B = 4475 | 16#200E/4C | 16#77/01/4C = 119/01/76 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 Y Interm.point] (AI4S) | [AI4 configuration] (AI4)
AI4T | Configuration of AI4 | 16#1135 = 4405 | 16#200E/6 | 16#77/01/06 = 119/01/06 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AI4 Type] (AI4T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
AI5C | Physical value AI5 | 16#147E = 5246 | 16#2016/2F | 16#7B/01/2F = 123/01/47 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI5E | AI5 intermediate point X | 16#1172 = 4466 | 16#200E/43 | 16#77/01/43 = 119/01/67 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 X Interm. point] (AI5E) | [AI5 configuration] (AI5)
AI5F | AI5 filter | 16#1168 = 4456 | 16#200E/39 | 16#77/01/39 = 119/01/57 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI5 filter] (AI5F) | [AI5] (AI5C) [AI5 configuration] (AI5)
AI5I | AI5 input physical image (MAX = 8192) | 16#146A = 5226 | 16#2016/1B | 16#7B/01/1B = 123/01/27 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI5R | Analog input 5 standardized value | 16#1474 = 5236 | 16#2016/25 | 16#7B/01/25 = 123/01/37 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI5S | AI5 delinearization output level | 16#117C = 4476 | 16#200E/4D | 16#77/01/4D = 119/01/77 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 Y Interm.point] (AI5S) | [AI5 configuration] (AI5)
AI5T | Configuration of AI5 | 16#1136 = 4406 | 16#200E/7 | 16#77/01/07 = 119/01/07 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AI5 Type] (AI5T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
AIC1 | Channel assignment for virtual Analog input AIV1 | 16#14A2 = 5282 | 16#2016/53 | 16#7B/01/53 = 123/01/83 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [AIV1 Channel Assign] (AIC1) | [Virtual AI1] (AV1)
AO1I | AO1 output physical image (MAX = 8192) | 16#1483 = 5251 | 16#2016/34 | 16#7B/01/34 = 123/01/52 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO2 | AQ2 assignment | 16#139E = 5022 | 16#2014/17 | 16#7A/01/17 = 122/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor current] OCR |  | [AQ2 assignment] (AO2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
AO2C | AQ2 physical value | 16#1498 = 5272 | 16#2016/49 | 16#7B/01/49 = 123/01/73 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AO2F | AQ2 filter | 16#1204 = 4612 | 16#2010/D | 16#78/01/0D = 120/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ2 Filter] (AO2F) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
AO2I | AO2 output physical image (MAX = 8192) | 16#1484 = 5252 | 16#2016/35 | 16#7B/01/35 = 123/01/53 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO2R | Analog output 2 standardized value | 16#148E = 5262 | 16#2016/3F | 16#7B/01/3F = 123/01/63 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AO2T | AQ2 Type | 16#11FA = 4602 | 16#2010/3 | 16#78/01/03 = 120/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AQ2 Type] (AO2T) | [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
AOH2 | AQ2 max output value | 16#122C = 4652 | 16#2010/35 | 16#78/01/35 = 120/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ2 max output] (AOH2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
AOL2 | AQ2 min output value | 16#1222 = 4642 | 16#2010/2B | 16#78/01/2B = 120/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ2 min output] (AOL2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
APPS | Application state | 16#3E6C = 15980 | 16#2081/51 | 16#B0/01/B5 = 176/01/181 | APPS | Status parameters | R | WORD (Enumeration) | - |  |  | [Application state] (APPS) | [Application Parameters] (APR)
ASH2 | Scaling AQ2 max | 16#1240 = 4672 | 16#2010/49 | 16#78/01/49 = 120/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 Max] (ASH2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
ASL2 | Scaling AQ2 min | 16#1236 = 4662 | 16#2010/3F | 16#78/01/3F = 120/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 Min] (ASL2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
CAR | Customer warning clearing | 16#3F98 = 16280 | 16#2084/51 | 16#B2/01/51 = 178/01/81 | CAR | Configuration and settings | R/W | WORD (Enumeration) | - | [No warning clearing] NO |  | [Warning Clearing] (CAR) | [Customer events] (CUEV)
CASH | Money saved | 16#2A36 = 10806 | 16#204E/7 | 16#97/01/07 = 151/01/07 |  | Actual values parameters | R | UINT (Unsigned32) | Refer to programming manual |  | 0 ... 4294967295 | [Money Saved] (CASH) | [Energy Saving] (ESA)
CC1 | Time counter 1 | 16#3F84 = 16260 | 16#2084/3D | 16#B2/01/3D = 178/01/61 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 1] (CC1) | [Customer event 1] (CE1)
CC2 | Time counter 2 | 16#3F86 = 16262 | 16#2084/3F | 16#B2/01/3F = 178/01/63 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 2] (CC2) | [Customer event 2] (CE2)
CC3 | Time counter 3 | 16#3F88 = 16264 | 16#2084/41 | 16#B2/01/41 = 178/01/65 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 3] (CC3) | [Customer event 3] (CE3)
CC4 | Time counter 4 | 16#3F8A = 16266 | 16#2084/43 | 16#B2/01/43 = 178/01/67 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 4] (CC4) | [Customer event 4] (CE4)
CC5 | Time counter 5 | 16#3F8C = 16268 | 16#2084/45 | 16#B2/01/45 = 178/01/69 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 5] (CC5) | [Customer event 5] (CE5)
CCA1 | Configuration of customer warning 1 | 16#3F48 = 16200 | 16#2084/1 | 16#B2/01/01 = 178/01/01 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 1] (CCA1) | [Customer event 1] (CE1)
CCA2 | Configuration of customer warning 2 | 16#3F49 = 16201 | 16#2084/2 | 16#B2/01/02 = 178/01/02 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 2] (CCA2) | [Customer event 2] (CE2)
CCA3 | Configuration of customer warning 3 | 16#3F4A = 16202 | 16#2084/3 | 16#B2/01/03 = 178/01/03 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 3] (CCA3) | [Customer event 3] (CE3)
CCA4 | Configuration of customer warning 4 | 16#3F4B = 16203 | 16#2084/4 | 16#B2/01/04 = 178/01/04 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 4] (CCA4) | [Customer event 4] (CE4)
CCA5 | Configuration of customer warning 5 | 16#3F4C = 16204 | 16#2084/5 | 16#B2/01/05 = 178/01/05 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 5] (CCA5) | [Customer event 5] (CE5)
CCL1 | Configuration counter limit 1 | 16#3F70 = 16240 | 16#2084/29 | 16#B2/01/29 = 178/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 1] (CCL1) | [Customer event 1] (CE1)
CCL2 | Configuration counter limit 2 | 16#3F72 = 16242 | 16#2084/2B | 16#B2/01/2B = 178/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 2] (CCL2) | [Customer event 2] (CE2)
CCL3 | Configuration counter limit 3 | 16#3F74 = 16244 | 16#2084/2D | 16#B2/01/2D = 178/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 3] (CCL3) | [Customer event 3] (CE3)
CCL4 | Configuration counter limit 4 | 16#3F76 = 16246 | 16#2084/2F | 16#B2/01/2F = 178/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 4] (CCL4) | [Customer event 4] (CE4)
CCL5 | Configuration counter limit 5 | 16#3F78 = 16248 | 16#2084/31 | 16#B2/01/31 = 178/01/49 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 5] (CCL5) | [Customer event 5] (CE5)
CCS1 | Configuration counter Source 1 | 16#3F52 = 16210 | 16#2084/B | 16#B2/01/0B = 178/01/11 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in running State] 2 |  | [Counter Source 1] (CCS1) | [Customer event 1] (CE1)
CCS2 | Configuration counter Source 2 | 16#3F53 = 16211 | 16#2084/C | 16#B2/01/0C = 178/01/12 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in running State] 2 |  | [Counter Source 2] (CCS2) | [Customer event 2] (CE2)
CCS3 | Configuration counter Source 3 | 16#3F54 = 16212 | 16#2084/D | 16#B2/01/0D = 178/01/13 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in running State] 2 |  | [Counter Source 3] (CCS3) | [Customer event 3] (CE3)
CCS4 | Configuration counter Source 4 | 16#3F55 = 16213 | 16#2084/E | 16#B2/01/0E = 178/01/14 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in running State] 2 |  | [Counter Source 4] (CCS4) | [Customer event 4] (CE4)
CCS5 | Configuration counter Source 5 | 16#3F56 = 16214 | 16#2084/F | 16#B2/01/0F = 178/01/15 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in running State] 2 |  | [Counter Source 5] (CCS5) | [Customer event 5] (CE5)
CDT1 | Date time warning 1 | 16#3F5C = 16220 | 16#2084/15 | 16#B2/01/15 = 178/01/21 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT2 | Date time warning 2 | 16#3F5E = 16222 | 16#2084/17 | 16#B2/01/17 = 178/01/23 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT3 | Date time warning 3 | 16#3F60 = 16224 | 16#2084/19 | 16#B2/01/19 = 178/01/25 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT4 | Date time warning 4 | 16#3F62 = 16226 | 16#2084/1B | 16#B2/01/1B = 178/01/27 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT5 | Date time warning 5 | 16#3F64 = 16228 | 16#2084/1D | 16#B2/01/1D = 178/01/29 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CMP9 | Cmd word | 16#1C47 = 7239 | 16#202A/28 | 16#85/01/28 = 133/01/40 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP9) | [None] (DP9)
CMPA | Cmd word | 16#1DCE = 7630 | 16#202E/1F | 16#87/01/1F = 135/01/31 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPA) | [None] (DPA)
CMPB | Cmd word | 16#1DCF = 7631 | 16#202E/20 | 16#87/01/20 = 135/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPB) | [None] (DPB)
CMPC | CMD command word | 16#1DD0 = 7632 | 16#202E/21 | 16#87/01/21 = 135/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPC) | [None] (DPC)
CMPD | CMD command word | 16#1DD1 = 7633 | 16#202E/22 | 16#87/01/22 = 135/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPD) | [None] (DPD)
CMPE | CMD command word | 16#1DD2 = 7634 | 16#202E/23 | 16#87/01/23 = 135/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPE) | [None] (DPE)
CMPF | CMD command word | 16#1DD3 = 7635 | 16#202E/24 | 16#87/01/24 = 135/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPF) | [None] (DPF)
CO2S | Co2 Saved | 16#2A38 = 10808 | 16#204E/9 | 16#97/01/09 = 151/01/09 |  | Actual values parameters | R | UINT (Unsigned32) | 0.1 t |  | 0.0 t ... 429496729.5 t | [Co2 Saved] (CO2S) | [Energy Saving] (ESA)
CRH1 | AI1 current scaling parameter of 100% | 16#115A = 4442 | 16#200E/2B | 16#77/01/2B = 119/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI1 Max Value] (CRH1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
CRH4 | AI4 current scaling parameter of 100% | 16#115D = 4445 | 16#200E/2E | 16#77/01/2E = 119/01/46 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI4 Max Value] (CRH4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
CRH5 | AI5 current scaling parameter of 100% | 16#115E = 4446 | 16#200E/2F | 16#77/01/2F = 119/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI5 Max Value] (CRH5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
CRL1 | AI1 current scaling parameter of 0% | 16#1150 = 4432 | 16#200E/21 | 16#77/01/21 = 119/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI1 Min. Value] (CRL1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
CRL4 | AI4 current scaling parameter of 0% | 16#1153 = 4435 | 16#200E/24 | 16#77/01/24 = 119/01/36 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI4 Min. Value] (CRL4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
CRL5 | AI5 current scaling parameter of 0% | 16#1154 = 4436 | 16#200E/25 | 16#77/01/25 = 119/01/37 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI5 Min. Value] (CRL5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
CRP9 | Active channels on error n-9 | 16#1C83 = 7299 | 16#202A/64 | 16#85/01/64 = 133/01/100 |  | History parameters | R | WORD (BitString16) | -
CRPA | Active channels on error n-10 | 16#1E0A = 7690 | 16#202E/5B | 16#87/01/5B = 135/01/91 |  | History parameters | R | WORD (BitString16) | -
CRPB | Active channels on error n-11 | 16#1E0B = 7691 | 16#202E/5C | 16#87/01/5C = 135/01/92 |  | History parameters | R | WORD (BitString16) | -
CRPC | Active channels on error n-12 | 16#1E0C = 7692 | 16#202E/5D | 16#87/01/5D = 135/01/93 |  | History parameters | R | WORD (BitString16) | -
CRPD | Active channels on error n-13 | 16#1E0D = 7693 | 16#202E/5E | 16#87/01/5E = 135/01/94 |  | History parameters | R | WORD (BitString16) | -
CRPE | Active channels on error n-14 | 16#1E0E = 7694 | 16#202E/5F | 16#87/01/5F = 135/01/95 |  | History parameters | R | WORD (BitString16) | -
CRPF | Active channels on error n-15 | 16#1E0F = 7695 | 16#202E/60 | 16#87/01/60 = 135/01/96 |  | History parameters | R | WORD (BitString16) | -
CTDL | Low current threshold | 16#2B02 = 11010 | 16#2050/B | 16#98/01/0B = 152/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Low I Threshold] (CTDL) | [Threshold reached] (THRE) [Settings] (SET)
D11D | DQ11 activation delay | 16#10BB = 4283 | 16#200C/54 | 16#76/01/54 = 118/01/84 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ11 actv delay] (D11D) | [DQ11 Configuration] (DO11)
D11H | DQ11 holding delay | 16#10B1 = 4273 | 16#200C/4A | 16#76/01/4A = 118/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ11 hold delay] (D11H) | [DQ11 Configuration] (DO11)
D11S | DQ11 status (output active level) | 16#10A7 = 4263 | 16#200C/40 | 16#76/01/40 = 118/01/64 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [DQ11 status] (D11S) | [DQ11 Configuration] (DO11)
D12D | DQ12 activation delay | 16#10BC = 4284 | 16#200C/55 | 16#76/01/55 = 118/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ12 actv delay] (D12D) | [DQ12 Configuration] (DO12)
D12H | DQ12 holding delay | 16#10B2 = 4274 | 16#200C/4B | 16#76/01/4B = 118/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ12 hold delay] (D12H) | [DQ12 Configuration] (DO12)
D12S | DQ12 status (output active level) | 16#10A8 = 4264 | 16#200C/41 | 16#76/01/41 = 118/01/65 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [DQ12 status] (D12S) | [DQ12 Configuration] (DO12)
DM0 | Hour and minute of actual fault | 16#1C8E = 7310 | 16#202B/B | 16#85/01/6F = 133/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM1 | Hour and minute of fault record x (1 is last) | 16#1C8F = 7311 | 16#202B/C | 16#85/01/70 = 133/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM2 | Hour and minute of fault record x (1 is last) | 16#1C90 = 7312 | 16#202B/D | 16#85/01/71 = 133/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM3 | Hour and minute of fault record x (1 is last) | 16#1C91 = 7313 | 16#202B/E | 16#85/01/72 = 133/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM4 | Hour and minute of fault record x (1 is last) | 16#1C92 = 7314 | 16#202B/F | 16#85/01/73 = 133/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM5 | Hour and minute of fault record x (1 is last) | 16#1C93 = 7315 | 16#202B/10 | 16#85/01/74 = 133/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM6 | Hour and minute of fault record x (1 is last) | 16#1C94 = 7316 | 16#202B/11 | 16#85/01/75 = 133/01/117 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM7 | Hour and minute of fault record x (1 is last) | 16#1C95 = 7317 | 16#202B/12 | 16#85/01/76 = 133/01/118 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM8 | Hour and minute of fault record x (1 is last) | 16#1C96 = 7318 | 16#202B/13 | 16#85/01/77 = 133/01/119 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM9 | Hour and minute of fault record x (1 is last) | 16#1C97 = 7319 | 16#202B/14 | 16#85/01/78 = 133/01/120 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMA | Hour and minute of fault record x (1 is last) | 16#1E1E = 7710 | 16#202F/B | 16#87/01/6F = 135/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMB | Hour and minute of fault record x (1 is last) | 16#1E1F = 7711 | 16#202F/C | 16#87/01/70 = 135/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMC | Hour and minute of fault record x (1 is last) | 16#1E20 = 7712 | 16#202F/D | 16#87/01/71 = 135/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMD | Hour and minute of fault record x (1 is last) | 16#1E21 = 7713 | 16#202F/E | 16#87/01/72 = 135/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DME | Hour and minute of fault record x (1 is last) | 16#1E22 = 7714 | 16#202F/F | 16#87/01/73 = 135/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMF | Hour and minute of fault record x (1 is last) | 16#1E23 = 7715 | 16#202F/10 | 16#87/01/74 = 135/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DO11 | DO11 assignment | 16#13A9 = 5033 | 16#2014/22 | 16#7A/01/22 = 122/01/34 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ11 assignment] (DO11) | [DQ11 Configuration] (DO11)
DO12 | DO12 assignment | 16#13AA = 5034 | 16#2014/23 | 16#7A/01/23 = 122/01/35 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ12 assignment] (DO12) | [DQ12 Configuration] (DO12)
DP9 | Last error 9 | 16#1C29 = 7209 | 16#202A/A | 16#85/01/0A = 133/01/10 | LFT | History parameters | R | WORD (Enumeration) | -
DPA | Last error 10 | 16#1DB0 = 7600 | 16#202E/1 | 16#87/01/01 = 135/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
DPB | Last error 11 | 16#1DB1 = 7601 | 16#202E/2 | 16#87/01/02 = 135/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
DPC | Last error 12 | 16#1DB2 = 7602 | 16#202E/3 | 16#87/01/03 = 135/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
DPD | Last error 13 | 16#1DB3 = 7603 | 16#202E/4 | 16#87/01/04 = 135/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
DPE | Last error 14 | 16#1DB4 = 7604 | 16#202E/5 | 16#87/01/05 = 135/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
DPF | Last error 15 | 16#1DB5 = 7605 | 16#202E/6 | 16#87/01/06 = 135/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
DRT | Dual rating state | 16#0BC2 = 3010 | 16#2000/B | 16#70/01/0B = 112/01/11 | DRT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Normal duty] NORMAL |  | [Dual rating] (DRT) | [Motor parameters] (MPA)
ECO2 | CO2 ratio | 16#2A32 = 10802 | 16#204E/3 | 16#97/01/03 = 151/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.001 kg/kWh | 0.000 kg/kWh | 0.000 kg/kWh ... 65.535 kg/kWh | [CO2 ratio] (ECO2) | [Energy Saving] (ESA)
ECST | kWh Cost | 16#2A31 = 10801 | 16#204E/2 | 16#97/01/02 = 151/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [kWh Cost] (ECST) | [Energy Saving] (ESA)
EP9 | State word | 16#1C33 = 7219 | 16#202A/14 | 16#85/01/14 = 133/01/20 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP9) | [None] (DP9)
EPA | State word | 16#1DBA = 7610 | 16#202E/B | 16#87/01/0B = 135/01/11 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPA) | [None] (DPA)
EPB | State word | 16#1DBB = 7611 | 16#202E/C | 16#87/01/0C = 135/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPB) | [None] (DPB)
EPC | State word | 16#1DBC = 7612 | 16#202E/D | 16#87/01/0D = 135/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPC) | [None] (DPC)
EPD | State word | 16#1DBD = 7613 | 16#202E/E | 16#87/01/0E = 135/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPD) | [None] (DPD)
EPE | State word | 16#1DBE = 7614 | 16#202E/F | 16#87/01/0F = 135/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPE) | [None] (DPE)
EPF | State word | 16#1DBF = 7615 | 16#202E/10 | 16#87/01/10 = 135/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPF) | [None] (DPF)
EPRW | Active Electrical output power in kW | 16#0CDD = 3293 | 16#2002/5E | 16#71/01/5E = 113/01/94 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Acv Elc Out Pwr in kW] (EPRW) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO) [Variable Speed Pump] (MPP)
ERR | Ethernet error Code | 16#FB0E = 64270 |  |  |  | Fault parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ESAV | Energy Saved | 16#2A34 = 10804 | 16#204E/5 | 16#97/01/05 = 151/01/05 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Energy Saved] (ESAV) | [Energy Saving] (ESA)
ETAD | DRIVECOM : Status word | 16#219B = 8603 | 16#2038/4 | 16#8C/01/04 = 140/01/04 |  | Status parameters | R | WORD (BitString16) | -
ETHF | Ethernet embedded fault (ETHF) | 16#1BE0 = 7136 | 16#2029/25 | 16#84/01/89 = 132/01/137 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
ETHL | Ethernet error response | 16#1B6D = 7021 | 16#2028/16 | 16#84/01/16 = 132/01/22 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Eth Error Response] (ETHL) | [Embedded modbus TCP] (EMTC) [Communication Module] (COMO)
F2DL | 2 frequency threshold | 16#2B04 = 11012 | 16#2050/D | 16#98/01/0D = 152/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [2 Freq. Threshold] (F2DL) | [Threshold reached] (THRE) [Settings] (SET)
FPBT | Fan operation time | 16#0CC0 = 3264 | 16#2002/41 | 16#71/01/41 = 113/01/65 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [Fan Operation Time] (FPBT) | [Counter Management] (ELT)
FSPD | Fan speed | 16#0CBF = 3263 | 16#2002/40 | 16#71/01/40 = 113/01/64 |  | Measurement parameters | R | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
FTDL | Low Freq. threshold | 16#2B03 = 11011 | 16#2050/C | 16#98/01/0C = 152/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Low Freq.Threshold] (FTDL) | [Threshold reached] (THRE) [Settings] (SET)
FTO | Ovld time Before Restart | 16#3857 = 14423 | 16#2072/18 | 16#A9/01/18 = 169/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Overload T.B.Rest.] (FTO) | [Settings] (SET) [Process overload] (OLD)
FTU | Unld time Before Restart | 16#384D = 14413 | 16#2072/E | 16#A9/01/0E = 169/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Underload T.B.Rest.] (FTU) | [Settings] (SET) [Process underload] (ULD)
GRFL | Ground fault activation | 16#1B76 = 7030 | 16#2028/1F | 16#84/01/1F = 132/01/31 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 % | -0.1 % | -0.2 % ... 100.0 % | [Ground Fault Activation] (GRFL) | [Ground Fault] (GRFL)
HS9 | Device state | 16#1CA1 = 7329 | 16#202B/1E | 16#85/01/82 = 133/01/130 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HS9) | [None] (DP9)
HSA | Device state | 16#1E28 = 7720 | 16#202F/15 | 16#87/01/79 = 135/01/121 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSA) | [None] (DPA)
HSB | Device state | 16#1E29 = 7721 | 16#202F/16 | 16#87/01/7A = 135/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSB) | [None] (DPB)
HSC | Device state | 16#1E2A = 7722 | 16#202F/17 | 16#87/01/7B = 135/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSC) | [None] (DPC)
HSD | Device state | 16#1E2B = 7723 | 16#202F/18 | 16#87/01/7C = 135/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSD) | [None] (DPD)
HSE | Device state | 16#1E2C = 7724 | 16#202F/19 | 16#87/01/7D = 135/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSE) | [None] (DPE)
HSF | Device state | 16#1E2D = 7725 | 16#202F/1A | 16#87/01/7E = 135/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSF) | [None] (DPF)
IC0 | Input Energy (Wh) | 16#2982 = 10626 | 16#204C/1B | 16#96/01/1B = 150/01/27 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh
IC1 | Input Energy (kWh) | 16#2983 = 10627 | 16#204C/1C | 16#96/01/1C = 150/01/28 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh
IC2 | Input Energy (MWh) | 16#2984 = 10628 | 16#204C/1D | 16#96/01/1D = 150/01/29 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh
IC3 | Input Energy (GWh) | 16#2985 = 10629 | 16#204C/1E | 16#96/01/1E = 150/01/30 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh
IC4 | Input Energy (TWh) | 16#2986 = 10630 | 16#204C/1F | 16#96/01/1F = 150/01/31 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh
IDLS | Energy Saving input assignment | 16#3624 = 13860 | 16#206C/3D | 16#A6/01/3D = 166/01/61 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Energy Saving Assign] (IDLS) | [Stop and Go] (STG)
IE0 | Real input Energy (Wh) | 16#298C = 10636 | 16#204C/25 | 16#96/01/25 = 150/01/37 |  | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Input Energy] (IE0) | [Elec Ener Input Counter] (ELI)
IE1 | Real input Energy (kWh) | 16#298D = 10637 | 16#204C/26 | 16#96/01/26 = 150/01/38 |  | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Input Energy] (IE1) | [Elec Ener Input Counter] (ELI)
IE2 | Real input Energy (MWh) | 16#298E = 10638 | 16#204C/27 | 16#96/01/27 = 150/01/39 |  | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Input Energy] (IE2) | [Elec Ener Input Counter] (ELI)
IE3 | Real input Energy (GWh) | 16#298F = 10639 | 16#204C/28 | 16#96/01/28 = 150/01/40 |  | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Input Energy] (IE3) | [Elec Ener Input Counter] (ELI)
IE4 | Real input Energy (TWh) | 16#2990 = 10640 | 16#204C/29 | 16#96/01/29 = 150/01/41 |  | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Input Energy] (IE4) | [Elec Ener Input Counter] (ELI)
IL1I | Logic inputs physical image | 16#1451 = 5201 | 16#2016/2 | 16#7B/01/02 = 123/01/02 |  | I/O parameters | R | WORD (BitString16) | -
INRC | NCR current scaling | 16#2649 = 9801 | 16#2044/2 | 16#92/01/02 = 146/01/02 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRL | LFA inductance scaling | 16#264C = 9804 | 16#2044/5 | 16#92/01/05 = 146/01/05 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRP | NPR power scaling | 16#264A = 9802 | 16#2044/3 | 16#92/01/03 = 146/01/03 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRR | RSA resistance scaling | 16#264B = 9803 | 16#2044/4 | 16#92/01/04 = 146/01/04 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRT | Torque scaling | 16#264D = 9805 | 16#2044/6 | 16#92/01/06 = 146/01/06 | CINR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque Scaling] (INRT) | [data] (MTD)
INTI | TRA time scaling | 16#264E = 9806 | 16#2044/7 | 16#92/01/07 = 146/01/07 | CINR | Configuration and settings | R | WORD (Enumeration) | -
IP9 | ETI state word | 16#1C3D = 7229 | 16#202A/1E | 16#85/01/1E = 133/01/30 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP9) | [None] (DP9)
IPA | ETI state word | 16#1DC4 = 7620 | 16#202E/15 | 16#87/01/15 = 135/01/21 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPA) | [None] (DPA)
IPAD | iPar detected error code | 16#FB18 = 64280 |  |  |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [iPar Error Code] (IPAD) | [Profinet diag] (PRN)
IPB | ETI state word | 16#1DC5 = 7621 | 16#202E/16 | 16#87/01/16 = 135/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPB) | [None] (DPB)
IPC | ETI state word | 16#1DC6 = 7622 | 16#202E/17 | 16#87/01/17 = 135/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPC) | [None] (DPC)
IPD | ETI state word | 16#1DC7 = 7623 | 16#202E/18 | 16#87/01/18 = 135/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPD) | [None] (DPD)
IPE | ETI state word | 16#1DC8 = 7624 | 16#202E/19 | 16#87/01/19 = 135/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPE) | [None] (DPE)
IPF | ETI state word | 16#1DC9 = 7625 | 16#202E/1A | 16#87/01/1A = 135/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPF) | [None] (DPF)
IPR | Active Electrical input power estimation (100% = drive power) | 16#0C92 = 3218 | 16#2002/13 | 16#71/01/13 = 113/01/19 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | 0 % ... 65535 %
IPRW | Instantaneous active input power | 16#0CDE = 3294 | 16#2002/5F | 16#71/01/5F = 113/01/95 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Active Input Power] (IPRW) | [Elec Ener Input Counter] (ELI)
L11D | DI11 delay | 16#0FAB = 4011 | 16#200A/C | 16#75/01/0C = 117/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI11 Delay] (L11D) | [DI11 Configuration] (DI11)
L12D | DI12 delay | 16#0FAC = 4012 | 16#200A/D | 16#75/01/0D = 117/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI12 Delay] (L12D) | [DI12 Configuration] (DI12)
L13D | DI13 delay | 16#0FAD = 4013 | 16#200A/E | 16#75/01/0E = 117/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI13 Delay] (L13D) | [DI13 Configuration] (DI13)
L14D | DI14 delay | 16#0FAE = 4014 | 16#200A/F | 16#75/01/0F = 117/01/15 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI14 Delay] (L14D) | [DI14 Configuration] (DI14)
L15D | DI15 delay | 16#0FAF = 4015 | 16#200A/10 | 16#75/01/10 = 117/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI15 Delay] (L15D) | [DI15 Configuration] (DI15)
L16D | DI16 delay | 16#0FB0 = 4016 | 16#200A/11 | 16#75/01/11 = 117/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI16 Delay] (L16D) | [DI16 Configuration] (DI16)
LALR | Last warning | 16#325A = 12890 | 16#2062/5B | 16#A1/01/5B = 161/01/91 | ALR | Actual values parameters | R | WORD (Enumeration) | - |  |  | [Last Warning] (LALR) | [Diag. data] (DDT)
LCAC | Lifecycle warning configuration | 16#3598 = 13720 | 16#206B/15 | 16#A5/01/79 = 165/01/121 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [LifeCycle Warning] (LCAC) | [Drive warranty mgnt] (DWMA)
LCAD | Life cycle Date | 16#3599 = 13721 | 16#206B/16 | 16#A5/01/7A = 165/01/122 |  | Actual values parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Warranty expired] (LCAD) | [Drive warranty mgnt] (DWMA)
LCP9 | Motor current | 16#1C51 = 7249 | 16#202A/32 | 16#85/01/32 = 133/01/50 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP9) | [None] (DP9)
LCPA | Motor current | 16#1DD8 = 7640 | 16#202E/29 | 16#87/01/29 = 135/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPA) | [None] (DPA)
LCPB | Motor current | 16#1DD9 = 7641 | 16#202E/2A | 16#87/01/2A = 135/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPB) | [None] (DPB)
LCPC | Motor current | 16#1DDA = 7642 | 16#202E/2B | 16#87/01/2B = 135/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPC) | [None] (DPC)
LCPD | Motor current | 16#1DDB = 7643 | 16#202E/2C | 16#87/01/2C = 135/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPD) | [None] (DPD)
LCPE | Motor current | 16#1DDC = 7644 | 16#202E/2D | 16#87/01/2D = 135/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPE) | [None] (DPE)
LCPF | Motor current | 16#1DDD = 7645 | 16#202E/2E | 16#87/01/2E = 135/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPF) | [None] (DPF)
LDD1 | Log Distribution Data 1 | 16#4010 = 16400 | 16#2086/1 | 16#B3/01/01 = 179/01/01 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 1] (LDD1) | [Log dstrb prm select] (LDP)
LDD2 | Log Distribution Data 2 | 16#4012 = 16402 | 16#2086/3 | 16#B3/01/03 = 179/01/03 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 2] (LDD2) | [Log dstrb prm select] (LDP)
LDD3 | Log Distribution Data 3 | 16#4014 = 16404 | 16#2086/5 | 16#B3/01/05 = 179/01/05 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 3] (LDD3) | [Log dstrb prm select] (LDP)
LDD4 | Log Distribution Data 4 | 16#4016 = 16406 | 16#2086/7 | 16#B3/01/07 = 179/01/07 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 4] (LDD4) | [Log dstrb prm select] (LDP)
LDEN | Logging Distribution State | 16#4019 = 16409 | 16#2086/A | 16#B3/01/0A = 179/01/10 | LDEN | Configuration and settings | R/W | WORD (Enumeration) | - | [Stop] STOP |  | [Log Distrib State] (LDEN) | [Distributed logging] (DLO)
LDM1 | Distribution data max value 1 | 16#4011 = 16401 | 16#2086/2 | 16#B3/01/02 = 179/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 1] (LDM1) | [Distributed logging] (DLO)
LDM2 | Distribution data max value 2 | 16#4013 = 16403 | 16#2086/4 | 16#B3/01/04 = 179/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 2] (LDM2) | [Distributed logging] (DLO)
LDM3 | Distribution data max value 3 | 16#4015 = 16405 | 16#2086/6 | 16#B3/01/06 = 179/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 3] (LDM3) | [Distributed logging] (DLO)
LDM4 | Distribution data max value 4 | 16#4017 = 16407 | 16#2086/8 | 16#B3/01/08 = 179/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 4] (LDM4) | [Distributed logging] (DLO)
LDST | Logging Distribution Sample time | 16#4018 = 16408 | 16#2086/9 | 16#B3/01/09 = 179/01/09 | LDST | Configuration and settings | R/W | WORD (Enumeration) | - | [1 second] 1S |  | [Log Distrib Spl Time] (LDST) | [Distributed logging] (DLO)
LFL1 | Response to 4-20mA loss on AI1 | 16#1B69 = 7017 | 16#2028/12 | 16#84/01/12 = 132/01/18 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI1 4-20mA loss] (LFL1) | [4-20 mA loss] (LFL)
LFL4 | Response to 4-20mA loss on AI4 | 16#1B66 = 7014 | 16#2028/F | 16#84/01/0F = 132/01/15 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI4 4-20mA loss] (LFL4) | [4-20 mA loss] (LFL)
LFL5 | Response to 4-20mA loss on AI5 | 16#1B6B = 7019 | 16#2028/14 | 16#84/01/14 = 132/01/20 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI5 4-20mA loss] (LFL5) | [4-20 mA loss] (LFL)
LOC | Current overload threshold | 16#3859 = 14425 | 16#2072/1A | 16#A9/01/1A = 169/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 70 % ... 150 % | [Overload Threshold] (LOC) | [Settings] (SET) [Process overload] (OLD)
MD0 | Year, month and day of actual fault | 16#1C84 = 7300 | 16#202B/1 | 16#85/01/65 = 133/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD1 | Year, month and day of fault record x (1 is last) | 16#1C85 = 7301 | 16#202B/2 | 16#85/01/66 = 133/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD2 | Year, month and day of fault record x (1 is last) | 16#1C86 = 7302 | 16#202B/3 | 16#85/01/67 = 133/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD3 | Year, month and day of fault record x (1 is last) | 16#1C87 = 7303 | 16#202B/4 | 16#85/01/68 = 133/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD4 | Year, month and day of fault record x (1 is last) | 16#1C88 = 7304 | 16#202B/5 | 16#85/01/69 = 133/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD5 | Year, month and day of fault record x (1 is last) | 16#1C89 = 7305 | 16#202B/6 | 16#85/01/6A = 133/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD6 | Year, month and day of fault record x (1 is last) | 16#1C8A = 7306 | 16#202B/7 | 16#85/01/6B = 133/01/107 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD7 | Year, month and day of fault record x (1 is last) | 16#1C8B = 7307 | 16#202B/8 | 16#85/01/6C = 133/01/108 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD8 | Year, month and day of fault record x (1 is last) | 16#1C8C = 7308 | 16#202B/9 | 16#85/01/6D = 133/01/109 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD9 | Year, month and day of fault record x (1 is last) | 16#1C8D = 7309 | 16#202B/A | 16#85/01/6E = 133/01/110 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDA | Year, month and day of fault record x (1 is last) | 16#1E14 = 7700 | 16#202F/1 | 16#87/01/65 = 135/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDB | Year, month and day of fault record x (1 is last) | 16#1E15 = 7701 | 16#202F/2 | 16#87/01/66 = 135/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDC | Year, month and day of fault record x (1 is last) | 16#1E16 = 7702 | 16#202F/3 | 16#87/01/67 = 135/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDD | Year, month and day of fault record x (1 is last) | 16#1E17 = 7703 | 16#202F/4 | 16#87/01/68 = 135/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDE | Year, month and day of fault record x (1 is last) | 16#1E18 = 7704 | 16#202F/5 | 16#87/01/69 = 135/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDF | Year, month and day of fault record x (1 is last) | 16#1E19 = 7705 | 16#202F/6 | 16#87/01/6A = 135/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
ME0 | Motor energy consumption (Wh) | 16#2969 = 10601 | 16#204C/2 | 16#96/01/02 = 150/01/02 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Motor Consumption] (ME0) | [Mechanical Energy] (MEC)
ME1 | Motor energy consumption (kWh) | 16#296A = 10602 | 16#204C/3 | 16#96/01/03 = 150/01/03 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Motor Consumption] (ME1) | [Mechanical Energy] (MEC)
ME2 | Motor energy consumption (MWh) | 16#296B = 10603 | 16#204C/4 | 16#96/01/04 = 150/01/04 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Motor Consumption] (ME2) | [Mechanical Energy] (MEC)
ME3 | Motor energy consumption (GWh) | 16#296C = 10604 | 16#204C/5 | 16#96/01/05 = 150/01/05 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Motor Consumption] (ME3) | [Mechanical Energy] (MEC)
ME4 | Motor energy consumption (TWh) | 16#296D = 10605 | 16#204C/6 | 16#96/01/06 = 150/01/06 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Motor Consumption] (ME4) | [Mechanical Energy] (MEC)
MOEP | Peak electrical output power | 16#2991 = 10641 | 16#204C/2A | 16#96/01/2A = 150/01/42 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Peak Elec Out Power] (MOEP) | [Elec Ener Output Counter] (ELO)
NSM | Number of motor starts | 16#0CBC = 3260 | 16#2002/3D | 16#71/01/3D = 113/01/61 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Nb Of Starts] (NSM) | [Diag. data] (DDT) [Counter Management] (ELT) [Variable Speed Pump] (MPP)
OC0 | Electrical energy consumed by the motor (Wh) | 16#296E = 10606 | 16#204C/7 | 16#96/01/07 = 150/01/07 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Elc Energy Cons] (OC0) | [kWh Counters] (KWC)
OC1 | Electrical energy consumed by the motor (KWh) | 16#296F = 10607 | 16#204C/8 | 16#96/01/08 = 150/01/08 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Elc Energy Cons] (OC1) | [kWh Counters] (KWC)
OC2 | Electrical energy consumed by the motor (MWh) | 16#2970 = 10608 | 16#204C/9 | 16#96/01/09 = 150/01/09 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Elc Energy Cons] (OC2) | [kWh Counters] (KWC)
OC3 | Electrical energy consumed by the motor (GWh) | 16#2971 = 10609 | 16#204C/A | 16#96/01/0A = 150/01/10 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Elc Energy Cons] (OC3) | [kWh Counters] (KWC)
OC4 | Electrical energy consumed by the motor (TWh) | 16#2972 = 10610 | 16#204C/B | 16#96/01/0B = 150/01/11 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Elc Energy Cons] (OC4) | [kWh Counters] (KWC)
OCA7 | Scan output 7 address | 16#3C43 = 15427 | 16#207C/1C | 16#AE/01/1C = 174/01/28 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA8 | Scan output 8 address | 16#3C44 = 15428 | 16#207C/1D | 16#AE/01/1D = 174/01/29 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA9 | Scan output 9 address | 16#3C45 = 15429 | 16#207C/1E | 16#AE/01/1E = 174/01/30 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAA | Scan output 10 address | 16#3C46 = 15430 | 16#207C/1F | 16#AE/01/1F = 174/01/31 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAB | Scan output 11 address | 16#3C47 = 15431 | 16#207C/20 | 16#AE/01/20 = 174/01/32 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAC | Scan output 12 address | 16#3C48 = 15432 | 16#207C/21 | 16#AE/01/21 = 174/01/33 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAD | Scan output 13 address | 16#3C49 = 15433 | 16#207C/22 | 16#AE/01/22 = 174/01/34 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAE | Scan output 14 address | 16#3C4A = 15434 | 16#207C/23 | 16#AE/01/23 = 174/01/35 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAF | Scan output 15 address | 16#3C4B = 15435 | 16#207C/24 | 16#AE/01/24 = 174/01/36 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAG | Scan output 16 address | 16#3C4C = 15436 | 16#207C/25 | 16#AE/01/25 = 174/01/37 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCT | Electrical energy consumed TODAY by the motor (KWh) | 16#297E = 10622 | 16#204C/17 | 16#96/01/17 = 150/01/23 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Today] (OCT) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO)
OCY | Electrical energy consumed YESTERDAY by the motor (KWh) | 16#2980 = 10624 | 16#204C/19 | 16#96/01/19 = 150/01/25 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Yesterday] (OCY) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO)
OE0 | Real energy consumption (Wh) | 16#2978 = 10616 | 16#204C/11 | 16#96/01/11 = 150/01/17 |  | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Consumption] (OE0) | [Elec Ener Output Counter] (ELO)
OE1 | Real energy consumption (kWh) | 16#2979 = 10617 | 16#204C/12 | 16#96/01/12 = 150/01/18 |  | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Consumption] (OE1) | [Elec Ener Output Counter] (ELO)
OE2 | Real energy consumption (MWh) | 16#297A = 10618 | 16#204C/13 | 16#96/01/13 = 150/01/19 |  | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Consumption] (OE2) | [Elec Ener Output Counter] (ELO)
OE3 | Real energy consumption (GWh) | 16#297B = 10619 | 16#204C/14 | 16#96/01/14 = 150/01/20 |  | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Consumption] (OE3) | [Elec Ener Output Counter] (ELO)
OE4 | Real energy consumption (TWh) | 16#297C = 10620 | 16#204C/15 | 16#96/01/15 = 150/01/21 |  | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Consumption] (OE4) | [Elec Ener Output Counter] (ELO)
OFI | Sinus filter activation | 16#0C25 = 3109 | 16#2001/A | 16#70/01/6E = 112/01/110 | OFI | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Sinus Filter Activation] (OFI) | [Motor monitoring] (MOP)
OMA7 | Scan input 7 address | 16#3C2F = 15407 | 16#207C/8 | 16#AE/01/08 = 174/01/08 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA8 | Scan input 8 address | 16#3C30 = 15408 | 16#207C/9 | 16#AE/01/09 = 174/01/09 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA9 | Scan input 9 address | 16#3C31 = 15409 | 16#207C/A | 16#AE/01/0A = 174/01/10 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAA | Scan input 10 address | 16#3C32 = 15410 | 16#207C/B | 16#AE/01/0B = 174/01/11 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAB | Scan input 11 address | 16#3C33 = 15411 | 16#207C/C | 16#AE/01/0C = 174/01/12 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAC | Scan input 12 address | 16#3C34 = 15412 | 16#207C/D | 16#AE/01/0D = 174/01/13 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAD | Scan input 13 address | 16#3C35 = 15413 | 16#207C/E | 16#AE/01/0E = 174/01/14 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAE | Scan input 14 address | 16#3C36 = 15414 | 16#207C/F | 16#AE/01/0F = 174/01/15 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAF | Scan input 15 address | 16#3C37 = 15415 | 16#207C/10 | 16#AE/01/10 = 174/01/16 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAG | Scan input 16 address | 16#3C38 = 15416 | 16#207C/11 | 16#AE/01/11 = 174/01/17 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OP0 | Electrical energy produced by the motor (Wh) | 16#2973 = 10611 | 16#204C/C | 16#96/01/0C = 150/01/12 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh
OP1 | Electrical energy produced by the motor (KWh) | 16#2974 = 10612 | 16#204C/D | 16#96/01/0D = 150/01/13 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh
OP2 | Electrical energy produced by the motor (MWh) | 16#2975 = 10613 | 16#204C/E | 16#96/01/0E = 150/01/14 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh
OP3 | Electrical energy produced by the motor (GWh) | 16#2976 = 10614 | 16#204C/F | 16#96/01/0F = 150/01/15 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh
OP4 | Electrical energy produced by the motor (TWh) | 16#2977 = 10615 | 16#204C/10 | 16#96/01/10 = 150/01/16 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh
OPRW | Motor mechanical power estimation | 16#0CDC = 3292 | 16#2002/5D | 16#71/01/5D = 113/01/93 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Power Estim Value] (OPRW) | [Mechanical Energy] (MEC)
OTP9 | Motor torque | 16#1CAB = 7339 | 16#202B/28 | 16#85/01/8C = 133/01/140 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTP9) | [None] (DP9)
OTPA | Motor torque | 16#1E32 = 7730 | 16#202F/1F | 16#87/01/83 = 135/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTPA) | [None] (DPA)
OTPB | Motor torque | 16#1E33 = 7731 | 16#202F/20 | 16#87/01/84 = 135/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTPB) | [None] (DPB)
OTPC | Motor torque | 16#1E34 = 7732 | 16#202F/21 | 16#87/01/85 = 135/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTPC) | [None] (DPC)
OTPD | Motor torque | 16#1E35 = 7733 | 16#202F/22 | 16#87/01/86 = 135/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTPD) | [None] (DPD)
OTPE | Motor torque | 16#1E36 = 7734 | 16#202F/23 | 16#87/01/87 = 135/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTPE) | [None] (DPE)
OTPF | Motor torque | 16#1E37 = 7735 | 16#202F/24 | 16#87/01/88 = 135/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque] (OTPF) | [None] (DPF)
PCAH | Over-consumption threshold | 16#2A62 = 10850 | 16#204E/33 | 16#97/01/33 = 151/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 200.0 % | [Over-Consumption Thd] (PCAH) | [Elec Ener Output Counter] (ELO)
PCAL | Under-consumption threshold | 16#2A63 = 10851 | 16#204E/34 | 16#97/01/34 = 151/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Under-Consumption Thd] (PCAL) | [Elec Ener Output Counter] (ELO)
PCAT | Over/Under-consumption time delay | 16#2A64 = 10852 | 16#204E/35 | 16#97/01/35 = 151/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 1 min | 0 min ... 60 min | [Over/Under-Cons Delay] (PCAT) | [Elec Ener Output Counter] (ELO)
PCPB | Response to pump cycle error | 16#3E1F = 15903 | 16#2081/4 | 16#B0/01/68 = 176/01/104 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [PumpCycleError Resp] (PCPB) | [Pumpcycle monitoring] (CSP)
PCPM | Pump cycle monitoring mode | 16#3E1C = 15900 | 16#2081/1 | 16#B0/01/65 = 176/01/101 | PCPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pump cycle monitoring disabled] NO |  | [PumpCycle Monitor] (PCPM) | [Pumpcycle monitoring] (CSP)
PCPN | Pump cycle maximum allowed starts | 16#3E1D = 15901 | 16#2081/2 | 16#B0/01/66 = 176/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 6 | 1 ... 99 | [PumpCycle MaxStarts] (PCPN) | [Pumpcycle monitoring] (CSP)
PCPT | Pump cycle timeframe | 16#3E1E = 15902 | 16#2081/3 | 16#B0/01/67 = 176/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 60 min | 0 min ... 3600 min | [PumpCycle timeframe] (PCPT) | [Pumpcycle monitoring] (CSP)
PEV1 | TPDO1 Event mask | 16#17B6 = 6070 | 16#201E/47 | 16#7F/01/47 = 127/01/71 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV2 | TPDO2 Event mask | 16#17B7 = 6071 | 16#201E/48 | 16#7F/01/48 = 127/01/72 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV3 | TPDO3 Event mask | 16#17B8 = 6072 | 16#201E/49 | 16#7F/01/49 = 127/01/73 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV4 | TPDO4 Event mask | 16#17B9 = 6073 | 16#201E/4A | 16#7F/01/4A = 127/01/74 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PFC7 | DI7 frequency measured | 16#343A = 13370 | 16#2067/47 | 16#A3/01/AB = 163/01/171 |  | Actual values parameters | R | UINT (Unsigned32) | 0.01 Hz |  | 0.00 Hz ... 42949672.95 Hz
PFC8 | DI8 frequency measured | 16#344E = 13390 | 16#2067/5B | 16#A3/01/BF = 163/01/191 |  | Actual values parameters | R | UINT (Unsigned32) | 0.01 Hz |  | 0.00 Hz ... 42949672.95 Hz
PFI7 | DI7 frequency filter | 16#3434 = 13364 | 16#2067/41 | 16#A3/01/A5 = 163/01/165 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI7 Frequency Filter] (PFI7) | [DI7 Frequency measured] (PFC7) [DI7 Pulse Config] (PAI7)
PFI8 | DI8 frequency filter | 16#3448 = 13384 | 16#2067/55 | 16#A3/01/B9 = 163/01/185 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI8 Frequency Filter] (PFI8) | [DI8 Frequency measured] (PFC8) [DI8 Pulse Config] (PAI8)
PFMB | PID feedback error response | 16#2E9D = 11933 | 16#2059/22 | 16#9C/01/86 = 156/01/134 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [PID Fdbk Error Resp] (PFMB) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM)
PFMD | PID feedback error delay | 16#2E9C = 11932 | 16#2059/21 | 16#9C/01/85 = 156/01/133 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PID Fdbk Error Delay] (PFMD) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Settings] (SET)
PFMM | PID feedback monitoring activation | 16#2E9A = 11930 | 16#2059/1F | 16#9C/01/83 = 156/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID Fdbk Monitoring] (PFMM) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM)
PFMR | PID feedback range | 16#2E9B = 11931 | 16#2059/20 | 16#9C/01/84 = 156/01/132 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 3 % | 0 % ... 100 % | [PID Fdbk Range] (PFMR) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Settings] (SET)
PHR | Output phase rotation | 16#3459 = 13401 | 16#2068/2 | 16#A4/01/02 = 164/01/02 | PHR | Configuration and settings | R/WS | WORD (Enumeration) | - | [A - B - C phase rotation] ABC |  | [Output Ph Rotation] (PHR) | [Motor control] (DRC)
PIH7 | DI7 pulseInput high frequency | 16#3432 = 13362 | 16#2067/3F | 16#A3/01/A3 = 163/01/163 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI7 PulseInput High Freq] (PIH7) | [DI7 Frequency measured] (PFC7) [DI7 Pulse Config] (PAI7)
PIH8 | DI8 pulseInput high frequency | 16#3446 = 13382 | 16#2067/53 | 16#A3/01/B7 = 163/01/183 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI8 PulseInput High Freq] (PIH8) | [DI8 Frequency measured] (PFC8) [DI8 Pulse Config] (PAI8)
PIL7 | DI7 pulseInput low frequency | 16#3430 = 13360 | 16#2067/3D | 16#A3/01/A1 = 163/01/161 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.01 Hz | 0.00 Hz | 0.00 Hz ... 30000.00 Hz | [DI7 PulseInput Low Freq] (PIL7) | [DI7 Frequency measured] (PFC7) [DI7 Pulse Config] (PAI7)
PIL8 | DI8 pulseInput low frequency | 16#3444 = 13380 | 16#2067/51 | 16#A3/01/B5 = 163/01/181 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.01 Hz | Refer to programming manual | 0.00 Hz ... 30000.00 Hz | [DI8 PulseInput Low Freq] (PIL8) | [DI8 Frequency measured] (PFC8) [DI8 Pulse Config] (PAI8)
R3 | R3 assignment | 16#138B = 5003 | 16#2014/4 | 16#7A/01/04 = 122/01/04 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R3 Assignment] (R3) | [R3 configuration] (R3)
R3D | R3 delay time | 16#1093 = 4243 | 16#200C/2C | 16#76/01/2C = 118/01/44 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R3 Delay time] (R3D) | [R3 configuration] (R3)
R3H | R3 holding time | 16#107F = 4223 | 16#200C/18 | 16#76/01/18 = 118/01/24 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R3 Holding time] (R3H) | [R3 configuration] (R3)
R3S | R3 active level | 16#106B = 4203 | 16#200C/4 | 16#76/01/04 = 118/01/04 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R3 Active at] (R3S) | [R3 configuration] (R3)
R4 | R4 assignment | 16#138C = 5004 | 16#2014/5 | 16#7A/01/05 = 122/01/05 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R4 Assignment] (R4) | [R4 configuration] (R4)
R4D | R4 delay time | 16#1094 = 4244 | 16#200C/2D | 16#76/01/2D = 118/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R4 Delay time] (R4D) | [R4 configuration] (R4)
R4H | R4 holding time | 16#1080 = 4224 | 16#200C/19 | 16#76/01/19 = 118/01/25 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R4 Holding time] (R4H) | [R4 configuration] (R4)
R4S | R4 active level | 16#106C = 4204 | 16#200C/5 | 16#76/01/05 = 118/01/05 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R4 Active at] (R4S) | [R4 configuration] (R4)
R5 | R5 assignment | 16#138D = 5005 | 16#2014/6 | 16#7A/01/06 = 122/01/06 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R5 Assignment] (R5) | [R5 configuration] (R5)
R5D | R5 delay time | 16#1095 = 4245 | 16#200C/2E | 16#76/01/2E = 118/01/46 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R5 Delay time] (R5D) | [R5 configuration] (R5)
R5H | R5 holding time | 16#1081 = 4225 | 16#200C/1A | 16#76/01/1A = 118/01/26 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R5 Holding time] (R5H) | [R5 configuration] (R5)
R5S | R5 active level | 16#106D = 4205 | 16#200C/6 | 16#76/01/06 = 118/01/06 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R5 Active at] (R5S) | [R5 configuration] (R5)
R6 | R6 assignment | 16#138E = 5006 | 16#2014/7 | 16#7A/01/07 = 122/01/07 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R6 Assignment] (R6) | [R6 configuration] (R6)
R6D | R6 activation delay time | 16#1096 = 4246 | 16#200C/2F | 16#76/01/2F = 118/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R6 activ delay time] (R6D) | [R6 configuration] (R6)
R6H | R6 holding delay time | 16#1082 = 4226 | 16#200C/1B | 16#76/01/1B = 118/01/27 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R6 hold delay time] (R6H) | [R6 configuration] (R6)
R6S | R6 active level | 16#106E = 4206 | 16#200C/7 | 16#76/01/07 = 118/01/07 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R6 Active at] (R6S) | [R6 configuration] (R6)
RFP9 | Motor frequency | 16#1C5B = 7259 | 16#202A/3C | 16#85/01/3C = 133/01/60 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFP9) | [None] (DP9)
RFPA | Motor frequency | 16#1DE2 = 7650 | 16#202E/33 | 16#87/01/33 = 135/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPA) | [None] (DPA)
RFPB | Motor frequency | 16#1DE3 = 7651 | 16#202E/34 | 16#87/01/34 = 135/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPB) | [None] (DPB)
RFPC | Motor frequency | 16#1DE4 = 7652 | 16#202E/35 | 16#87/01/35 = 135/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPC) | [None] (DPC)
RFPD | Motor frequency | 16#1DE5 = 7653 | 16#202E/36 | 16#87/01/36 = 135/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPD) | [None] (DPD)
RFPE | Motor frequency | 16#1DE6 = 7654 | 16#202E/37 | 16#87/01/37 = 135/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPE) | [None] (DPE)
RFPF | Motor frequency | 16#1DE7 = 7655 | 16#202E/38 | 16#87/01/38 = 135/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPF) | [None] (DPF)
RTD | Reference high threshold | 16#2B05 = 11013 | 16#2050/E | 16#98/01/0E = 152/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Reference high Thd] (RTD) | [Threshold reached] (THRE) [Settings] (SET)
RTDL | Reference low threshold | 16#2B06 = 11014 | 16#2050/F | 16#98/01/0F = 152/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Reference low Thd] (RTDL) | [Threshold reached] (THRE) [Settings] (SET)
RTP9 | Run Elapsed time | 16#1C65 = 7269 | 16#202A/46 | 16#85/01/46 = 133/01/70 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP9) | [None] (DP9)
RTPA | Run Elapsed time | 16#1DEC = 7660 | 16#202E/3D | 16#87/01/3D = 135/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPA) | [None] (DPA)
RTPB | Run Elapsed time | 16#1DED = 7661 | 16#202E/3E | 16#87/01/3E = 135/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPB) | [None] (DPB)
RTPC | Run Elapsed time | 16#1DEE = 7662 | 16#202E/3F | 16#87/01/3F = 135/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPC) | [None] (DPC)
RTPD | Run Elapsed time | 16#1DEF = 7663 | 16#202E/40 | 16#87/01/40 = 135/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPD) | [None] (DPD)
RTPE | Run Elapsed time | 16#1DF0 = 7664 | 16#202E/41 | 16#87/01/41 = 135/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPE) | [None] (DPE)
RTPF | Run Elapsed time | 16#1DF1 = 7665 | 16#202E/42 | 16#87/01/42 = 135/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPF) | [None] (DPF)
SAI4 | AI4 physical value without filter | 16#14AE = 5294 | 16#2016/5F | 16#7B/01/5F = 123/01/95 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI5 | AI5 physical value without filter | 16#14B2 = 5298 | 16#2016/63 | 16#7B/01/63 = 123/01/99 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAO2 | AO2 physical value without filter | 16#14B0 = 5296 | 16#2016/61 | 16#7B/01/61 = 123/01/97 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SFP9 | Switching frequency | 16#1CC9 = 7369 | 16#202B/46 | 16#85/01/AA = 133/01/170 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP9) | [None] (DP9)
SFPA | Switching frequency | 16#1E50 = 7760 | 16#202F/3D | 16#87/01/A1 = 135/01/161 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPA) | [None] (DPA)
SFPB | Switching frequency | 16#1E51 = 7761 | 16#202F/3E | 16#87/01/A2 = 135/01/162 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPB) | [None] (DPB)
SFPC | Switching frequency | 16#1E52 = 7762 | 16#202F/3F | 16#87/01/A3 = 135/01/163 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPC) | [None] (DPC)
SFPD | Switching frequency | 16#1E53 = 7763 | 16#202F/40 | 16#87/01/A4 = 135/01/164 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPD) | [None] (DPD)
SFPE | Switching frequency | 16#1E54 = 7764 | 16#202F/41 | 16#87/01/A5 = 135/01/165 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPE) | [None] (DPE)
SFPF | Switching frequency | 16#1E55 = 7765 | 16#202F/42 | 16#87/01/A6 = 135/01/166 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPF) | [None] (DPF)
SFS | PID start ref frequency | 16#2EB3 = 11955 | 16#2059/38 | 16#9C/01/9C = 156/01/156 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [PID Start Ref Freq] (SFS) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
SLBS | Sleep boost speed | 16#2DEC = 11756 | 16#2057/39 | 16#9B/01/9D = 155/01/157 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Boost Speed] (SLBS) | [Boost] (SBT) [Settings] (SET)
SLBT | Sleep boost time | 16#2DED = 11757 | 16#2057/3A | 16#9B/01/9E = 155/01/158 |  | Configuration and settings | R/W | INT (Signed16) | 1 s | 0 s | 0 s ... 3600 s | [Sleep Boost Time] (SLBT) | [Boost] (SBT) [Settings] (SET)
SLE | Sleep offset threshold | 16#2DB6 = 11702 | 16#2057/3 | 16#9B/01/67 = 155/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 1.0 Hz ... 1000.0 Hz | [Sleep Offset Thres.] (SLE) | [Settings] (SET) [Stop after speed timeout] (PRSP)
SLPD | Sleep delay | 16#2DEB = 11755 | 16#2057/38 | 16#9B/01/9C = 155/01/156 |  | Actual values parameters | R/W | INT (Signed16) | 1 s | 20 s | 0 s ... 3600 s | [Sleep Delay] (SLPD) | [Sleep menu] (SLP) [Settings] (SET)
SLPM | Sleep Detection mode | 16#2DE6 = 11750 | 16#2057/33 | 16#9B/01/97 = 155/01/151 | SLPM | Actual values parameters | R/WS | WORD (Enumeration) | - | [No] NO |  | [Sleep Detect Mode] (SLPM) | [Sleep menu] (SLP)
SLPR | Sleep power level | 16#2DEA = 11754 | 16#2057/37 | 16#9B/01/9B = 155/01/155 |  | Actual values parameters | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Sleep Power Level] (SLPR) | [Sleep menu] (SLP) [Settings] (SET)
SLPW | Sleep switch assignment | 16#2DE7 = 11751 | 16#2057/34 | 16#9B/01/98 = 155/01/152 | PSLIN | Actual values parameters | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Sleep Switch Assign] (SLPW) | [Sleep menu] (SLP)
SLSL | Sleep minimum speed level | 16#2DE9 = 11753 | 16#2057/36 | 16#9B/01/9A = 155/01/154 |  | Actual values parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Min Speed] (SLSL) | [Sleep menu] (SLP) [Settings] (SET)
SPD | Motor speed | 16#2EE4 = 12004 | 16#205A/5 | 16#9D/01/05 = 157/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Speed] (SPD) | [System] (DST) [Motor parameters] (MMO)
ST00 | Status registers 0 | 16#3EE4 = 16100 | 16#2083/1 | 16#B1/01/65 = 177/01/101 |  | Status parameters | R | WORD (BitString16) | -
ST01 | Status registers 1 | 16#3EE5 = 16101 | 16#2083/2 | 16#B1/01/66 = 177/01/102 |  | Status parameters | R | WORD (BitString16) | -
ST02 | Status registers 2 | 16#3EE6 = 16102 | 16#2083/3 | 16#B1/01/67 = 177/01/103 |  | Status parameters | R | WORD (BitString16) | -
ST03 | Status registers 3 | 16#3EE7 = 16103 | 16#2083/4 | 16#B1/01/68 = 177/01/104 |  | Status parameters | R | WORD (BitString16) | -
ST04 | Status registers 4 | 16#3EE8 = 16104 | 16#2083/5 | 16#B1/01/69 = 177/01/105 |  | Status parameters | R | WORD (BitString16) | -
ST05 | Status registers 5 | 16#3EE9 = 16105 | 16#2083/6 | 16#B1/01/6A = 177/01/106 |  | Status parameters | R | WORD (BitString16) | -
ST06 | Status registers 6 | 16#3EEA = 16106 | 16#2083/7 | 16#B1/01/6B = 177/01/107 |  | Status parameters | R | WORD (BitString16) | -
ST07 | Status registers 7 | 16#3EEB = 16107 | 16#2083/8 | 16#B1/01/6C = 177/01/108 |  | Status parameters | R | WORD (BitString16) | -
ST08 | Status registers 8 | 16#3EEC = 16108 | 16#2083/9 | 16#B1/01/6D = 177/01/109 |  | Status parameters | R | WORD (BitString16) | -
ST09 | Status registers 9 | 16#3EED = 16109 | 16#2083/A | 16#B1/01/6E = 177/01/110 |  | Status parameters | R | WORD (BitString16) | -
ST10 | Status registers 10 | 16#3EEE = 16110 | 16#2083/B | 16#B1/01/6F = 177/01/111 |  | Status parameters | R | WORD (BitString16) | -
ST11 | Status registers 11 | 16#3EEF = 16111 | 16#2083/C | 16#B1/01/70 = 177/01/112 |  | Status parameters | R | WORD (BitString16) | -
ST12 | Status registers 12 | 16#3EF0 = 16112 | 16#2083/D | 16#B1/01/71 = 177/01/113 |  | Status parameters | R | WORD (BitString16) | -
ST13 | Status registers 13 | 16#3EF1 = 16113 | 16#2083/E | 16#B1/01/72 = 177/01/114 |  | Status parameters | R | WORD (BitString16) | -
ST14 | Status registers 14 | 16#3EF2 = 16114 | 16#2083/F | 16#B1/01/73 = 177/01/115 |  | Status parameters | R | WORD (BitString16) | -
ST15 | Status registers 15 | 16#3EF3 = 16115 | 16#2083/10 | 16#B1/01/74 = 177/01/116 |  | Status parameters | R | WORD (BitString16) | -
ST16 | Status registers 16 | 16#3EF4 = 16116 | 16#2083/11 | 16#B1/01/75 = 177/01/117 |  | Status parameters | R | WORD (BitString16) | -
ST17 | Status registers 17 | 16#3EF5 = 16117 | 16#2083/12 | 16#B1/01/76 = 177/01/118 |  | Status parameters | R | WORD (BitString16) | -
ST18 | Status registers 18 | 16#3EF6 = 16118 | 16#2083/13 | 16#B1/01/77 = 177/01/119 |  | Status parameters | R | WORD (BitString16) | -
ST19 | Status registers 19 | 16#3EF7 = 16119 | 16#2083/14 | 16#B1/01/78 = 177/01/120 |  | Status parameters | R | WORD (BitString16) | -
STOF | STOx digital input State | 16#3BDB = 15323 | 16#207B/18 | 16#AD/01/7C = 173/01/124 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
STP1 | Motor stall max time | 16#2437 = 9271 | 16#203E/48 | 16#8F/01/48 = 143/01/72 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 200.0 s | [Stall Max Time] (STP1) | [Settings] (SET) [Stall monitoring] (STPR)
STP2 | Stall monitoring current level | 16#2438 = 9272 | 16#203E/49 | 16#8F/01/49 = 143/01/73 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 150.0 % | 0.0 % ... 150.0 % | [Stall Current] (STP2) | [Settings] (SET) [Stall monitoring] (STPR)
STP3 | Stall monitoring frequency level | 16#2439 = 9273 | 16#203E/4A | 16#8F/01/4A = 143/01/74 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 2.0 Hz | 0.0 Hz ... 599.0 Hz | [Stall Frequency] (STP3) | [Settings] (SET) [Stall monitoring] (STPR)
STPC | Stall monitoring activation | 16#2436 = 9270 | 16#203E/47 | 16#8F/01/47 = 143/01/71 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Stall Monitoring] (STPC) | [Stall monitoring] (STPR)
SUCU | Application Currency Unit | 16#2EF9 = 12025 | 16#205A/1A | 16#9D/01/1A = 157/01/26 | SUCU | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Currency unit list] (SUCU) | [Define system units] (SUC)
SUTP | Application Temperature Unit (used as default) | 16#2EF8 = 12024 | 16#205A/19 | 16#9D/01/19 = 157/01/25 | SUTP | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Temperature unit] (SUTP) | [Define system units] (SUC)
TBR2 | Modbus 2 baud rate | 16#1787 = 6023 | 16#201E/18 | 16#7F/01/18 = 127/01/24 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [Modbus 2 baud rate] (TBR2) | [Modbus HMI] (MD2)
TDP9 | Drive thermal state | 16#1CB5 = 7349 | 16#202B/32 | 16#85/01/96 = 133/01/150 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP9) | [None] (DP9)
TDPA | Drive thermal state | 16#1E3C = 7740 | 16#202F/29 | 16#87/01/8D = 135/01/141 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPA) | [None] (DPA)
TDPB | Drive thermal state | 16#1E3D = 7741 | 16#202F/2A | 16#87/01/8E = 135/01/142 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPB) | [None] (DPB)
TDPC | Drive thermal state | 16#1E3E = 7742 | 16#202F/2B | 16#87/01/8F = 135/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPC) | [None] (DPC)
TDPD | Drive thermal state | 16#1E3F = 7743 | 16#202F/2C | 16#87/01/90 = 135/01/144 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPD) | [None] (DPD)
TDPE | Drive thermal state | 16#1E40 = 7744 | 16#202F/2D | 16#87/01/91 = 135/01/145 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPE) | [None] (DPE)
TDPF | Drive thermal state | 16#1E41 = 7745 | 16#202F/2E | 16#87/01/92 = 135/01/146 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPF) | [None] (DPF)
TFO2 | Modbus 2 format | 16#1788 = 6024 | 16#201E/19 | 16#7F/01/19 = 127/01/25 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [Modbus 2 format] (TFO2) | [Modbus HMI] (MD2)
TH1A | Thermal warning level for AI1 | 16#33A3 = 13219 | 16#2066/14 | 16#A3/01/14 = 163/01/20 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI1 Th Warn Level] (TH1A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH1B | Response to thermal error for AI1 | 16#33B7 = 13239 | 16#2066/28 | 16#A3/01/28 = 163/01/40 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI1 Th Error Resp] (TH1B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3A | Thermal warning level for AI3 | 16#33A5 = 13221 | 16#2066/16 | 16#A3/01/16 = 163/01/22 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI3 Th Warn Level] (TH3A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH1F | Thermal error level for AI1 | 16#33AD = 13229 | 16#2066/1E | 16#A3/01/1E = 163/01/30 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI1 Th Error Level] (TH1F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH3B | Response to thermal error for AI3 | 16#33B9 = 13241 | 16#2066/2A | 16#A3/01/2A = 163/01/42 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI3 Th Error Resp] (TH3B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH1S | Activation of the thermal monitoring on AI1 | 16#3399 = 13209 | 16#2066/A | 16#A3/01/0A = 163/01/10 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI1 Th Monitoring] (TH1S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3F | Thermal error level for AI3 | 16#33AF = 13231 | 16#2066/20 | 16#A3/01/20 = 163/01/32 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI3 Th Error Level] (TH3F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH1V | AI1 thermal value | 16#33C1 = 13249 | 16#2066/32 | 16#A3/01/32 = 163/01/50 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI1 Th Value] (TH1V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3S | Activation of the thermal monitoring on AI3 | 16#339B = 13211 | 16#2066/C | 16#A3/01/0C = 163/01/12 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI3 Th Monitoring] (TH3S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3V | AI3 thermal value | 16#33C3 = 13251 | 16#2066/34 | 16#A3/01/34 = 163/01/52 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI3 Th Value] (TH3V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4A | Thermal warning level for AI4 | 16#33A6 = 13222 | 16#2066/17 | 16#A3/01/17 = 163/01/23 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI4 Th Warn Level] (TH4A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH4B | Response to thermal error for AI4 | 16#33BA = 13242 | 16#2066/2B | 16#A3/01/2B = 163/01/43 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI4 Th Error Resp] (TH4B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4F | Thermal error level for AI4 | 16#33B0 = 13232 | 16#2066/21 | 16#A3/01/21 = 163/01/33 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI4 Th Error Level] (TH4F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH4S | Activation of the thermal monitoring on AI4 | 16#339C = 13212 | 16#2066/D | 16#A3/01/0D = 163/01/13 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI4 Th Monitoring] (TH4S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4V | AI4 thermal value | 16#33C4 = 13252 | 16#2066/35 | 16#A3/01/35 = 163/01/53 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI4 Th Value] (TH4V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5A | Thermal warning level for AI5 | 16#33A7 = 13223 | 16#2066/18 | 16#A3/01/18 = 163/01/24 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI5 Th Warn Level] (TH5A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH5B | Response to thermal error for AI5 | 16#33BB = 13243 | 16#2066/2C | 16#A3/01/2C = 163/01/44 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI5 Th Error Resp] (TH5B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5F | Thermal error level for AI5 | 16#33B1 = 13233 | 16#2066/22 | 16#A3/01/22 = 163/01/34 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI5 Th Error Level] (TH5F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH5S | Activation of the thermal monitoring on AI5 | 16#339D = 13213 | 16#2066/E | 16#A3/01/0E = 163/01/14 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI5 Th Monitoring] (TH5S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5V | AI5 thermal value | 16#33C5 = 13253 | 16#2066/36 | 16#A3/01/36 = 163/01/54 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI5 Th Value] (TH5V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THP9 | Motor thermal state | 16#1C79 = 7289 | 16#202A/5A | 16#85/01/5A = 133/01/90 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP9) | [None] (DP9)
THPA | Motor thermal state | 16#1E00 = 7680 | 16#202E/51 | 16#87/01/51 = 135/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPA) | [None] (DPA)
THPB | Motor thermal state | 16#1E01 = 7681 | 16#202E/52 | 16#87/01/52 = 135/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPB) | [None] (DPB)
THPC | Motor thermal state | 16#1E02 = 7682 | 16#202E/53 | 16#87/01/53 = 135/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPC) | [None] (DPC)
THPD | Motor thermal state | 16#1E03 = 7683 | 16#202E/54 | 16#87/01/54 = 135/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPD) | [None] (DPD)
THPE | Motor thermal state | 16#1E04 = 7684 | 16#202E/55 | 16#87/01/55 = 135/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPE) | [None] (DPE)
THPF | Motor thermal state | 16#1E05 = 7685 | 16#202E/56 | 16#87/01/56 = 135/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPF) | [None] (DPF)
TJP9 | IGBT junction temp | 16#1CBF = 7359 | 16#202B/3C | 16#85/01/A0 = 133/01/160 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP9) | [None] (DP9)
TJPA | IGBT junction temp | 16#1E46 = 7750 | 16#202F/33 | 16#87/01/97 = 135/01/151 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPA) | [None] (DPA)
TJPB | IGBT junction temp | 16#1E47 = 7751 | 16#202F/34 | 16#87/01/98 = 135/01/152 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPB) | [None] (DPB)
TJPC | IGBT junction temp | 16#1E48 = 7752 | 16#202F/35 | 16#87/01/99 = 135/01/153 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPC) | [None] (DPC)
TJPD | IGBT junction temp | 16#1E49 = 7753 | 16#202F/36 | 16#87/01/9A = 135/01/154 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPD) | [None] (DPD)
TJPE | IGBT junction temp | 16#1E4A = 7754 | 16#202F/37 | 16#87/01/9B = 135/01/155 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPE) | [None] (DPE)
TJPF | IGBT junction temp | 16#1E4B = 7755 | 16#202F/38 | 16#87/01/9C = 135/01/156 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPF) | [None] (DPF)
TOCT | Type of control | 16#2E8F = 11919 | 16#2059/14 | 16#9C/01/78 = 156/01/120 | TOCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not available] NA |  | [Type of control] (TOCT) | [PID Feedback] (FDB) [PID Feedback] (FDB)
TQB | Pulse without Run delay | 16#3910 = 14608 | 16#2074/9 | 16#AA/01/09 = 170/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse wo Run delay] (TQB) | [Frequency meter] (FQF)
TTOB | Ethernet embedded : time-out | 16#FB9F = 64415 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Eth embd : Time-out] (TTOB) | [Embd Eth Config] (ETE)
UIH3 | AI3 voltage scaling parameter of 100% | 16#1148 = 4424 | 16#200E/19 | 16#77/01/19 = 119/01/25 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI3 Max Value] (UIH3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
UIH4 | AI4 voltage scaling parameter of 100% | 16#1149 = 4425 | 16#200E/1A | 16#77/01/1A = 119/01/26 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI4 Max Value] (UIH4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
UIH5 | AI5 voltage scaling parameter of 100% | 16#114A = 4426 | 16#200E/1B | 16#77/01/1B = 119/01/27 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI5 Max Value] (UIH5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
UIL3 | AI3 voltage scaling parameter of 0% | 16#113E = 4414 | 16#200E/F | 16#77/01/0F = 119/01/15 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI3 Min. Value] (UIL3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
UIL4 | AI4 voltage scaling parameter of 0% | 16#113F = 4415 | 16#200E/10 | 16#77/01/10 = 119/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI4 Min. Value] (UIL4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
UIL5 | AI5 voltage scaling parameter of 0% | 16#1140 = 4416 | 16#200E/11 | 16#77/01/11 = 119/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI5 Min. Value] (UIL5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
ULP9 | DC bus voltage | 16#1C6F = 7279 | 16#202A/50 | 16#85/01/50 = 133/01/80 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP9) | [None] (DP9)
ULPA | DC bus voltage | 16#1DF6 = 7670 | 16#202E/47 | 16#87/01/47 = 135/01/71 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPA) | [None] (DPA)
ULPB | DC bus voltage | 16#1DF7 = 7671 | 16#202E/48 | 16#87/01/48 = 135/01/72 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPB) | [None] (DPB)
ULPC | DC bus voltage | 16#1DF8 = 7672 | 16#202E/49 | 16#87/01/49 = 135/01/73 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPC) | [None] (DPC)
ULPD | DC bus voltage | 16#1DF9 = 7673 | 16#202E/4A | 16#87/01/4A = 135/01/74 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPD) | [None] (DPD)
ULPE | DC bus voltage | 16#1DFA = 7674 | 16#202E/4B | 16#87/01/4B = 135/01/75 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPE) | [None] (DPE)
ULPF | DC bus voltage | 16#1DFB = 7675 | 16#202E/4C | 16#87/01/4C = 135/01/76 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPF) | [None] (DPF)
UOH2 | AQ2 maximum output | 16#1218 = 4632 | 16#2010/21 | 16#78/01/21 = 120/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ2 max Output] (UOH2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
UOL2 | AQ2 minimum output | 16#120E = 4622 | 16#2010/17 | 16#78/01/17 = 120/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ2 min Output] (UOL2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
VBUS | DC bus voltage | 16#0CAB = 3243 | 16#2002/2C | 16#71/01/2C = 113/01/44 |  | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (VBUS) | [Drive parameters] (MPI)
VCB | Catch on fly sensitivity | 16#0C27 = 3111 | 16#2001/C | 16#70/01/70 = 112/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 V | 0.20 V | 0.10 V ... 100.00 V | [Catch on Fly Sensitivity] (VCB) | [Catch on the fly] (FLR)
WUPE | Wake UP process error level | 16#2DF0 = 11760 | 16#2057/3D | 16#9B/01/A1 = 155/01/161 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Wake Up Process Error] (WUPE) | [Wake up menu] (WKP) [Settings] (SET)
WUPF | Wake Up process level | 16#2DEF = 11759 | 16#2057/3C | 16#9B/01/A0 = 155/01/160 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Wake Up Process level] (WUPF) | [Wake up menu] (WKP) [Settings] (SET)
WUPM | Wake Up mode | 16#2DEE = 11758 | 16#2057/3B | 16#9B/01/9F = 155/01/159 | WUPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Feedback] FBK |  | [Wake Up Mode] (WUPM) | [Wake up menu] (WKP)
PREF | Reference power without drive | 16#2A30 = 10800 | 16#204E/1 | 16#97/01/01 = 151/01/01 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Reference Power] (PREF) | [Energy Saving] (ESA)
EPR | Active Electrical output power in % | 16#0CE1 = 3297 | 16#2002/62 | 16#71/01/62 = 113/01/98 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -300 % ... 300 %
SPDM | Motor Mechanical speed | 16#2EEB = 12011 | 16#205A/C | 16#9D/01/0C = 157/01/12 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Mechanical speed] (SPDM) | [Variable Speed Pump] (MPP)
DRC9 | Channel for reference frequency | 16#FB3F = 64319 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC9) | [None] (DP9)
DRCA | Channel for reference frequency | 16#FB40 = 64320 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCA) | [None] (DPA)
DRCB | Channel for reference frequency | 16#FB41 = 64321 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCB) | [None] (DPB)
DRCC | Channel for reference frequency | 16#FB42 = 64322 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCC) | [None] (DPC)
DRCD | Channel for reference frequency | 16#FB43 = 64323 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCD) | [None] (DPD)
DRCE | Channel for reference frequency | 16#FB44 = 64324 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCE) | [None] (DPE)
DRCF | Channel for reference frequency | 16#FB45 = 64325 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCF) | [None] (DPF)
DCC9 | Command channel | 16#FB4A = 64330 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC9) | [None] (DP9)
DCCA | Command channel | 16#FB4B = 64331 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCA) | [None] (DPA)
DCCB | Command channel | 16#FB4C = 64332 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCB) | [None] (DPB)
DCCZ | Command channel | 16#FB4D = 64333 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCZ) | [None] (DPC)
DCCD | Command channel | 16#FB4E = 64334 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCD) | [None] (DPD)
DCCE | Command channel | 16#FB4F = 64335 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCE) | [None] (DPE)
DCCF | Command channel | 16#FB50 = 64336 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCF) | [None] (DPF)
ILCI | Cabinet input physical state | 16#1453 = 5203 | 16#2016/4 | 16#7B/01/04 = 123/01/04 |  | I/O parameters | R | WORD (BitString16) | -
ILCR | Cabinet IO : Logic inputs real image (bit0 = DI50 ...) | 16#1454 = 5204 | 16#2016/5 | 16#7B/01/05 = 123/01/05 |  | I/O parameters | R | WORD (BitString16) | -
OLCI | Cabinet Ouput physical state | 16#145D = 5213 | 16#2016/E | 16#7B/01/0E = 123/01/14 |  | I/O parameters | R | WORD (BitString16) | -
OLCR | Cabinet IO : Logic outputs real image (bit0 = R60 ...) | 16#145E = 5214 | 16#2016/F | 16#7B/01/0F = 123/01/15 |  | I/O parameters | R/W | WORD (BitString16) | -
PSS | Drive Systems pre-settings status | 16#1F7C = 8060 | 16#2032/3D | 16#89/01/3D = 137/01/61 | PSS | Configuration management | R | WORD (Enumeration) | - |  |  | [Pre-settings Status] (PSS) | [Pre-settings] (PRES)
CBS | Circuit breaker status | 16#352B = 13611 | 16#206A/C | 16#A5/01/0C = 165/01/12 | CBS | Status parameters | R | WORD (Enumeration) | - | [Circuit breaker not configured] NO |  | [CB status] (CBS) | [Circuit breaker] (CCBK)
BPI0 | Power Brick error ID | 16#1E78 = 7800 | 16#2030/1 | 16#88/01/01 = 136/01/01 |  | History parameters | R | WORD (BitString16) | -
BPI1 | Power Brick error ID | 16#1E79 = 7801 | 16#2030/2 | 16#88/01/02 = 136/01/02 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI1) | [None] (DP1)
BPI2 | Power Brick error ID | 16#1E7A = 7802 | 16#2030/3 | 16#88/01/03 = 136/01/03 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI2) | [None] (DP2)
BPI3 | Power Brick error ID | 16#1E7B = 7803 | 16#2030/4 | 16#88/01/04 = 136/01/04 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI3) | [None] (DP3)
BPI4 | Power Brick error ID | 16#1E7C = 7804 | 16#2030/5 | 16#88/01/05 = 136/01/05 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI4) | [None] (DP4)
BPI5 | Power Brick error ID | 16#1E7D = 7805 | 16#2030/6 | 16#88/01/06 = 136/01/06 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI5) | [None] (DP5)
BPI6 | Power Brick error ID | 16#1E7E = 7806 | 16#2030/7 | 16#88/01/07 = 136/01/07 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI6) | [None] (DP6)
BPI7 | Power Brick error ID | 16#1E7F = 7807 | 16#2030/8 | 16#88/01/08 = 136/01/08 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI7) | [None] (DP7)
BPI8 | Power Brick error ID | 16#1E80 = 7808 | 16#2030/9 | 16#88/01/09 = 136/01/09 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI8) | [None] (DP8)
BPI9 | Power Brick error ID | 16#1E81 = 7809 | 16#2030/A | 16#88/01/0A = 136/01/10 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI9) | [None] (DP9)
BPIA | Power Brick error ID | 16#1E82 = 7810 | 16#2030/B | 16#88/01/0B = 136/01/11 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIA) | [None] (DPA)
BPIB | Power Brick error ID | 16#1E83 = 7811 | 16#2030/C | 16#88/01/0C = 136/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIB) | [None] (DPB)
BPIC | Power Brick error ID | 16#1E84 = 7812 | 16#2030/D | 16#88/01/0D = 136/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIC) | [None] (DPC)
BPID | Power Brick error ID | 16#1E85 = 7813 | 16#2030/E | 16#88/01/0E = 136/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPID) | [None] (DPD)
BPIE | Power Brick error ID | 16#1E86 = 7814 | 16#2030/F | 16#88/01/0F = 136/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIE) | [None] (DPE)
BPIF | Power Brick error ID | 16#1E87 = 7815 | 16#2030/10 | 16#88/01/10 = 136/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIF) | [None] (DPF)
BFI0 | AFE power brick error ID | 16#1E8C = 7820 | 16#2030/15 | 16#88/01/15 = 136/01/21 |  | History parameters | R | WORD (BitString16) | -
BFI1 | AFE power brick error ID | 16#1E8D = 7821 | 16#2030/16 | 16#88/01/16 = 136/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI1) | [None] (DP1)
BFI2 | AFE power brick error ID | 16#1E8E = 7822 | 16#2030/17 | 16#88/01/17 = 136/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI2) | [None] (DP2)
BFI3 | AFE power brick error ID | 16#1E8F = 7823 | 16#2030/18 | 16#88/01/18 = 136/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI3) | [None] (DP3)
BFI4 | AFE power brick error ID | 16#1E90 = 7824 | 16#2030/19 | 16#88/01/19 = 136/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI4) | [None] (DP4)
BFI5 | AFE power brick error ID | 16#1E91 = 7825 | 16#2030/1A | 16#88/01/1A = 136/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI5) | [None] (DP5)
BFI6 | AFE power brick error ID | 16#1E92 = 7826 | 16#2030/1B | 16#88/01/1B = 136/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI6) | [None] (DP6)
BFI7 | AFE power brick error ID | 16#1E93 = 7827 | 16#2030/1C | 16#88/01/1C = 136/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI7) | [None] (DP7)
BFI8 | AFE power brick error ID | 16#1E94 = 7828 | 16#2030/1D | 16#88/01/1D = 136/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI8) | [None] (DP8)
BFI9 | AFE power brick error ID | 16#1E95 = 7829 | 16#2030/1E | 16#88/01/1E = 136/01/30 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI9) | [None] (DP9)
BFIA | AFE power brick error ID | 16#1E96 = 7830 | 16#2030/1F | 16#88/01/1F = 136/01/31 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIA) | [None] (DPA)
BFIB | AFE power brick error ID | 16#1E97 = 7831 | 16#2030/20 | 16#88/01/20 = 136/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIB) | [None] (DPB)
BFIC | AFE power brick error ID | 16#1E98 = 7832 | 16#2030/21 | 16#88/01/21 = 136/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIC) | [None] (DPC)
BFID | AFE power brick error ID | 16#1E99 = 7833 | 16#2030/22 | 16#88/01/22 = 136/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFID) | [None] (DPD)
BFIE | AFE power brick error ID | 16#1E9A = 7834 | 16#2030/23 | 16#88/01/23 = 136/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIE) | [None] (DPE)
BFIF | AFE power brick error ID | 16#1E9B = 7835 | 16#2030/24 | 16#88/01/24 = 136/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIF) | [None] (DPF)
BUI0 | BU brick error ID | 16#1EA0 = 7840 | 16#2030/29 | 16#88/01/29 = 136/01/41 |  | History parameters | R | WORD (BitString16) | -
BUI1 | BU brick error ID | 16#1EA1 = 7841 | 16#2030/2A | 16#88/01/2A = 136/01/42 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI1) | [None] (DP1)
BUI2 | BU brick error ID | 16#1EA2 = 7842 | 16#2030/2B | 16#88/01/2B = 136/01/43 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI2) | [None] (DP2)
BUI3 | BU brick error ID | 16#1EA3 = 7843 | 16#2030/2C | 16#88/01/2C = 136/01/44 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI3) | [None] (DP3)
BUI4 | BU brick error ID | 16#1EA4 = 7844 | 16#2030/2D | 16#88/01/2D = 136/01/45 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI4) | [None] (DP4)
BUI5 | BU brick error ID | 16#1EA5 = 7845 | 16#2030/2E | 16#88/01/2E = 136/01/46 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI5) | [None] (DP5)
BUI6 | BU brick error ID | 16#1EA6 = 7846 | 16#2030/2F | 16#88/01/2F = 136/01/47 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI6) | [None] (DP6)
BUI7 | BU brick error ID | 16#1EA7 = 7847 | 16#2030/30 | 16#88/01/30 = 136/01/48 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI7) | [None] (DP7)
BUI8 | BU brick error ID | 16#1EA8 = 7848 | 16#2030/31 | 16#88/01/31 = 136/01/49 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI8) | [None] (DP8)
BUI9 | BU brick error ID | 16#1EA9 = 7849 | 16#2030/32 | 16#88/01/32 = 136/01/50 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUI9) | [None] (DP9)
BUIA | BU brick error ID | 16#1EAA = 7850 | 16#2030/33 | 16#88/01/33 = 136/01/51 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUIA) | [None] (DPA)
BUIB | BU brick error ID | 16#1EAB = 7851 | 16#2030/34 | 16#88/01/34 = 136/01/52 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUIB) | [None] (DPB)
BUIC | BU brick error ID | 16#1EAC = 7852 | 16#2030/35 | 16#88/01/35 = 136/01/53 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUIC) | [None] (DPC)
BUID | BU brick error ID | 16#1EAD = 7853 | 16#2030/36 | 16#88/01/36 = 136/01/54 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUID) | [None] (DPD)
BUIE | BU brick error ID | 16#1EAE = 7854 | 16#2030/37 | 16#88/01/37 = 136/01/55 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUIE) | [None] (DPE)
BUIF | BU brick error ID | 16#1EAF = 7855 | 16#2030/38 | 16#88/01/38 = 136/01/56 |  | History parameters | R | WORD (BitString16) | - |  |  | [BU Brick Error ID] (BUIF) | [None] (DPF)
HTQ | High torque | 16#241A = 9242 | 16#203E/2B | 16#8F/01/2B = 143/01/43 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 300.0 % | -300.0 % ... 300.0 % | [High Torque] (HTQ) | [Torque control] (TOR) [Settings] (SET) [M/S Torque Control] (MSQ)
LTQ | Low torque | 16#241B = 9243 | 16#203E/2C | 16#8F/01/2C = 143/01/44 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | -300.0 % | -300.0 % ... 300.0 % | [Low Torque] (LTQ) | [Torque control] (TOR) [Settings] (SET) [M/S Torque Control] (MSQ)
ILN | Mains current | 16#35D7 = 13783 | 16#206B/54 | 16#A5/01/B8 = 165/01/184 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Current] (ILN) | [Drive parameters] (MPI)
IQRW | Input reactive power | 16#0CE2 = 3298 | 16#2002/63 | 16#71/01/63 = 113/01/99 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Input Reactive Power] (IQRW) | [Elec Ener Input Counter] (ELI)
PWF | Input power factor | 16#35DA = 13786 | 16#206B/57 | 16#A5/01/BB = 165/01/187 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Input Power Factor] (PWF) | [Elec Ener Input Counter] (ELI)
FAC | Mains frequency | 16#35B6 = 13750 | 16#206B/33 | 16#A5/01/97 = 165/01/151 |  | Measurement parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Mains Frequency] (FAC) | [Drive parameters] (MPI)
FSBA | AFE : Fan speed | 16#35CA = 13770 | 16#206B/47 | 16#A5/01/AB = 165/01/171 |  | Measurement parameters | R | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
FBAT | AFE fan operation time | 16#35CB = 13771 | 16#206B/48 | 16#A5/01/AC = 165/01/172 |  | Actual values parameters | R | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [AFE Fan Operation Time] (FBAT) | [Counter Management] (ELT)
FCT | Cabinet Fan operation time | 16#35CD = 13773 | 16#206B/4A | 16#A5/01/AE = 165/01/174 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [Cabinet Fan Oper Time] (FCT) | [Counter Management] (ELT)
THDA | AFE : Thermal state | 16#9B22 = 39714 |  |  |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 %
BRTH | AFE Run time | 16#35CF = 13775 | 16#206B/4C | 16#A5/01/B0 = 165/01/176 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
BPTH | AFE power-on time | 16#35D1 = 13777 | 16#206B/4E | 16#A5/01/B2 = 165/01/178 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
BNSA | AFE Number of starts | 16#35D3 = 13779 | 16#206B/50 | 16#A5/01/B4 = 165/01/180 |  | Actual values parameters | R | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [AFE Nb of starts] (BNSA) | [Counter Management] (ELT)
TJD | Estimated TJ value in degree | 16#35B8 = 13752 | 16#206B/35 | 16#A5/01/99 = 165/01/153 |  | Measurement parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
CLIG | AFE generator mode | 16#35D9 = 13785 | 16#206B/56 | 16#A5/01/BA = 165/01/186 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | -0.2 % | -0.2 % ... 120.0 % | [AFE Generator Mode] (CLIG) | [Settings] (SET) [Active Front End] (AFE)
BRC | Braking resistor connected | 16#3725 = 14117 | 16#206F/12 | 16#A7/01/76 = 167/01/118 | BRC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Braking Resistor] (BRC) | [Ramp] (RAMP)
THB | DBR thermal state | 16#3722 = 14114 | 16#206F/F | 16#A7/01/73 = 167/01/115 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 118 % | [DBR thermal state] (THB) | [Braking Unit Option] (BUO) [Braking Resistor monit] (BRP)
BREC | Braking resistor energy counter | 16#3732 = 14130 | 16#206F/1F | 16#A7/01/83 = 167/01/131 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Braking Resistor Energy] (BREC) | [Braking Unit Option] (BUO)
RRTH | DBR run time | 16#373E = 14142 | 16#206F/2B | 16#A7/01/8F = 167/01/143 |  | Measurement parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
FBBT | BUO fan operation time | 16#373C = 14140 | 16#206F/29 | 16#A7/01/8D = 167/01/141 |  | Actual values parameters | R | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [BUO Fan Operation Time] (FBBT) | [Counter Management] (ELT) [Braking Unit Option] (BUO)
BSTB | BUO status | 16#9AF4 = 39668 |  |  | HMIS | Status parameters | R | WORD (Enumeration) | -
OT4Q | 4 Quadrant output torque value (100% = Cn motor) | 16#0CCE = 3278 | 16#2002/4F | 16#71/01/4F = 113/01/79 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
ST4Q | 4 Quadrant output torque value (% of Cn motor in Q12) without filter | 16#0CCF = 3279 | 16#2002/50 | 16#71/01/50 = 113/01/80 |  | Actual values parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
PTOH | PTO maximum output frequency | 16#1251 = 4689 | 16#2010/5A | 16#78/01/5A = 120/01/90 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | Refer to programming manual | 1.00 kHz ... 30.00 kHz | [PTO Max Output Freq] (PTOH) | [PTO Frequency] (PTOC) [PTO configuration] (PTO) [PTO configuration] (PTO)
PTO | PTO assignment | 16#13BA = 5050 | 16#2014/33 | 16#7A/01/33 = 122/01/51 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [PTO Assign] (PTO) | [PTO Frequency] (PTOC) [PTO configuration] (PTO) [PTO configuration] (PTO)
PTOC | PTO frequency | 16#14A9 = 5289 | 16#2016/5A | 16#7B/01/5A = 123/01/90 |  | I/O parameters | R/W | UINT (Unsigned16) | 0.01 kHz | 0.00 kHz | 0.00 kHz ... 655.35 kHz
PUC | Encoder pulse count | 16#15EB = 5611 | 16#201A/C | 16#7D/01/0C = 125/01/12 |  | Actual values parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
PUCD | Encoder pulse count (32 bits) | 16#1624 = 5668 | 16#201A/45 | 16#7D/01/45 = 125/01/69 |  | Actual values parameters | R | UINT (Unsigned32) | 1 |  | 0 ... 4294967295
SSCD | SSI code type | 16#15F4 = 5620 | 16#201A/15 | 16#7D/01/15 = 125/01/21 | SSCD | Configuration and settings | R/WS | WORD (Enumeration) | - | [Undefined] UND |  | [SSI code type] (SSCD) | [Encoder configuration] (IEN)
SSCP | SSI parity | 16#15F5 = 5621 | 16#201A/16 | 16#7D/01/16 = 125/01/22 | SSCP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Undefined] UND |  | [SSI parity] (SSCP) | [Encoder configuration] (IEN)
SSFS | SSI frame size | 16#15F6 = 5622 | 16#201A/17 | 16#7D/01/17 = 125/01/23 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | 0 ... 31 | [SSI frame size] (SSFS) | [Encoder configuration] (IEN)
ENMR | Number of revolutions | 16#15F7 = 5623 | 16#201A/18 | 16#7D/01/18 = 125/01/24 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | -1 | -1 ... 25 | [Nbr of revolutions] (ENMR) | [Encoder configuration] (IEN)
ENTR | Turn bit resolution | 16#15F8 = 5624 | 16#201A/19 | 16#7D/01/19 = 125/01/25 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | -1 | -1 ... 25 | [Turn bit resolution] (ENTR) | [Encoder configuration] (IEN)
REFQ | Resolver excitation frequency | 16#15FD = 5629 | 16#201A/1E | 16#7D/01/1E = 125/01/30 | REFQ | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 kHz] 8K |  | [Resolver Exct. Freq.] (REFQ) | [Encoder configuration] (IEN)
ENSP | Clock frequency | 16#15FB = 5627 | 16#201A/1C | 16#7D/01/1C = 125/01/28 | ENSP | Configuration and settings | R/WS | WORD (Enumeration) | - | [200 kHz] 200k |  | [Clock frequency] (ENSP) | [Encoder configuration] (IEN)
RPOS | Reset position assignment | 16#15FC = 5628 | 16#201A/1D | 16#7D/01/1D = 125/01/29 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Reset Position Assign] (RPOS) | [Encoder configuration] (IEN)
ABMF | AB encoder maximum frequency | 16#1600 = 5632 | 16#201A/21 | 16#7D/01/21 = 125/01/33 | ABMF | Configuration and settings | R/WS | WORD (Enumeration) | - | [300 kHz] 300K |  | [AB Encoder Max Freq] (ABMF) | [Encoder configuration] (IEN)
ENCR | Encoder resolution characteristic | 16#1642 = 5698 | 16#201A/63 | 16#7D/01/63 = 125/01/99 |  | Actual values parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NSL | Nominal motor slip | 16#2585 = 9605 | 16#2042/6 | 16#91/01/06 = 145/01/06 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 Hz |  | 0.0 Hz ... 6553.5 Hz | [Nominal motor slip] (NSL) | [data] (MTD)
TUNT | Autotuning type | 16#259A = 9626 | 16#2042/1B | 16#91/01/1B = 145/01/27 | TUNT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] STD |  | [Autotuning Type] (TUNT) | [Motor tune] (MTU)
SPD1 | Signed mechanical speed | 16#2EEC = 12012 | 16#205A/D | 16#9D/01/0D = 157/01/13 |  | Actual values parameters | R | INT (Signed32) | Refer to programming manual |  | -100000 ... 100000 | [Signed Mech Speed] (SPD1) | [Motor parameters] (MMO)
MSTP | Memo stop | 16#30EB = 12523 | 16#205F/18 | 16#9F/01/7C = 159/01/124 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Memo Stop] (MSTP) | [Positioning by sensors] (LPO)
PRST | Priority restart | 16#30EC = 12524 | 16#205F/19 | 16#9F/01/7D = 159/01/125 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Priority restart] (PRST) | [Positioning by sensors] (LPO)
MDCM | AFE bus reference link | 16#362E = 13870 | 16#206C/47 | 16#A6/01/47 = 166/01/71 | MDCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] NO |  | [AFE Bus Ref Link] (MDCM) | [DC-Bus Ref Link] (DBS)
DCBS | DC Bus source type | 16#362F = 13871 | 16#206C/48 | 16#A6/01/48 = 166/01/72 | DCBS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [DC Bus Source Type] (DCBS) | [DC-Bus Ref Link] (DBS)
BSCC | Backspin activation | 16#3728 = 14120 | 16#206F/15 | 16#A7/01/79 = 167/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [BS Activation] (BSCC) | [Backspin Control] (BSCC)
BVPL | Vbus reference for deceleration phase | 16#3729 = 14121 | 16#206F/16 | 16#A7/01/7A = 167/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 1130 V | [Deceleration Vbus Ref] (BVPL) | [Backspin Control] (BSCC)
BRS | Frequency threshold for DC Bus voltage control | 16#372A = 14122 | 16#206F/17 | 16#A7/01/7B = 167/01/123 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 Hz | -10.0 Hz | -599.0 Hz ... 599.0 Hz | [BS DCBus Reg Freq Thd] (BRS) | [Backspin Control] (BSCC)
BTS | Speed trigger for reverse | 16#372B = 14123 | 16#206F/18 | 16#A7/01/7C = 167/01/124 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 Hz | 10.0 Hz | -599.0 Hz ... 599.0 Hz | [Reverse Speed Trigger] (BTS) | [Backspin Control] (BSCC)
BZCD | Deceleration time for reverse | 16#372C = 14124 | 16#206F/19 | 16#A7/01/7D = 167/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 9999 | [Reverse Deceleration] (BZCD) | [Backspin Control] (BSCC)
RPTH | BUO power-on time | 16#3740 = 14144 | 16#206F/2D | 16#A7/01/91 = 167/01/145 |  | Measurement parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
BQM | Backlash mode | 16#41DC = 16860 | 16#208A/3D | 16#B5/01/3D = 181/01/61 | BQM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [BL Mode] (BQM) | [Backlash compensation] (BSQM)
BQFB | Response to backlash error | 16#41DD = 16861 | 16#208A/3E | 16#B5/01/3E = 181/01/62 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [BL ErrorResp] (BQFB) | [Backlash compensation] (BSQM)
BQSL | Backlash reference frequency | 16#41DF = 16863 | 16#208A/40 | 16#B5/01/40 = 181/01/64 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [BL Ref Freq] (BQSL) | [Backlash compensation] (BSQM)
BQA | Backlash acceleration | 16#41E0 = 16864 | 16#208A/41 | 16#B5/01/41 = 181/01/65 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 1 ... 9999 | [BL Acceleration] (BQA) | [Backlash compensation] (BSQM)
BQTL | Backlash torque limitation value | 16#41E1 = 16865 | 16#208A/42 | 16#B5/01/42 = 181/01/66 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 5.0 % | 0.0 % ... 100.0 % | [BL Trq Lim Value] (BQTL) | [Backlash compensation] (BSQM)
BQT | Backlash torque limitation monitoring delay | 16#41E2 = 16866 | 16#208A/43 | 16#B5/01/43 = 181/01/67 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 100.0 s | [BL Monit Delay] (BQT) | [Backlash compensation] (BSQM)
BQST | Backlash start delay | 16#41E3 = 16867 | 16#208A/44 | 16#B5/01/44 = 181/01/68 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 100.0 s | [BL Start Delay] (BQST) | [Backlash compensation] (BSQM)
BQFD | Backlash timeout | 16#41E4 = 16868 | 16#208A/45 | 16#B5/01/45 = 181/01/69 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | Refer to programming manual | 0.0 s ... 100.0 s | [BL Timeout] (BQFD) | [Backlash compensation] (BSQM)
BQMM | Backlash type | 16#41E6 = 16870 | 16#208A/47 | 16#B5/01/47 = 181/01/71 | BQMM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Sequential] SEQ |  | [BL Type] (BQMM) | [Backlash compensation] (BSQM)
BQMC | Backlash on slave(s) feedback | 16#41E7 = 16871 | 16#208A/48 | 16#B5/01/48 = 181/01/72 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [BL Slave Fdbck] (BQMC) | [Backlash compensation] (BSQM)
BQMT | Backlash time | 16#41E8 = 16872 | 16#208A/49 | 16#B5/01/49 = 181/01/73 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 100.0 s | [BL Time] (BQMT) | [Backlash compensation] (BSQM)
FDR0 | FDR error status | 16#FBB0 = 64432 |  |  | EFDR | Configuration management | R | WORD (Enumeration) | - |  |  | [FDR Error Status] (FDR0) | [Emb Eth FDR] (FDR)
FDS0 | FDR operating state | 16#FBB1 = 64433 |  |  | SFDR | Configuration management | R | WORD (Enumeration) | - |  |  | [FDR Operating State] (FDS0) | [Emb Eth FDR] (FDR)
FDA0 | FDR action | 16#FBB2 = 64434 |  |  | FDRA | Configuration management | R/W | WORD (Enumeration) | - | [NOT ACTIVE] IDLE |  | [FDR Action] (FDA0) | [Emb Eth FDR] (FDR)
FDV0 | Enable FDR function | 16#FBB3 = 64435 |  |  | N_Y | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable FDR] (FDV0) | [Emb Eth FDR] (FDR)
INF6 | Internal error 6 (Module identification error) information | 16#1BE1 = 7137 | 16#2029/26 | 16#84/01/8A = 132/01/138 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Error Info (INF6)] (INF6) | [Diag. data] (DDT)
INFJ | Internal error 19 (Encoder) | 16#1BE6 = 7142 | 16#2029/2B | 16#84/01/8F = 132/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Internal Error 19] (INFJ) | [Diag. data] (DDT)
ENCE | Encoder feedback error number | 16#1643 = 5699 | 16#201A/64 | 16#7D/01/64 = 125/01/100 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Encoder Fdbck Error] (ENCE) | [Diag. data] (DDT)
HS1 | HMI status | 16#1C99 = 7321 | 16#202B/16 | 16#85/01/7A = 133/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS1) | [None] (DP1)
HS2 | HMI status | 16#1C9A = 7322 | 16#202B/17 | 16#85/01/7B = 133/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS2) | [None] (DP2)
HS3 | HMI status | 16#1C9B = 7323 | 16#202B/18 | 16#85/01/7C = 133/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS3) | [None] (DP3)
HS4 | HMI status | 16#1C9C = 7324 | 16#202B/19 | 16#85/01/7D = 133/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS4) | [None] (DP4)
HS5 | HMI status | 16#1C9D = 7325 | 16#202B/1A | 16#85/01/7E = 133/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS5) | [None] (DP5)
HS6 | HMI status | 16#1C9E = 7326 | 16#202B/1B | 16#85/01/7F = 133/01/127 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS6) | [None] (DP6)
HS7 | HMI status | 16#1C9F = 7327 | 16#202B/1C | 16#85/01/80 = 133/01/128 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS7) | [None] (DP7)
HS8 | HMI status | 16#1CA0 = 7328 | 16#202B/1D | 16#85/01/81 = 133/01/129 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS8) | [None] (DP8)
AVS | ENA average speed | 16#2F46 = 12102 | 16#205B/3 | 16#9D/01/67 = 157/01/103 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [ENA avg speed] (AVS) | [Variable Speed Pump] (MPP)
MSS | M/S function status | 16#41C8 = 16840 | 16#208A/29 | 16#B5/01/29 = 181/01/41 | MSS | Status parameters | R | WORD (Enumeration) | - |  |  | [M/S Status] (MSS) | [M/S Local Display] (MSO)
MSMS | M/S Master speed reference | 16#41C9 = 16841 | 16#208A/2A | 16#B5/01/2A = 181/01/42 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -599.0 Hz ... 599.0 Hz | [M/S Master Speed Ref] (MSMS) | [M/S Local Display] (MSO)
MSMT | M/S Master torque reference | 16#41CA = 16842 | 16#208A/2B | 16#B5/01/2B = 181/01/43 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
MSSR | M/S Local speed reference | 16#41CB = 16843 | 16#208A/2C | 16#B5/01/2C = 181/01/44 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -599.0 Hz ... 599.0 Hz | [M/S Local Speed Ref] (MSSR) | [M/S Local Display] (MSO) [M/S System Display] (MSR)
MSTR | M/S Local torque reference | 16#41CC = 16844 | 16#208A/2D | 16#B5/01/2D = 181/01/45 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
OTQN | Motor torque in Nm | 16#0CC4 = 3268 | 16#2002/45 | 16#71/01/45 = 113/01/69 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor Torque (Nm)] (OTQN) | [M/S Local Display] (MSO) [Motor parameters] (MMO)
MSDN | M/S device selection | 16#41CD = 16845 | 16#208A/2E | 16#B5/01/2E = 181/01/46 | MSID | Configuration and settings | R/W | WORD (Enumeration) | - | [Master] MSTER |  | [M/S Device Selection] (MSDN) | [M/S System Display] (MSR)
MSDS | M/S device status | 16#41CE = 16846 | 16#208A/2F | 16#B5/01/2F = 181/01/47 | MSS | Status parameters | R | WORD (Enumeration) | - |  |  | [M/S Device Status] (MSDS) | [M/S System Display] (MSR)
MSXS | M/S device speed reference | 16#41D0 = 16848 | 16#208A/31 | 16#B5/01/31 = 181/01/49 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -599.0 Hz ... 599.0 Hz | [M/S Device Speed Ref] (MSXS) | [M/S System Display] (MSR)
MSXT | M/S device torque reference | 16#41CF = 16847 | 16#208A/30 | 16#B5/01/30 = 181/01/48 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
TQN | Computed nominal motor torque | 16#25C5 = 9669 | 16#2042/46 | 16#91/01/46 = 145/01/70 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual | 499 | 1 ... 65535 | [Nom Motor torque] (TQN) | [Motor parameters] (MMO) [data] (MTD)
LTR | Torque reference | 16#2139 = 8505 | 16#2037/6 | 16#8B/01/6A = 139/01/106 |  | Setpoint parameters | R/W | INT (Signed16) | 0.1 % | 0.0 % | -300.0 % ... 300.0 % | [Torque ref.] (LTR) | [Drive parameters] (MPI)
TRR | Torque reference before ramp | 16#240F = 9231 | 16#203E/20 | 16#8F/01/20 = 143/01/32 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Torque reference] (TRR) | [Drive parameters] (MPI)
SFQ | Stator frequency | 16#0CC3 = 3267 | 16#2002/44 | 16#71/01/44 = 113/01/68 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.8 Hz ... 3276.7 Hz | [Stator Frequency] (SFQ) | [Drive parameters] (MPI)
RFQ | Rotor frequency | 16#0CC2 = 3266 | 16#2002/43 | 16#71/01/43 = 113/01/67 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.8 Hz ... 3276.7 Hz | [Rotor Frequency] (RFQ) | [Drive parameters] (MPI)
UL1 | Mains voltage phase 1-2 | 16#35B3 = 13747 | 16#206B/30 | 16#A5/01/94 = 165/01/148 |  | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 1-2] (UL1) | [Drive parameters] (MPI)
UL2 | Mains voltage phase 2-3 | 16#35B4 = 13748 | 16#206B/31 | 16#A5/01/95 = 165/01/149 |  | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 2-3] (UL2) | [Drive parameters] (MPI)
UL3 | Mains voltage phase 3-1 | 16#35B5 = 13749 | 16#206B/32 | 16#A5/01/96 = 165/01/150 |  | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 3-1] (UL3) | [Drive parameters] (MPI)
THEV | Encoder thermal value | 16#161F = 5663 | 16#201A/40 | 16#7D/01/40 = 125/01/64 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Enc Th Value] (THEV) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THER | Encoder thermal resistor value | 16#161E = 5662 | 16#201A/3F | 16#7D/01/3F = 125/01/63 |  | Measurement parameters | R | INT (Signed16) | 1 Ohm |  | -32767 Ohm ... 32767 Ohm | [Enc Resistor Value] (THER) | [Analog inputs image] (AIA)
APPT | Application selection | 16#3D53 = 15699 | 16#207E/64 | 16#AF/01/64 = 175/01/100 | APPT | Configuration and settings | R/WS | WORD (Enumeration) | - | [All application functions available] ALL |  | [Application Selection] (APPT) | [Macro Configuration] (MCR)
MPC | Motor parameter choice | 16#258E = 9614 | 16#2042/F | 16#91/01/0F = 145/01/15 | MPC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Nominal motor power] NPR |  | [Motor param choice] (MPC) | [data] (MTD)
CRFA | Internal currents filter time | 16#239E = 9118 | 16#203D/13 | 16#8E/01/77 = 142/01/119 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms |  | 0.0 ms ... 100.0 ms | [Currents Filter] (CRFA) | [data] (MTD)
RDAE | Relative d-axis error in % | 16#25CC = 9676 | 16#2042/4D | 16#91/01/4D = 145/01/77 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Relative d-axis error] (RDAE) | [data] (MTD)
TUNU | Autotuning usage | 16#2593 = 9619 | 16#2042/14 | 16#91/01/14 = 145/01/20 | TUNU | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Autotuning Usage] (TUNU) | [Motor tune] (MTU)
TCR | Level of current for autotuning | 16#259B = 9627 | 16#2042/1C | 16#91/01/1C = 145/01/28 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Autotuning Lvl Of Current] (TCR) | [Motor tune] (MTU)
RCL | Alignment rotational current level | 16#3668 = 13928 | 16#206D/1D | 16#A6/01/81 = 166/01/129 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 75 % | 10 % ... 300 % | [Rotational Current Level] (RCL) | [Motor tune] (MTU)
RCIR | RCI alignment with transformer | 16#366A = 13930 | 16#206D/1F | 16#A6/01/83 = 166/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [RCI With Transformer] (RCIR) | [Motor tune] (MTU)
RCSP | RCI maximum output frequency | 16#366B = 13931 | 16#206D/20 | 16#A6/01/84 = 166/01/132 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 Hz | RCSP_AUTO | -0.1 Hz ... 599.0 Hz | [RCI Max Freq] (RCSP) | [Motor tune] (MTU)
THET | Encoder thermal sensor type | 16#161D = 5661 | 16#201A/3E | 16#7D/01/3E = 125/01/62 | THET | Configuration and settings | R/WS | WORD (Enumeration) | - | [None] NONE |  | [Enc Therm Sensor Type] (THET) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THEB | Response to thermal error for encoder | 16#1622 = 5666 | 16#201A/43 | 16#7D/01/43 = 125/01/67 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [Enc Th ErrorResp] (THEB) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THEF | Thermal error level for encoder | 16#1621 = 5665 | 16#201A/42 | 16#7D/01/42 = 125/01/66 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [Enc Th Error Level] (THEF) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THEA | Thermal warning level for encoder | 16#1620 = 5664 | 16#201A/41 | 16#7D/01/41 = 125/01/65 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [Enc Th Warn Level] (THEA) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
BOO | Boost | 16#3658 = 13912 | 16#206D/D | 16#A6/01/71 = 166/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | Refer to programming manual | -100 % ... 100 % | [Boost] (BOO) | [Motor control] (DRC)
BOO2 | Boost on deceleration | 16#3659 = 13913 | 16#206D/E | 16#A6/01/72 = 166/01/114 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | -25 % | -100 % ... 0 % | [Boost On Deceleration] (BOO2) | [Motor control] (DRC)
FAB | Frequency boost | 16#3657 = 13911 | 16#206D/C | 16#A6/01/70 = 166/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Freq Boost] (FAB) | [Motor control] (DRC)
TEFF | External feed forward assignment | 16#23AA = 9130 | 16#203D/1F | 16#8E/01/83 = 142/01/131 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [External FeedFwd Assign] (TEFF) | [Spd Loop Optimization] (MCL)
FRI | Frequency of the HF injection signal | 16#3CF1 = 15601 | 16#207E/2 | 16#AF/01/02 = 175/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 500 Hz | 250 Hz ... 1000 Hz | [HF injection freq.] (FRI) | [Motor control] (DRC)
MSCM | M/S communication mode | 16#41A0 = 16800 | 16#208A/1 | 16#B5/01/01 = 181/01/01 | MSCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [M/S Comm Mode] (MSCM) | [M/S System Architecture] (MSA)
MSID | Master or slave ID selection | 16#41A1 = 16801 | 16#208A/2 | 16#B5/01/02 = 181/01/02 | MSID | Configuration and settings | R/WS | WORD (Enumeration) | - | [Master] MSTER |  | [M/S Device ID] (MSID) | [M/S System Architecture] (MSA)
MSDT | Master or slave selection | 16#41A2 = 16802 | 16#208A/3 | 16#B5/01/03 = 181/01/03 | MSDT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Master] MSTER |  | [M/S Device Role] (MSDT) | [M/S System Architecture] (MSA)
MSSN | M/S number of slaves | 16#41A3 = 16803 | 16#208A/4 | 16#B5/01/04 = 181/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 10 | [M/S Number of Slaves] (MSSN) | [M/S System Architecture] (MSA)
MSSI | M/S Master speed reference input assignment | 16#41A4 = 16804 | 16#208A/5 | 16#B5/01/05 = 181/01/05 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [M/S Speed Ref In Assign] (MSSI) | [M/S System Architecture] (MSA)
MSTI | M/S Master torque reference input assignment | 16#41A6 = 16806 | 16#208A/7 | 16#B5/01/07 = 181/01/07 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [M/S Trq Ref In Assign] (MSTI) | [M/S System Architecture] (MSA)
MSSO | M/S speed reference output assignment | 16#41A5 = 16805 | 16#208A/6 | 16#B5/01/06 = 181/01/06 | CSA | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [M/S Speed Ref Out Assign] (MSSO) | [M/S System Architecture] (MSA)
MSTO | M/S torque reference output assignment | 16#41A7 = 16807 | 16#208A/8 | 16#B5/01/08 = 181/01/08 | CSA | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [M/S Trq Ref Out Assign] (MSTO) | [M/S System Architecture] (MSA)
MSDI | M/S local mode assignment | 16#41A8 = 16808 | 16#208A/9 | 16#B5/01/09 = 181/01/09 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [M/S Local Mode Assign] (MSDI) | [M/S System Architecture] (MSA)
MLTO | MultiDrive Link communication timeout | 16#17C5 = 6085 | 16#201E/56 | 16#7F/01/56 = 127/01/86 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.05 s | 0.01 s ... 10.00 s | [MDL Comm Timeout] (MLTO) | [M/S System Architecture] (MSA)
MSCB | M/S Response to communication error | 16#41A9 = 16809 | 16#208A/A | 16#B5/01/0A = 181/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [M/S Comm ErrorResp] (MSCB) | [M/S System Architecture] (MSA)
MSDB | M/S Response to device error | 16#41AA = 16810 | 16#208A/B | 16#B5/01/0B = 181/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [M/S Device ErrorResp] (MSDB) | [M/S System Architecture] (MSA)
MSDD | M/S device error delay | 16#41AB = 16811 | 16#208A/C | 16#B5/01/0C = 181/01/12 |  | Configuration and settings | R/WS | INT (Signed16) | 1 s | -1 s | -1 s ... 60 s | [M/S Device Error Delay] (MSDD) | [M/S System Architecture] (MSA)
MSMC | M/S mechanical coupling type | 16#41B4 = 16820 | 16#208A/15 | 16#B5/01/15 = 181/01/21 | MSMC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Rigid coupling] RIGID |  | [M/S Coupling Type] (MSMC) | [M/S Control] (MST)
MSCT | M/S control type | 16#41B5 = 16821 | 16#208A/16 | 16#B5/01/16 = 181/01/22 | MSCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Direct torque control] TRQD |  | [M/S Control Type] (MSCT) | [M/S Control] (MST)
SSD | Speed reference direction | 16#41D1 = 16849 | 16#208A/32 | 16#B5/01/32 = 181/01/50 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Speed Ref Direction] (SSD) | [M/S Torque Control] (MSQ)
TQOP | Torque reference offset | 16#2412 = 9234 | 16#203E/23 | 16#8F/01/23 = 143/01/35 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -1000.0 % ... 1000.0 % | [Torque Ref Offset] (TQOP) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TRF | Torque filter activation | 16#2414 = 9236 | 16#203E/25 | 16#8F/01/25 = 143/01/37 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Torque Filter] (TRF) | [Torque control] (TOR) [M/S Control] (MST)
TRW | Torque filter bandwidth | 16#2415 = 9237 | 16#203E/26 | 16#8F/01/26 = 143/01/38 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 Hz | 20 Hz | 1 Hz ... 1000 Hz | [Torque Filter Bandwidth] (TRW) | [Torque control] (TOR) [M/S Control] (MST)
MSFE | M/S advanced filter activation | 16#41BE = 16830 | 16#208A/1F | 16#B5/01/1F = 181/01/31 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [M/S Advanced Filter] (MSFE) | [M/S Filters] (MSF)
MSFF | M/S advanced filter frequency | 16#41BF = 16831 | 16#208A/20 | 16#B5/01/20 = 181/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 10.0 Hz ... 150.0 Hz | [M/S Advanced Filter Freq] (MSFF) | [M/S Filters] (MSF)
MSFB | M/S advanced filter bandwidth | 16#41C0 = 16832 | 16#208A/21 | 16#B5/01/21 = 181/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 10 % ... 400 % | [M/S Advanced Filter Bdw] (MSFB) | [M/S Filters] (MSF)
MSFD | M/S advanced filter depth | 16#41C1 = 16833 | 16#208A/22 | 16#B5/01/22 = 181/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 99 % | [M/S Advanced Filter Depth] (MSFD) | [M/S Filters] (MSF)
MSFG | M/S advanced filter gain | 16#41C2 = 16834 | 16#208A/23 | 16#B5/01/23 = 181/01/35 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 1000 % | [M/S Advanced Filter Gain] (MSFG) | [M/S Filters] (MSF)
MSFC | M/S advanced filter coefficient | 16#41C3 = 16835 | 16#208A/24 | 16#B5/01/24 = 181/01/36 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 1000 % | [M/S Advanced Filter Coeff] (MSFC) | [M/S Filters] (MSF)
MSIB | M/S load balancing torque reference selection | 16#41BC = 16828 | 16#208A/1D | 16#B5/01/1D = 181/01/29 | MSTS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Before advanced filter] BFILT |  | [M/S Balance Trq Ref Sel] (MSIB) | [Load Sharing M/S] (MSB)
MSIT | M/S Master torque reference entry in control chain | 16#41BA = 16826 | 16#208A/1B | 16#B5/01/1B = 181/01/27 | MSTS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Before advanced filter] BFILT |  | [M/S Torque Ref Entry] (MSIT) | [M/S Control] (MST)
MSOT | M/S output torque reference selection | 16#41BB = 16827 | 16#208A/1C | 16#B5/01/1C = 181/01/28 | MSTS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Before advanced filter] BFILT |  | [M/S Out Torque Ref Select] (MSOT) | [M/S Control] (MST)
MSIS | M/S Master speed reference entry in control chain | 16#41B8 = 16824 | 16#208A/19 | 16#B5/01/19 = 181/01/25 | MSSS | Configuration and settings | R/WS | WORD (Enumeration) | - | [After ramp] ARMP |  | [M/S Speed Ref Entry] (MSIS) | [M/S Control] (MST)
MSOS | M/S output speed reference selection | 16#41B9 = 16825 | 16#208A/1A | 16#B5/01/1A = 181/01/26 | MSSS | Configuration and settings | R/WS | WORD (Enumeration) | - | [After ramp] ARMP |  | [M/S Out Speed Ref Select] (MSOS) | [M/S Control] (MST)
TPMM | Maximum power in motor mode | 16#2400 = 9216 | 16#203E/11 | 16#8F/01/11 = 143/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 10 % ... 300 % | [Pmax Motor] (TPMM) | [Torque limitation] (TOL) [Settings] (SET)
TPMG | Maximum power in generator mode | 16#2401 = 9217 | 16#203E/12 | 16#8F/01/12 = 143/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 10 % ... 300 % | [Pmax Generator] (TPMG) | [Torque limitation] (TOL) [Settings] (SET)
PTOL | PTO min output frequency | 16#1250 = 4688 | 16#2010/59 | 16#78/01/59 = 120/01/89 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | Refer to programming manual | 1.00 kHz ... 30.00 kHz | [PTO Min Output Freq] (PTOL) | [PTO configuration] (PTO) [PTO configuration] (PTO)
TRES | Resolver transformation ratio | 16#15F3 = 5619 | 16#201A/14 | 16#7D/01/14 = 125/01/20 | TRES | Configuration and settings | R/WS | WORD (Enumeration) | - | [0.5] 05 |  | [Transformation ratio] (TRES) | [Encoder configuration] (IEN)
UELC | Sincos lines count | 16#15F1 = 5617 | 16#201A/12 | 16#7D/01/12 = 125/01/18 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 10000 | [Sincos lines count] (UELC) | [Encoder configuration] (IEN)
TOST | Stop on next top Z detection | 16#2BE8 = 11240 | 16#2052/29 | 16#99/01/29 = 153/01/41 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Stop on top Z] (TOST) | [Encoder configuration] (IEN)
TLOL | Drive overload monitoring activation | 16#1B77 = 7031 | 16#2028/20 | 16#84/01/20 = 132/01/32 | TLOL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Drive Overload Monit] (TLOL) | [Drive overload monit] (OBR)
TWO | Terminal Modbus: Word order | 16#1776 = 6006 | 16#201E/7 | 16#7F/01/07 = 127/01/07 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term word order] (TWO) | [Modbus Fieldbus] (MD1)
TWO2 | Terminal Modbus 2: Word order | 16#178A = 6026 | 16#201E/1B | 16#7F/01/1B = 127/01/27 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term 2 word order] (TWO2) | [Modbus HMI] (MD2)
FDR1 | FDR error status | 16#FBBA = 64442 |  |  | EFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Error Status] (FDR1) | [Opt Eth FDR] (FDRO)
FDS1 | FDR operating state | 16#FBBB = 64443 |  |  | SFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Operating State] (FDS1) | [Opt Eth FDR] (FDRO)
FDA1 | FDR action | 16#FBBC = 64444 |  |  | FDRA | Configuration and settings | R/W | WORD (Enumeration) | - | [NOT ACTIVE] IDLE |  | [FDR Action] (FDA1) | [Opt Eth FDR] (FDRO)
FDV1 | Enable FDR function | 16#FBBD = 64445 |  |  | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable FDR] (FDV1) | [Opt Eth FDR] (FDRO)
CIC2 | Incorrect configuration 2 | 16#1C16 = 7190 | 16#2029/5B | 16#84/01/BF = 132/01/191 |  | Fault parameters | R/WS | WORD (BitString16) | -
ST20 | Status registers 20 | 16#3EF8 = 16120 | 16#2083/15 | 16#B1/01/79 = 177/01/121 |  | Status parameters | R | WORD (BitString16) | -
PSA1 | Control Scope Assignment 1 | 16#F69A = 63130 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 6 | 0 ... 65535
PSA2 | Control Scope Assignment 2 | 16#F69B = 63131 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 7 | 0 ... 65535
PSA3 | Control Scope Assignment 3 | 16#F69C = 63132 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 9 | 0 ... 65535
PSA4 | Control Scope Assignment 4 | 16#F69D = 63133 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 2 | 0 ... 65535
PSD1 | Control Scope Data 1 | 16#F69E = 63134 |  |  |  | Actual values parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
PSD2 | Control Scope Data 2 | 16#F69F = 63135 |  |  |  | Actual values parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
PSD3 | Control Scope Data 3 | 16#F6A0 = 63136 |  |  |  | Actual values parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
PSD4 | Control Scope Data 4 | 16#F6A1 = 63137 |  |  |  | Actual values parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
PSST | Password status | 16#1F72 = 8050 | 16#2032/33 | 16#89/01/33 = 137/01/51 | PSST | Status parameters | R | WORD (Enumeration) | - |  |  | [Password status] (PSST) | [Password] (COD)
ULR | Upload rights | 16#1F69 = 8041 | 16#2032/2A | 16#89/01/2A = 137/01/42 | ULR | Configuration and settings | R/W | WORD (Enumeration) | - | [Upload access allowed] ULR0 |  | [Upload rights] (ULR) | [Password] (COD)
DLR | Download rights | 16#1F6A = 8042 | 16#2032/2B | 16#89/01/2B = 137/01/43 | DLR | Configuration and settings | R/W | WORD (Enumeration) | - | [Drive unlocked] DLR1 |  | [Download rights] (DLR) | [Password] (COD)
PSRT | Drive Systems pre-settings unlock | 16#1F7E = 8062 | 16#2032/3F | 16#89/01/3F = 137/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Pre-settings Unlock] (PSRT) | [Pre-settings] (PRES)
AV1A | AIV1 assignment | 16#12FD = 4861 | 16#2012/3E | 16#79/01/3E = 121/01/62 | CSA | Configuration and settings | R | WORD (Enumeration) | - |  |  | [AIV1 assignment] (AV1A) | [AIV1 assignment] (AV1A) [Virtual AI1] (AV1)
LFR1 | Modbus reference frequency | 16#2149 = 8521 | 16#2037/16 | 16#8B/01/7A = 139/01/122 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Modbus Ref Freq] (LFR1) | [Freq. ref. word map] (RWI)
LFR2 | CANopen reference frequency | 16#214A = 8522 | 16#2037/17 | 16#8B/01/7B = 139/01/123 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [CAN Ref Freq] (LFR2) | [Freq. ref. word map] (RWI)
LFR3 | Communication module reference frequency | 16#214B = 8523 | 16#2037/18 | 16#8B/01/7C = 139/01/124 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Com Module Ref Freq] (LFR3) | [Freq. ref. word map] (RWI)
LFR5 | Embedded ethernet reference frequency | 16#214D = 8525 | 16#2037/1A | 16#8B/01/7E = 139/01/126 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Ethernet Embd Ref Freq] (LFR5) | [Freq. ref. word map] (RWI)
HRFC | Extended fault reset activation | 16#1BEE = 7150 | 16#2029/33 | 16#84/01/97 = 132/01/151 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Extended Fault Reset] (HRFC) | [Fault reset] (RST)
AFFL | Fieldbus communication loss fallback channel | 16#1B70 = 7024 | 16#2028/19 | 16#84/01/19 = 132/01/25 | AFFL | Configuration and settings | R/W | WORD (Enumeration) | - | [Not active] NO |  | [Fallback Channel] (AFFL) | [Fieldbus monitoring] (CLL) [Embedded modbus TCP] (EMTC) [Communication Module] (COMO)
INLF | AI loss inhibition | 16#1B72 = 7026 | 16#2028/1B | 16#84/01/1B = 132/01/27 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI Loss Inhibition] (INLF) | [4-20 mA loss] (LFL)
R60 | R60 assignment | 16#13B0 = 5040 | 16#2014/29 | 16#7A/01/29 = 122/01/41 | PSL | Configuration and settings | R | WORD (Enumeration) | - | Refer to programming manual |  | [R60 Assignment] (R60) | [R60 configuration] (R60)
R61 | R61 assignment | 16#13B1 = 5041 | 16#2014/2A | 16#7A/01/2A = 122/01/42 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R61 Assignment] (R61) | [R61 configuration] (R61)
R62 | R62 assignment | 16#13B2 = 5042 | 16#2014/2B | 16#7A/01/2B = 122/01/43 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R62 Assignment] (R62) | [R62 configuration] (R62)
R63 | R63 assignment | 16#13B3 = 5043 | 16#2014/2C | 16#7A/01/2C = 122/01/44 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R63 Assignment] (R63) | [R63 configuration] (R63)
R64 | R64 assignment | 16#13B4 = 5044 | 16#2014/2D | 16#7A/01/2D = 122/01/45 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R64 Assignment] (R64) | [R64 configuration] (R64)
R65 | R65 assignment | 16#13B5 = 5045 | 16#2014/2E | 16#7A/01/2E = 122/01/46 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R65 Assignment] (R65) | [R65 configuration] (R65)
R66 | R66 assignment | 16#13B6 = 5046 | 16#2014/2F | 16#7A/01/2F = 122/01/47 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R66 Assignment] (R66) | [R66 configuration] (R66)
P24D | Cabinet I/O 24V missing error timeout | 16#414A = 16714 | 16#2089/F | 16#B4/01/73 = 180/01/115 |  | Configuration and settings | R/WS | INT (Signed16) | 1 s | Refer to programming manual | -1 s ... 3000 s | [Cab I/O 24V Timeout] (P24D) | [Error/Warning handling] (CSWM) [Cabinet I/O functions] (CABF)
TQTF | Torque filter time | 16#3718 = 14104 | 16#206F/5 | 16#A7/01/69 = 167/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 ms | 0.0 ms | 0.0 ms ... 100.0 ms | [Tq Corr. Filter Time] (TQTF) | [Input Filter] (DCR)
FWBW | Field weakening correction bandwidth | 16#3719 = 14105 | 16#206F/6 | 16#A7/01/6A = 167/01/106 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | -0.1 Hz | -0.1 Hz ... 100.0 Hz | [Field Weak. Corr. BW] (FWBW) | [Input Filter] (DCR)
BDCL | Maximum braking current level | 16#3746 = 14150 | 16#206F/33 | 16#A7/01/97 = 167/01/151 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 500.0 % | [Braking Current Level] (BDCL) | [Ramp] (RAMP)
SYTM | Synchro to mains selection | 16#41F0 = 16880 | 16#208A/51 | 16#B5/01/51 = 181/01/81 | SYTM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Function inactive] NOSM |  | [SM Selection] (SYTM) | [Synchro. To Mains] (SYTM)
SMAD | Synchro to mains angle damping coefficient | 16#41F1 = 16881 | 16#208A/52 | 16#B5/01/52 = 181/01/82 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | 1.00 | 0.00 ... 10.00 | [SM Angle Damp coef.] (SMAD) | [Synchro. To Mains] (SYTM)
SMAB | Synchro to mains angle bandwidth | 16#41F2 = 16882 | 16#208A/53 | 16#B5/01/53 = 181/01/83 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 Hz | 0.10 Hz | 0.10 Hz ... 1.00 Hz | [SM Angle Bandwidth] (SMAB) | [Synchro. To Mains] (SYTM)
SMAP | Synchro to mains angle phase-shift | 16#41F3 = 16883 | 16#208A/54 | 16#B5/01/54 = 181/01/84 |  | Configuration and settings | R/W | INT (Signed16) | 0.01 ° | 0.00 ° | -180.00 ° ... 180.00 ° | [SM Angle Phase-shift] (SMAP) | [Synchro. To Mains] (SYTM)
SMMB | Synchro to mains magnitude bandwidth | 16#41F4 = 16884 | 16#208A/55 | 16#B5/01/55 = 181/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 Hz | 0.10 Hz | 0.10 Hz ... 1.00 Hz | [SM Magn. Bandwidth] (SMMB) | [Synchro. To Mains] (SYTM)
SMST | Synchro to mains stabilization time | 16#41F6 = 16886 | 16#208A/57 | 16#B5/01/57 = 181/01/87 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 2.0 s | 0.1 s ... 10.0 s | [SM Stabilization Time] (SMST) | [Synchro. To Mains] (SYTM)
SMFT | Synchro to mains error timeout | 16#41FA = 16890 | 16#208A/5B | 16#B5/01/5B = 181/01/91 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 120.0 s | 0.0 s ... 1000.0 s | [SM Timeout] (SMFT) | [Synchro. To Mains] (SYTM)
SLPC | Slip compensation strategy in Generator mode | 16#25A6 = 9638 | 16#2042/27 | 16#91/01/27 = 145/01/39 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [None] (SLPC) | [Appli. hidden menu] (APW)
TQNC | Nominal motor torque scaling | 16#25D7 = 9687 | 16#2042/58 | 16#91/01/58 = 145/01/88 | TQNC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Expert] OPTI |  | [Nom Motor Tq Scaling] (TQNC) | [data] (MTD)
TQNO | Expert nominal motor torque | 16#25D8 = 9688 | 16#2042/59 | 16#91/01/59 = 145/01/89 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Expert Motor Tq] (TQNO) | [data] (MTD)
TQNP | Nameplate nominal motor torque | 16#25D9 = 9689 | 16#2042/5A | 16#91/01/5A = 145/01/90 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Plate Nom Motor Tq] (TQNP) | [data] (MTD)
AEMC | Advanced motor control | 16#25A4 = 9636 | 16#2042/25 | 16#91/01/25 = 145/01/37 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Adv. Motor Control] (AEMC) | [Motor parameters] (MPA)
PTR | Profidrive profile - RFG Tolerance parameter | 16#2340 = 9024 | 16#203C/19 | 16#8E/01/19 = 142/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Profidrive - Tolerance] (PTR) | [Ramp] (RAMP)
PTM | Profidrive profile - RFG Tmax parameter | 16#2341 = 9025 | 16#203C/1A | 16#8E/01/1A = 142/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 9999 | [Profidrive - Tmax] (PTM) | [Ramp] (RAMP)
M1EC | Mdb CRC errors | 16#177A = 6010 | 16#201E/B | 16#7F/01/0B = 127/01/11 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb CRC errors] (M1EC) | [Modbus network diag] (MND)
M2EC | Mdb NET CRC errors | 16#178E = 6030 | 16#201E/1F | 16#7F/01/1F = 127/01/31 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb Net CRC errors] (M2EC) | [Modbus HMI Diag] (MDH)
M1CT | Mdb frame number | 16#177B = 6011 | 16#201E/C | 16#7F/01/0C = 127/01/12 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb Frame Nb] (M1CT) | [Modbus network diag] (MND)
M2CT | Mdb NET frames | 16#178F = 6031 | 16#201E/20 | 16#7F/01/20 = 127/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb Net frames] (M2CT) | [Modbus HMI Diag] (MDH)
COM1 | Modbus com. status | 16#FA2F = 64047 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM1) | [Modbus Fieldbus] (MD1)
COM2 | Mdb com stat | 16#FA30 = 64048 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM2) | [Modbus HMI] (MD2)
TWOP | Profinet ModbusTCP word order | 16#FB1E = 64286 |  |  | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [PNT Mdb Word Order] (TWOP) | [Profinet] (PNC)
IPAV | iPar service activation | 16#FB12 = 64274 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Activation] (IPAV) | [Profinet] (PNC)
IPAS | iPar autosave activation | 16#FB13 = 64275 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Autosave Act] (IPAS) | [Profinet] (PNC)
ICFG | iPAR local configuration | 16#FB14 = 64276 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Local Conf] (ICFG) | [Profinet] (PNC)
IPAF | iPar response to detected error | 16#FB15 = 64277 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [iPar Error Response] (IPAF) | [Profinet] (PNC)
IPAT | iPar autosave timer | 16#FB16 = 64278 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 0 ... 9999 | [iPar Autosave Timer] (IPAT) | [Profinet] (PNC)
IPAE | iPar service status | 16#FB17 = 64279 |  |  | IPAE | Configuration and settings | R/W | WORD (Enumeration) | - | [Idle State] IDLE |  | [iPar Status] (IPAE) | [Profinet diag] (PRN)
IPAA | IPAR action | 16#FB1C = 64284 |  |  | IPAA | Configuration and settings | R/W | WORD (Enumeration) | - | [Inactive] DEAC |  | [IPAR Action] (IPAA) | [Profinet] (PNC)
IPAC | IPAR action status | 16#FB1D = 64285 |  |  | IPAC | Configuration and settings | R | WORD (Enumeration) | - | [In Progress] EXEC |  | [IPAR Action Status] (IPAC) | [Profinet] (PNC)
IPAM | IPAR configuration selection | 16#FB1F = 64287 |  |  | IPAM | Configuration and settings | R/W | WORD (Enumeration) | - | [Active drive configuration] ACTI |  | [IPAR Config Selection] (IPAM) | [Profinet] (PNC)
PNU | PNU 1000 behavior | 16#FB20 = 64288 |  |  | PNU | Configuration and settings | R/W | WORD (Enumeration) | - | [Conformance mode] PROF |  | [PNU 1000 Behavior] (PNU) | [Profinet] (PNC)
ST0A | Embedded RSTP actual configuration | 16#45EC = 17900 | 16#2095/1 | 16#BA/01/65 = 186/01/101 | STAC | Status parameters | R | WORD (Enumeration) | - |  |  | [eRSTP Actual Config] (ST0A) | [RSTP configuration] (RSTP)
ST1A | RSTP option module actual configuration | 16#45F1 = 17905 | 16#2095/6 | 16#BA/01/6A = 186/01/106 | STAC | Status parameters | R | WORD (Enumeration) | - |  |  | [oRSTP Actual Config] (ST1A) | [RSTP configuration] (RSTO)
ST0C | Embedded RSTP configuration | 16#45ED = 17901 | 16#2095/2 | 16#BA/01/66 = 186/01/102 | STAC | Configuration and settings | R/W | WORD (Enumeration) | - |  |  | [eRSTP Config] (ST0C) | [RSTP configuration] (RSTP)
ST1C | RSTP option module configuration | 16#45F2 = 17906 | 16#2095/7 | 16#BA/01/6B = 186/01/107 | STAC | Configuration and settings | R/W | WORD (Enumeration) | - |  |  | [oRSTP Config] (ST1C) | [RSTP configuration] (RSTO)
ST0S | Embedded RSTP service status | 16#45EE = 17902 | 16#2095/3 | 16#BA/01/67 = 186/01/103 | STS | Status parameters | R | WORD (Enumeration) | - |  |  | [eRSTP Status] (ST0S) | [RSTP configuration] (RSTP)
ST1S | RSTP option module service status | 16#45F3 = 17907 | 16#2095/8 | 16#BA/01/6C = 186/01/108 | STS | Status parameters | R | WORD (Enumeration) | - |  |  | [oRSTP Status] (ST1S) | [RSTP configuration] (RSTO)
ST0V | Embedded RSTP modification status | 16#45EF = 17903 | 16#2095/4 | 16#BA/01/68 = 186/01/104 | STV | Status parameters | R | WORD (Enumeration) | - |  |  | [eRSTP Modif Status] (ST0V) | [RSTP configuration] (RSTP)
ST1V | RSTP option module modification status | 16#45F4 = 17908 | 16#2095/9 | 16#BA/01/6D = 186/01/109 | STV | Status parameters | R | WORD (Enumeration) | - |  |  | [oRSTP Modif Status] (ST1V) | [RSTP configuration] (RSTO)
REC1 | RX error counter | 16#17AB = 6059 | 16#201E/3C | 16#7F/01/3C = 127/01/60 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [RX Error Counter] (REC1) | [CANopen map] (CNM)
TEC1 | TX error counter | 16#17AA = 6058 | 16#201E/3B | 16#7F/01/3B = 127/01/59 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [TX Error Counter] (TEC1) | [CANopen map] (CNM)
NMTS | Canopen NMT state | 16#17A9 = 6057 | 16#201E/3A | 16#7F/01/3A = 127/01/58 | NMTS | Status parameters | R | WORD (Enumeration) | - |  |  | [Canopen NMT state] (NMTS) | [CANopen map] (CNM)
RP11 | Receive PDO1-1 | 16#32F1 = 13041 | 16#2064/2A | 16#A2/01/2A = 162/01/42 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-1] (RP11) | [PDO1 image] (P01)
RP12 | Receive PDO1-2 | 16#32F2 = 13042 | 16#2064/2B | 16#A2/01/2B = 162/01/43 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-2] (RP12) | [PDO1 image] (P01)
RP13 | Receive PDO1-3 | 16#32F3 = 13043 | 16#2064/2C | 16#A2/01/2C = 162/01/44 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-3] (RP13) | [PDO1 image] (P01)
RP14 | Receive PDO1-4 | 16#32F4 = 13044 | 16#2064/2D | 16#A2/01/2D = 162/01/45 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-4] (RP14) | [PDO1 image] (P01)
TP11 | Transmit PDO1-1 | 16#32FB = 13051 | 16#2064/34 | 16#A2/01/34 = 162/01/52 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-1] (TP11) | [PDO1 image] (P01)
TP12 | Transmit PDO1-2 | 16#32FC = 13052 | 16#2064/35 | 16#A2/01/35 = 162/01/53 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-2] (TP12) | [PDO1 image] (P01)
TP13 | Transmit PDO1-3 | 16#32FD = 13053 | 16#2064/36 | 16#A2/01/36 = 162/01/54 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-3] (TP13) | [PDO1 image] (P01)
TP14 | Transmit PDO1-4 | 16#32FE = 13054 | 16#2064/37 | 16#A2/01/37 = 162/01/55 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-4] (TP14) | [PDO1 image] (P01)
RP21 | Receive PDO2-1 | 16#32DD = 13021 | 16#2064/16 | 16#A2/01/16 = 162/01/22 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-1] (RP21) | [PDO2 image] (P02)
RP22 | Receive PDO2-2 | 16#32DE = 13022 | 16#2064/17 | 16#A2/01/17 = 162/01/23 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-2] (RP22) | [PDO2 image] (P02)
RP23 | Receive PDO2-3 | 16#32DF = 13023 | 16#2064/18 | 16#A2/01/18 = 162/01/24 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-3] (RP23) | [PDO2 image] (P02)
RP24 | Receive PDO2-4 | 16#32E0 = 13024 | 16#2064/19 | 16#A2/01/19 = 162/01/25 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-4] (RP24) | [PDO2 image] (P02)
TP21 | Transmit PDO2-1 | 16#32E7 = 13031 | 16#2064/20 | 16#A2/01/20 = 162/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-1] (TP21) | [PDO2 image] (P02)
TP22 | Transmit PDO2-2 | 16#32E8 = 13032 | 16#2064/21 | 16#A2/01/21 = 162/01/33 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-2] (TP22) | [PDO2 image] (P02)
TP23 | Transmit PDO2-3 | 16#32E9 = 13033 | 16#2064/22 | 16#A2/01/22 = 162/01/34 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-3] (TP23) | [PDO2 image] (P02)
TP24 | Transmit PDO2-4 | 16#32EA = 13034 | 16#2064/23 | 16#A2/01/23 = 162/01/35 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-4] (TP24) | [PDO2 image] (P02)
RP31 | Receive PDO3-1 | 16#32C9 = 13001 | 16#2064/2 | 16#A2/01/02 = 162/01/02 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-1] (RP31) | [PDO3 image] (P03)
RP32 | Receive PDO3-2 | 16#32CA = 13002 | 16#2064/3 | 16#A2/01/03 = 162/01/03 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-2] (RP32) | [PDO3 image] (P03)
RP33 | Receive PDO3-3 | 16#32CB = 13003 | 16#2064/4 | 16#A2/01/04 = 162/01/04 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-3] (RP33) | [PDO3 image] (P03)
RP34 | Receive PDO3-4 | 16#32CC = 13004 | 16#2064/5 | 16#A2/01/05 = 162/01/05 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-4] (RP34) | [PDO3 image] (P03)
TP31 | Transmit PDO3-1 | 16#32D3 = 13011 | 16#2064/C | 16#A2/01/0C = 162/01/12 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-1] (TP31) | [PDO3 image] (P03)
TP32 | Transmit PDO3-2 | 16#32D4 = 13012 | 16#2064/D | 16#A2/01/0D = 162/01/13 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-2] (TP32) | [PDO3 image] (P03)
TP33 | Transmit PDO3-3 | 16#32D5 = 13013 | 16#2064/E | 16#A2/01/0E = 162/01/14 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-3] (TP33) | [PDO3 image] (P03)
TP34 | Transmit PDO3-4 | 16#32D6 = 13014 | 16#2064/F | 16#A2/01/0F = 162/01/15 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-4] (TP34) | [PDO3 image] (P03)
NBTP | Number of TX PDO | 16#330E = 13070 | 16#2064/47 | 16#A2/01/47 = 162/01/71 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of TX PDO] (NBTP) | [CANopen map] (CNM)
NBRP | Number of RX PDO | 16#330F = 13071 | 16#2064/48 | 16#A2/01/48 = 162/01/72 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of RX PDO] (NBRP) | [CANopen map] (CNM)
AV1T | Configuration of virtual analog input AIV1 | 16#14A7 = 5287 | 16#2016/58 | 16#7B/01/58 = 123/01/88 | AVOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [+/- 8192] INEG |  | [AIV1 Type] (AV1T) | [Virtual AI1] (AV1)
EPF2 | EPF2 (external error detected by fieldbus) info | 16#1BE8 = 7144 | 16#2029/2D | 16#84/01/91 = 132/01/145 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [external error detected by fieldbus info] (EPF2) | [Profinet diag] (PRN)
CHR | Cabinet overheat response | 16#35DE = 13790 | 16#206B/5B | 16#A5/01/BF = 165/01/191 | CHR | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Cabinet Overheat Resp] (CHR) | [Error/Warning handling] (CSWM) [Cabinet I/O functions] (CABF)
TAFI | DC injection angle | 16#2903 = 10499 | 16#204A/64 | 16#95/01/64 = 149/01/100 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ° | 0 ° | 0 ° ... 360 ° | [DC injection angle] (TAFI) | [Mot. ctrl hidden menu] (MCW)
DBS | Delay to close o/p cont. | 16#332D = 13101 | 16#2065/2 | 16#A2/01/66 = 162/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.15 s | 0.05 s ... 60.00 s | [Delay to motor run] (DBS) | [Output contactor cmd] (OCC)
DAS | Delay to open contactor | 16#332E = 13102 | 16#2065/3 | 16#A2/01/67 = 162/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 5.00 s | [Delay to open cont.] (DAS) | [Output contactor cmd] (OCC)
RCA | Output contactor fdbk | 16#332F = 13103 | 16#2065/4 | 16#A2/01/68 = 162/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Output contact fdbk] (RCA) | [Output contactor cmd] (OCC)
OCC | Output contactor control assignment | 16#3330 = 13104 | 16#2065/5 | 16#A2/01/69 = 162/01/105 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Out. Contactor Assign] (OCC) | [Output contactor cmd] (OCC)
RFT | Power backup input assignment | 16#3607 = 13831 | 16#206C/20 | 16#A6/01/20 = 166/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Power Backup Assign] (RFT) | [Power Backup] (RFT) [Power Backup] (RFT)
RSU | Power backup voltage | 16#3608 = 13832 | 16#206C/21 | 16#A6/01/21 = 166/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 220 V | 220 V ... 415 V | [Pwr Backup Voltage] (RSU) | [Power Backup] (RFT) [Power Backup] (RFT)
RSP | Power backup reference frequency | 16#3609 = 13833 | 16#206C/22 | 16#A6/01/22 = 166/01/34 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 5.0 Hz | 0.0 Hz ... 6553.5 Hz | [Pwr Backup Ref Freq] (RSP) | [Power Backup] (RFT) [Power Backup] (RFT)
TPFV | Torque filter time | 16#0CC5 = 3269 | 16#2002/46 | 16#71/01/46 = 113/01/70 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 10000 ms | [Torque Filter Time] (TPFV) | [Motor monitoring] (MOP)
RTHH | Motor run time | 16#0CCA = 3274 | 16#2002/4B | 16#71/01/4B = 113/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 119304.6 h | [Motor Run Time] (RTHH) | [Variable Speed Pump] (MPP) [Counter Management] (ELT) [Diag. data] (DDT)
PTHH | Power-on time | 16#0CCC = 3276 | 16#2002/4D | 16#71/01/4D = 113/01/77 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 119304.6 h | [Power-on time] (PTHH) | [Counter Management] (ELT)
BRHH | AFE Run time | 16#35BC = 13756 | 16#206B/39 | 16#A5/01/9D = 165/01/157 |  | Status parameters | R | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [AFE Run Time] (BRHH) | [Counter Management] (ELT)
BPHH | AFE power-On time | 16#35BE = 13758 | 16#206B/3B | 16#A5/01/9F = 165/01/159 |  | Status parameters | R | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [AFE Power-On Time] (BPHH) | [Counter Management] (ELT)
RRHH | DBR run time | 16#3742 = 14146 | 16#206F/2F | 16#A7/01/93 = 167/01/147 |  | Status parameters | R | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [DBR Run Time] (RRHH) | [Counter Management] (ELT) [Braking Unit Option] (BUO)
RPHH | BUO power-on time | 16#3744 = 14148 | 16#206F/31 | 16#A7/01/95 = 167/01/149 |  | Status parameters | R | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [BUO Power-on time] (RPHH) | [Counter Management] (ELT) [Braking Unit Option] (BUO)
MSLO | Memo slowdown | 16#30ED = 12525 | 16#205F/1A | 16#9F/01/7E = 159/01/126 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Memo Slowdown] (MSLO) | [Positioning by sensors] (LPO)
BRI | Brake relay feedback | 16#2744 = 10052 | 16#2046/35 | 16#93/01/35 = 147/01/53 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Brake Relay Fdbk] (BRI) | [Brake logic control] (BLC) [Brake logic control] (BLC)
FBRI | Brake relay feedback filter | 16#2745 = 10053 | 16#2046/36 | 16#93/01/36 = 147/01/54 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 100 ms | 0 ms ... 1000 ms | [Brake Rly Fdbk Filter] (FBRI) | [Brake logic control] (BLC) [Brake logic control] (BLC)
SRT | +/- speed reference | 16#2CF3 = 11507 | 16#2055/8 | 16#9A/01/6C = 154/01/108 | SRT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor speed] NO |  | [+/- Speed Reference] (SRT) | [+/- speed] (UPD)
IDAD | Optimal magnetizing current | 16#25CD = 9677 | 16#2042/4E | 16#91/01/4E = 145/01/78 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Opt Magn Current] (IDAD) | [data] (MTD)
QITA | Optimal confidence index | 16#25B0 = 9648 | 16#2042/31 | 16#91/01/31 = 145/01/49 |  | Status parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Opt Confidence Index] (QITA) | [data] (MTD)
TRAD | Optimal rotor time constant | 16#25CE = 9678 | 16#2042/4F | 16#91/01/4F = 145/01/79 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Opt Rotor Time Const] (TRAD) | [data] (MTD)
TLFR | Rotation tune reference frequency | 16#267A = 9850 | 16#2044/33 | 16#92/01/33 = 146/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Rotation Tune Freq] (TLFR) | [Rotation Tune] (TRAM)
PHI0 | Nameplate nominal flux | 16#267B = 9851 | 16#2044/34 | 16#92/01/34 = 146/01/52 |  | Actual values parameters | R | UINT (Unsigned16) | 0.01 Wb |  | 0.00 Wb ... 655.35 Wb | [Nameplate Nominal Flux] (PHI0) | [data] (MTD) [Rotation Tune] (TRAM)
TPD | Tune Periodic Duration without power off | 16#25AE = 9646 | 16#2042/2F | 16#91/01/2F = 145/01/47 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 d | 0 d | 0 d ... 365 d | [None] (TPD) | [Motor tune] (MTU)
RLS | Speed maintain's behavior | 16#1B73 = 7027 | 16#2028/1C | 16#84/01/1C = 132/01/28 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 Hz | 0.0 Hz | -0.1 Hz ... 0.0 Hz | [Spd Maint Behavior] (RLS) | [Spd Maint Behavior] (RLS)
D50D | DI50 delay | 16#0FC8 = 4040 | 16#200A/29 | 16#75/01/29 = 117/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI50 delay] (D50D) | [DI50 configuration] (DI50)
D51D | DI51 delay | 16#0FC9 = 4041 | 16#200A/2A | 16#75/01/2A = 117/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI51 delay] (D51D) | [DI51 configuration] (DI51)
D52D | DI52 delay | 16#0FCA = 4042 | 16#200A/2B | 16#75/01/2B = 117/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI52 delay] (D52D) | [DI52 configuration] (DI52)
D53D | DI53 delay | 16#0FCB = 4043 | 16#200A/2C | 16#75/01/2C = 117/01/44 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI53 delay] (D53D) | [DI53 configuration] (DI53)
D54D | DI54 delay | 16#0FCC = 4044 | 16#200A/2D | 16#75/01/2D = 117/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI54 delay] (D54D) | [DI54 configuration] (DI54)
D55D | DI55 delay | 16#0FCD = 4045 | 16#200A/2E | 16#75/01/2E = 117/01/46 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI55 delay] (D55D) | [DI55 configuration] (DI55)
D56D | DI56 delay | 16#0FCE = 4046 | 16#200A/2F | 16#75/01/2F = 117/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI56 delay] (D56D) | [DI56 configuration] (DI56)
D57D | DI57 delay | 16#0FCF = 4047 | 16#200A/30 | 16#75/01/30 = 117/01/48 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI57 delay] (D57D) | [DI57 configuration] (DI57)
D58D | DI58 delay | 16#0FD0 = 4048 | 16#200A/31 | 16#75/01/31 = 117/01/49 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI58 delay] (D58D) | [DI58 configuration] (DI58)
D59D | DI59 delay | 16#0FD1 = 4049 | 16#200A/32 | 16#75/01/32 = 117/01/50 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI59 delay] (D59D) | [DI59 configuration] (DI59)
R1F | Enable relay 1 fallback | 16#10C2 = 4290 | 16#200C/5B | 16#76/01/5B = 118/01/91 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R1 fallback] (R1F) | [R1 configuration] (R1)
R2F | Enable relay 2 fallback | 16#10C3 = 4291 | 16#200C/5C | 16#76/01/5C = 118/01/92 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R2 fallback] (R2F) | [R2 configuration] (R2)
R3F | Enable relay 3 fallback | 16#44C0 = 17600 | 16#2092/1 | 16#B9/01/01 = 185/01/01 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R3 fallback] (R3F) | [R3 configuration] (R3)
R4F | Enable relay 4 fallback | 16#44C1 = 17601 | 16#2092/2 | 16#B9/01/02 = 185/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R4 fallback] (R4F) | [R4 configuration] (R4)
R5F | Enable relay 5 fallback | 16#44C2 = 17602 | 16#2092/3 | 16#B9/01/03 = 185/01/03 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R5 fallback] (R5F) | [R5 configuration] (R5)
R6F | Enable relay 6 fallback | 16#44C3 = 17603 | 16#2092/4 | 16#B9/01/04 = 185/01/04 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable R6 fallback] (R6F) | [R6 configuration] (R6)
LO1F | Enable DQ1 fallback | 16#10C4 = 4292 | 16#200C/5D | 16#76/01/5D = 118/01/93 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable DQ1 fallback] (LO1F) | [DQ1 configuration] (DO1)
D11F | Enable DQ11 fallback | 16#44C5 = 17605 | 16#2092/6 | 16#B9/01/06 = 185/01/06 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable DQ11 fallback] (D11F) | [DQ11 Configuration] (DO11)
D12F | Enable DQ12 fallback | 16#44C6 = 17606 | 16#2092/7 | 16#B9/01/07 = 185/01/07 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable DQ12 fallback] (D12F) | [DQ12 Configuration] (DO12)
R60S | R60 active at | 16#10CC = 4300 | 16#200D/1 | 16#76/01/65 = 118/01/101 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R60 Active at] (R60S) | [R60 configuration] (R60)
R60D | R60 delay time | 16#10CD = 4301 | 16#200D/2 | 16#76/01/66 = 118/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R60 Delay time] (R60D) | [R60 configuration] (R60)
R60H | R60 holding time | 16#10CE = 4302 | 16#200D/3 | 16#76/01/67 = 118/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R60 Holding time] (R60H) | [R60 configuration] (R60)
R61S | R61 active at | 16#10CF = 4303 | 16#200D/4 | 16#76/01/68 = 118/01/104 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R61 Active at] (R61S) | [R61 configuration] (R61)
R62S | R62 active at | 16#10D2 = 4306 | 16#200D/7 | 16#76/01/6B = 118/01/107 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R62 Active at] (R62S) | [R62 configuration] (R62)
R63S | R63 active at | 16#10D5 = 4309 | 16#200D/A | 16#76/01/6E = 118/01/110 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R63 Active at] (R63S) | [R63 configuration] (R63)
R64S | R64 active at | 16#10D8 = 4312 | 16#200D/D | 16#76/01/71 = 118/01/113 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R64 Active at] (R64S) | [R64 configuration] (R64)
R65S | R65 active at | 16#10DB = 4315 | 16#200D/10 | 16#76/01/74 = 118/01/116 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R65 Active at] (R65S) | [R65 configuration] (R65)
R66S | R66 active at | 16#10DE = 4318 | 16#200D/13 | 16#76/01/77 = 118/01/119 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R66 Active at] (R66S) | [R66 configuration] (R66)
R61D | R61 delay time | 16#10D0 = 4304 | 16#200D/5 | 16#76/01/69 = 118/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R61 Delay time] (R61D) | [R61 configuration] (R61)
R62D | R62 delay time | 16#10D3 = 4307 | 16#200D/8 | 16#76/01/6C = 118/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R62 Delay time] (R62D) | [R62 configuration] (R62)
R63D | R63 delay time | 16#10D6 = 4310 | 16#200D/B | 16#76/01/6F = 118/01/111 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R63 Delay time] (R63D) | [R63 configuration] (R63)
R64D | R64 delay time | 16#10D9 = 4313 | 16#200D/E | 16#76/01/72 = 118/01/114 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R64 Delay time] (R64D) | [R64 configuration] (R64)
R65D | R65 delay time | 16#10DC = 4316 | 16#200D/11 | 16#76/01/75 = 118/01/117 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R65 Delay time] (R65D) | [R65 configuration] (R65)
R66D | R66 delay time | 16#10DF = 4319 | 16#200D/14 | 16#76/01/78 = 118/01/120 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R66 Delay time] (R66D) | [R66 configuration] (R66)
R61H | R61 holding time | 16#10D1 = 4305 | 16#200D/6 | 16#76/01/6A = 118/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R61 Holding time] (R61H) | [R61 configuration] (R61)
R62H | R62 holding time | 16#10D4 = 4308 | 16#200D/9 | 16#76/01/6D = 118/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R62 Holding time] (R62H) | [R62 configuration] (R62)
R63H | R63 holding time | 16#10D7 = 4311 | 16#200D/C | 16#76/01/70 = 118/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R63 Holding time] (R63H) | [R63 configuration] (R63)
R64H | R64 holding time | 16#10DA = 4314 | 16#200D/F | 16#76/01/73 = 118/01/115 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R64 Holding time] (R64H) | [R64 configuration] (R64)
R65H | R65 holding time | 16#10DD = 4317 | 16#200D/12 | 16#76/01/76 = 118/01/118 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R65 Holding time] (R65H) | [R65 configuration] (R65)
R66H | R66 holding time | 16#10E0 = 4320 | 16#200D/15 | 16#76/01/79 = 118/01/121 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R66 Holding time] (R66H) | [R66 configuration] (R66)
IFAA | Monitoring circuit A assignment | 16#413C = 16700 | 16#2089/1 | 16#B4/01/65 = 180/01/101 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit A Assign] (IFAA) | [Monitoring circuit A] (CMCA) [Monitoring circuit A] (CMCA)
IFAB | Monitoring circuit B assignment | 16#413D = 16701 | 16#2089/2 | 16#B4/01/66 = 180/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit B Assign] (IFAB) | [Monitoring circuit B] (CMCB) [Monitoring circuit B] (CMCB)
IFAC | Monitoring circuit C assignment | 16#413E = 16702 | 16#2089/3 | 16#B4/01/67 = 180/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit C Assign] (IFAC) | [Monitoring circuit C] (CMCC) [Monitoring circuit C] (CMCC)
IFAD | Monitoring circuit D assignment | 16#413F = 16703 | 16#2089/4 | 16#B4/01/68 = 180/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit D Assign] (IFAD) | [Monitoring circuit D] (CMCD) [Monitoring circuit D] (CMCD)
CFAA | Cabinet circuit A assignment | 16#4140 = 16704 | 16#2089/5 | 16#B4/01/69 = 180/01/105 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit A Assign] (CFAA) | [Cabinet circuit A] (CCMA)
CFAB | Cabinet circuit B assignment | 16#4141 = 16705 | 16#2089/6 | 16#B4/01/6A = 180/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit B Assign] (CFAB) | [Cabinet circuit B] (CCMB)
CFAC | Cabinet circuit C assignment | 16#4142 = 16706 | 16#2089/7 | 16#B4/01/6B = 180/01/107 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit C Assign] (CFAC) | [Cabinet circuit C] (CCMC)
TFAA | Motor winding A assignment | 16#4143 = 16707 | 16#2089/8 | 16#B4/01/6C = 180/01/108 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorWinding A Assign] (TFAA) | [Motor winding A] (CTIA)
TFAB | Motor winding B assignment | 16#4144 = 16708 | 16#2089/9 | 16#B4/01/6D = 180/01/109 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorWinding B Assign] (TFAB) | [Motor winding B] (CTIB)
TFAC | Motor bearing A assignment | 16#4145 = 16709 | 16#2089/A | 16#B4/01/6E = 180/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorBearing A Assign] (TFAC) | [Motor bearing A] (CTIC)
TFAD | Motor bearing B assignment | 16#4146 = 16710 | 16#2089/B | 16#B4/01/6F = 180/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorBearing B Assign] (TFAD) | [Motor bearing B] (CTID)
IFMA | Monitoring circuit A error monitoring type | 16#4150 = 16720 | 16#2089/15 | 16#B4/01/79 = 180/01/121 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit A Monitor] (IFMA) | [Monitoring circuit A] (CMCA) [Monitoring circuit A] (CMCA)
IFMB | Monitoring circuit B error monitoring type | 16#4151 = 16721 | 16#2089/16 | 16#B4/01/7A = 180/01/122 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit B Monitor] (IFMB) | [Monitoring circuit B] (CMCB) [Monitoring circuit B] (CMCB)
IFMC | Monitoring circuit C error monitoring type | 16#4152 = 16722 | 16#2089/17 | 16#B4/01/7B = 180/01/123 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit C Monitor] (IFMC) | [Monitoring circuit C] (CMCC) [Monitoring circuit C] (CMCC)
IFMD | Monitoring circuit D error monitoring type | 16#4153 = 16723 | 16#2089/18 | 16#B4/01/7C = 180/01/124 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit D Monitor] (IFMD) | [Monitoring circuit D] (CMCD) [Monitoring circuit D] (CMCD)
CFMA | Cabinet circuit A monitoring type | 16#4154 = 16724 | 16#2089/19 | 16#B4/01/7D = 180/01/125 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit A Monitor] (CFMA) | [Cabinet circuit A] (CCMA)
CFMB | Cabinet circuit B monitoring type | 16#4155 = 16725 | 16#2089/1A | 16#B4/01/7E = 180/01/126 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit B Monitor] (CFMB) | [Cabinet circuit B] (CCMB)
CFMC | Cabinet circuit C monitoring type | 16#4156 = 16726 | 16#2089/1B | 16#B4/01/7F = 180/01/127 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit C Monitor] (CFMC) | [Cabinet circuit C] (CCMC)
TFMA | Motor winding A monitoring | 16#4157 = 16727 | 16#2089/1C | 16#B4/01/80 = 180/01/128 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorWinding A Monitor] (TFMA) | [Motor winding A] (CTIA)
TFMB | Motor winding B monitoring | 16#4158 = 16728 | 16#2089/1D | 16#B4/01/81 = 180/01/129 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorWinding B Monitor] (TFMB) | [Motor winding B] (CTIB)
TFMC | Motor bearing A monitoring | 16#4159 = 16729 | 16#2089/1E | 16#B4/01/82 = 180/01/130 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorBearing A Monitor] (TFMC) | [Motor bearing A] (CTIC)
TFMD | Motor bearing B monitoring | 16#415A = 16730 | 16#2089/1F | 16#B4/01/83 = 180/01/131 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorBearing B Monitor] (TFMD) | [Motor bearing B] (CTID)
IFDA | Monitoring circuit A delay after Run | 16#4164 = 16740 | 16#2089/29 | 16#B4/01/8D = 180/01/141 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit A Delay] (IFDA) | [Monitoring circuit A] (CMCA) [Monitoring circuit A] (CMCA)
IFDB | Monitoring circuit B delay after Run | 16#4165 = 16741 | 16#2089/2A | 16#B4/01/8E = 180/01/142 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit B Delay] (IFDB) | [Monitoring circuit B] (CMCB) [Monitoring circuit B] (CMCB)
IFDC | Monitoring circuit C delay after Run | 16#4166 = 16742 | 16#2089/2B | 16#B4/01/8F = 180/01/143 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit C Delay] (IFDC) | [Monitoring circuit C] (CMCC) [Monitoring circuit C] (CMCC)
IFDD | Monitoring circuit D delay after Run | 16#4167 = 16743 | 16#2089/2C | 16#B4/01/90 = 180/01/144 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit D Delay] (IFDD) | [Monitoring circuit D] (CMCD) [Monitoring circuit D] (CMCD)
CFDA | Cabinet circuit A delay after Run | 16#4168 = 16744 | 16#2089/2D | 16#B4/01/91 = 180/01/145 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit A Delay] (CFDA) | [Cabinet circuit A] (CCMA)
CFDB | Cabinet circuit B delay after Run | 16#4169 = 16745 | 16#2089/2E | 16#B4/01/92 = 180/01/146 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit B Delay] (CFDB) | [Cabinet circuit B] (CCMB)
CFDC | Cabinet circuit C delay after Run | 16#416A = 16746 | 16#2089/2F | 16#B4/01/93 = 180/01/147 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit C Delay] (CFDC) | [Cabinet circuit C] (CCMC)
TFDA | Motor winding A delay after Run | 16#416B = 16747 | 16#2089/30 | 16#B4/01/94 = 180/01/148 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorWinding A Delay] (TFDA) | [Motor winding A] (CTIA)
TFDB | Motor winding B delay after Run | 16#416C = 16748 | 16#2089/31 | 16#B4/01/95 = 180/01/149 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorWinding B Delay] (TFDB) | [Motor winding B] (CTIB)
TFDC | Motor bearing A delay after Run | 16#416D = 16749 | 16#2089/32 | 16#B4/01/96 = 180/01/150 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorBearing A Delay] (TFDC) | [Motor bearing A] (CTIC)
TFDD | Motor bearing B delay after Run | 16#416E = 16750 | 16#2089/33 | 16#B4/01/97 = 180/01/151 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorBearing B Delay] (TFDD) | [Motor bearing B] (CTID)
IFRA | Response to monitoring circuit A error | 16#4178 = 16760 | 16#2089/3D | 16#B4/01/A1 = 180/01/161 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit A ErrorResp] (IFRA) | [Monitoring circuit A] (CMCA) [Monitoring circuit A] (CMCA)
IFRB | Response to monitoring circuit B error | 16#4179 = 16761 | 16#2089/3E | 16#B4/01/A2 = 180/01/162 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit B ErrorResp] (IFRB) | [Monitoring circuit B] (CMCB) [Monitoring circuit B] (CMCB)
IFRC | Response to monitoring circuit C error | 16#417A = 16762 | 16#2089/3F | 16#B4/01/A3 = 180/01/163 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit C ErrorResp] (IFRC) | [Monitoring circuit C] (CMCC) [Monitoring circuit C] (CMCC)
IFRD | Response to monitoring circuit D error | 16#417B = 16763 | 16#2089/40 | 16#B4/01/A4 = 180/01/164 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit D ErrorResp] (IFRD) | [Monitoring circuit D] (CMCD) [Monitoring circuit D] (CMCD)
CFRA | Response to cabinet circuit A error | 16#417C = 16764 | 16#2089/41 | 16#B4/01/A5 = 180/01/165 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit A ErrorResp] (CFRA) | [Cabinet circuit A] (CCMA)
CFRB | Response to cabinet circuit B error | 16#417D = 16765 | 16#2089/42 | 16#B4/01/A6 = 180/01/166 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit B ErrorResp] (CFRB) | [Cabinet circuit B] (CCMB)
CFRC | Response to cabinet circuit C error | 16#417E = 16766 | 16#2089/43 | 16#B4/01/A7 = 180/01/167 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit C ErrorResp] (CFRC) | [Cabinet circuit C] (CCMC)
TFRA | Response to motor winding A error | 16#417F = 16767 | 16#2089/44 | 16#B4/01/A8 = 180/01/168 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorWinding A ErrorResp] (TFRA) | [Motor winding A] (CTIA)
TFRB | Response to motor winding B error | 16#4180 = 16768 | 16#2089/45 | 16#B4/01/A9 = 180/01/169 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorWinding B ErrorResp] (TFRB) | [Motor winding B] (CTIB)
TFRC | Response to motor bearing A error | 16#4181 = 16769 | 16#2089/46 | 16#B4/01/AA = 180/01/170 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorBearing A ErrorResp] (TFRC) | [Motor bearing A] (CTIC)
TFRD | Response to motor bearing B error | 16#4182 = 16770 | 16#2089/47 | 16#B4/01/AB = 180/01/171 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorBearing B ErrorResp] (TFRD) | [Motor bearing B] (CTID)
CBSR | Response to circuit breaker error | 16#352A = 13610 | 16#206A/B | 16#A5/01/0B = 165/01/11 | CBSR | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error] FLT |  | [CB Error Resp] (CBSR) | [Circuit breaker] (CCBK)
CBEP | Circuit breaker start pulse activated | 16#352C = 13612 | 16#206A/D | 16#A5/01/0D = 165/01/13 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [CB start pulse activated] (CBEP) | [Circuit breaker] (CCBK)
CBDP | Circuit breaker stop pulse activated | 16#352D = 13613 | 16#206A/E | 16#A5/01/0E = 165/01/14 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [CB stop pulse activated] (CBDP) | [Circuit breaker] (CCBK)
CBT1 | Circuit breaker start pulse time | 16#352E = 13614 | 16#206A/F | 16#A5/01/0F = 165/01/15 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB start pulse time] (CBT1) | [Circuit breaker] (CCBK)
CBT2 | Circuit breaker stop pulse time | 16#352F = 13615 | 16#206A/10 | 16#A5/01/10 = 165/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB stop pulse time] (CBT2) | [Circuit breaker] (CCBK)
CBT3 | Circuit breaker switch-on delay | 16#3530 = 13616 | 16#206A/11 | 16#A5/01/11 = 165/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB Switch-on delay] (CBT3) | [Circuit breaker] (CCBK)
CBT4 | Circuit breaker switch-off delay | 16#3531 = 13617 | 16#206A/12 | 16#A5/01/12 = 165/01/18 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB Switch-off delay] (CBT4) | [Circuit breaker] (CCBK)
CBT5 | Circuit breaker Disable stop delay | 16#3532 = 13618 | 16#206A/13 | 16#A5/01/13 = 165/01/19 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 360.0 s | [CB Disable stop delay] (CBT5) | [Circuit breaker] (CCBK)
AI1L | Analog input 1 range | 16#1182 = 4482 | 16#200E/53 | 16#77/01/53 = 119/01/83 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI1 range] (AI1L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1 configuration] (AI1)
AI3L | Analog input 3 range | 16#1184 = 4484 | 16#200E/55 | 16#77/01/55 = 119/01/85 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI3 range] (AI3L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3 configuration] (AI3)
AI4L | Analog input 4 range | 16#1185 = 4485 | 16#200E/56 | 16#77/01/56 = 119/01/86 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI4 range] (AI4L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4 configuration] (AI4)
AI5L | Analog input 5 range | 16#1186 = 4486 | 16#200E/57 | 16#77/01/57 = 119/01/87 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI5 range] (AI5L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5 configuration] (AI5)
PGA | Reference type | 16#33F5 = 13301 | 16#2067/2 | 16#A3/01/66 = 163/01/102 | PGA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Encoder] ENC |  | [Reference Type] (PGA) | [Encoder Config] (PG)
PEIL | Frequency min value | 16#42AE = 17070 | 16#208C/47 | 16#B6/01/47 = 182/01/71 |  | Configuration and settings | R/WS | INT (Signed32) | 0.01 kHz | 0.00 kHz | -300.00 kHz ... 300.00 kHz | [Freq Min Value] (PEIL) | [Encoder Config] (PG)
PEFR | Frequency max value | 16#42B0 = 17072 | 16#208C/49 | 16#B6/01/49 = 182/01/73 |  | Configuration and settings | R/WS | INT (Signed32) | 0.01 kHz | 300.00 kHz | -300.00 kHz ... 300.00 kHz | [Freq Max Value] (PEFR) | [Encoder Config] (PG)
EFI | Frequency signal filter | 16#3400 = 13312 | 16#2067/D | 16#A3/01/71 = 163/01/113 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [Freq Signal Filter] (EFI) | [Encoder Config] (PG)
ECFR | Encoder pulse frequency | 16#42B2 = 17074 | 16#208C/4B | 16#B6/01/4B = 182/01/75 |  | Status parameters | R | INT (Signed32) | 0.01 kHz |  | -21474836.47 kHz ... 21474836.47 kHz | [Encoder Pulse Freq] (ECFR) | [Freq. signal image] (FSI)
EIFC | Encoder frequency | 16#42B4 = 17076 | 16#208C/4D | 16#B6/01/4D = 182/01/77 |  | Status parameters | R | INT (Signed32) | 0.01 Hz |  | -21474836.47 Hz ... 21474836.47 Hz | [Encoder Frequency] (EIFC) | [Freq. signal image] (FSI)
AOF1 | Enable AQ1 fallback | 16#10C5 = 4293 | 16#200C/5E | 16#76/01/5E = 118/01/94 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable AQ1 fallback] (AOF1) | [AQ1 configuration] (AO1)
AOF2 | Enable AQ2 fallback | 16#1253 = 4691 | 16#2010/5C | 16#78/01/5C = 120/01/92 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable AQ2 fallback] (AOF2) | [AQ2 configuration] (AO2)
HSOM | HSH speed mode | 16#302A = 12330 | 16#205D/1F | 16#9E/01/83 = 158/01/131 | HSOM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [HSH Speed Mode] (HSOM) | [High speed hoisting] (HSH)
HTQ1 | HSH torque 1 | 16#302B = 12331 | 16#205D/20 | 16#9E/01/84 = 158/01/132 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 7 % | 0 % ... 99 % | [HSH Torque 1] (HTQ1) | [High speed hoisting] (HSH)
HTQ2 | HSH torque 2 | 16#302C = 12332 | 16#205D/21 | 16#9E/01/85 = 158/01/133 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 45 % | 0 % ... 100 % | [HSH Torque 2] (HTQ2) | [High speed hoisting] (HSH)
SLCA | Slewing control mode | 16#48A8 = 18600 | 16#209C/1 | 16#BE/01/01 = 190/01/01 | SLCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Slewing Control Mode] (SLCA) | [Slewing control] (SLC)
SLLS | Slewing low speed stop | 16#48A9 = 18601 | 16#209C/2 | 16#BE/01/02 = 190/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.2 Hz | 0.0 Hz ... 599.0 Hz | [SL Low Speed Stop] (SLLS) | [Slewing control] (SLC)
SLST | Slewing stop time | 16#48AA = 18602 | 16#209C/3 | 16#BE/01/03 = 190/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 1000 s | [SL Stop Time] (SLST) | [Slewing control] (SLC)
SLFD | Slewing fast deceleration | 16#48AB = 18603 | 16#209C/4 | 16#BE/01/04 = 190/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 5 % ... 100 % | [SL Fast Deceleration] (SLFD) | [Slewing control] (SLC)
SLGF | Slewing speed filter gain | 16#48AC = 18604 | 16#209C/5 | 16#BE/01/05 = 190/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 150 Hz | 0 Hz ... 150 Hz | [SL Spd Filt Gain] (SLGF) | [Slewing control] (SLC)
SLDF | Slewing speed filter damping | 16#48AD = 18605 | 16#209C/6 | 16#BE/01/06 = 190/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 30 % | 0 % ... 100 % | [SL Spd Filt Damp] (SLDF) | [Slewing control] (SLC)
SLBF | Slewing speed filter bandwidth | 16#48AE = 18606 | 16#209C/7 | 16#BE/01/07 = 190/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 4.0 Hz | 0.0 Hz ... 500.0 Hz | [SL Spd Filt Bandwidth] (SLBF) | [Slewing control] (SLC)
SLTM | Slewing torque boost: Minimum torque at start | 16#48AF = 18607 | 16#209C/8 | 16#BE/01/08 = 190/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 2.0 % | 0.0 % ... 100.0 % | [None] (SLTM) | [Slewing control] (SLC)
SLTI | Slewing torque boost: minimum duration | 16#48B0 = 18608 | 16#209C/9 | 16#BE/01/09 = 190/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | Refer to programming manual | 0.00 s ... 10.00 s | [None] (SLTI) | [Slewing control] (SLC)
SLTR | Slewing torque boost: Torque ramp at start | 16#48B1 = 18609 | 16#209C/A | 16#BE/01/0A = 190/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 30.00 s | 0.00 s ... 300.00 s | [None] (SLTR) | [Slewing control] (SLC)
SLTQ | Slewing torque boost: Torque set point | 16#48B2 = 18610 | 16#209C/B | 16#BE/01/0B = 190/01/11 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [None] (SLTQ) | [Slewing control] (SLC)
SLDT | Slewing torque boost: deactivation speed threshold | 16#48BD = 18621 | 16#209C/16 | 16#BE/01/16 = 190/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 599.0 Hz | [None] (SLDT) | [Slewing control] (SLC)
SLLD | Slewing fast stop: low speed threshold | 16#48B3 = 18611 | 16#209C/C | 16#BE/01/0C = 190/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 2.0 Hz | 0.0 Hz ... 599.0 Hz | [None] (SLLD) | [Slewing control] (SLC)
SLSR | Slewing relay management: Low condition speed threshold | 16#48B4 = 18612 | 16#209C/D | 16#BE/01/0D = 190/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.0 Hz ... 5.0 Hz | [None] (SLSR) | [Slewing control] (SLC)
SLHF | Slewing ramp management: High speed threshold | 16#48B5 = 18613 | 16#209C/E | 16#BE/01/0E = 190/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 599.0 Hz | [None] (SLHF) | [Slewing control] (SLC)
SLSC | Slewing Torque-Speed switch High threshold | 16#48B6 = 18614 | 16#209C/F | 16#BE/01/0F = 190/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [None] (SLSC) | [Slewing control] (SLC)
SLTA | Slewing Torque-Speed switch low threshold | 16#48B7 = 18615 | 16#209C/10 | 16#BE/01/10 = 190/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [None] (SLTA) | [Slewing control] (SLC)
SLRP | Slewing speed control gain boost | 16#48B8 = 18616 | 16#209C/11 | 16#BE/01/11 = 190/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 4.0 % | 0.0 % ... 20.0 % | [None] (SLRP) | [Slewing control] (SLC)
SLFR | Slewing positioning ramp switch threshold | 16#48B9 = 18617 | 16#209C/12 | 16#BE/01/12 = 190/01/18 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.0 Hz ... 599.0 Hz | [None] (SLFR) | [Slewing control] (SLC)
SLDE | Slewing positioning deceleration time (between FRS and 0) | 16#48BA = 18618 | 16#209C/13 | 16#BE/01/13 = 190/01/19 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 220 | 1 ... 9999 | [None] (SLDE) | [Slewing control] (SLC)
SLD2 | Slewing positioning deceleration time 2 (between FRS and 0) | 16#48BB = 18619 | 16#209C/14 | 16#BE/01/14 = 190/01/20 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 220 | 1 ... 9999 | [None] (SLD2) | [Slewing control] (SLC)
SLFT | Slewing fast stop torque threshold deactivation | 16#48BC = 18620 | 16#209C/15 | 16#BE/01/15 = 190/01/21 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 300 % | 0 % ... 300 % | [None] (SLFT) | [Slewing control] (SLC)
ASV | Offset value between motor and encoder | 16#3662 = 13922 | 16#206D/17 | 16#A6/01/7B = 166/01/123 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | -1 | -1 ... 8192 | [Angle offset value] (ASV) | [Angle test setting] (ASA)
RTC | Alignment rotational torque current | 16#3669 = 13929 | 16#206D/1E | 16#A6/01/82 = 166/01/130 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 0 % | 0 % ... 300 % | [Rotational Torque Current] (RTC) | [Motor tune] (MTU)
RCRP | RCI round number | 16#366C = 13932 | 16#206D/21 | 16#A6/01/85 = 166/01/133 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | RCSP_AUTO | -1 ... 32767 | [RCI Round Nb] (RCRP) | [Motor tune] (MTU)
PES | Weight sensor assignment | 16#2756 = 10070 | 16#2046/47 | 16#93/01/47 = 147/01/71 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Weight Sensor Assign] (PES) | [External weight meas.] (ELM)
IBRA | IBR when weight loss | 16#275B = 10075 | 16#2046/4C | 16#93/01/4C = 147/01/76 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Ibr 4-20 mA loss] (IBRA) | [External weight meas.] (ELM)
LP1 | Ext weight point 1 X | 16#2757 = 10071 | 16#2046/48 | 16#93/01/48 = 147/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 0.00 % | 0.00 % ... 99.99 % | [Point 1 X] (LP1) | [External weight meas.] (ELM)
CP1 | Ext weight point 1Y | 16#2758 = 10072 | 16#2046/49 | 16#93/01/49 = 147/01/73 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32767 ... 32767 | [Point 1Y] (CP1) | [External weight meas.] (ELM)
LP2 | Ext weight point 2 X | 16#2759 = 10073 | 16#2046/4A | 16#93/01/4A = 147/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 50.00 % | 0.01 % ... 100.00 % | [Point 2 X] (LP2) | [External weight meas.] (ELM)
CP2 | Ext weight point 2Y | 16#275A = 10074 | 16#2046/4B | 16#93/01/4B = 147/01/75 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32767 ... 32767 | [Point 2Y] (CP2) | [External weight meas.] (ELM)
OVMA | Overmodulation activation | 16#3634 = 13876 | 16#206C/4D | 16#A6/01/4D = 166/01/77 | OVMA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Default] DEFAULT |  | [Overmodul. Activation] (OVMA) | [Motor control] (DRC)
VLIM | Output voltage limitation | 16#3637 = 13879 | 16#206C/50 | 16#A6/01/50 = 166/01/80 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | VLIM_DEFAULT | 0 V ... 9999 V | [Output Voltage Limit] (VLIM) | [Motor control] (DRC)
DCRA | DC bus ripple amplitude | 16#3639 = 13881 | 16#206C/52 | 16#A6/01/52 = 166/01/82 |  | Status parameters | R | INT (Signed16) | 1 V |  | -32767 V ... 32767 V | [DC Bus Rip Amp Val] (DCRA) | [Input Filter] (DCR)
DCRF | DC bus ripple estimated frequency | 16#363A = 13882 | 16#206C/53 | 16#A6/01/53 = 166/01/83 |  | Status parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [DC Bus Rip Est Freq] (DCRF) | [Input Filter] (DCR)
DCRD | DC bus ripple time counter | 16#363B = 13883 | 16#206C/54 | 16#A6/01/54 = 166/01/84 |  | Status parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [DC Bus Rip Counter] (DCRD) | [Input Filter] (DCR)
DCRC | DC bus ripple configuration | 16#363C = 13884 | 16#206C/55 | 16#A6/01/55 = 166/01/85 | DCRC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [DC Bus Ripple Config] (DCRC) | [Input Filter] (DCR)
CRB | Current loop configured gain | 16#363D = 13885 | 16#206C/56 | 16#A6/01/56 = 166/01/86 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 65535 Hz | [Cur Loop Config Gain] (CRB) | [Motor control] (DRC) [Input Filter] (DCR)
CRBA | Current loop default gain | 16#363E = 13886 | 16#206C/57 | 16#A6/01/57 = 166/01/87 |  | Status parameters | R | INT (Signed16) | 1 Hz |  | 8 Hz ... 100 Hz | [Cur Loop Default Gain] (CRBA) | [Motor control] (DRC) [Input Filter] (DCR)
CRDR | Current loop damping coefficient | 16#363F = 13887 | 16#206C/58 | 16#A6/01/58 = 166/01/88 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | Refer to programming manual | 1 % ... 800 % | [Cur Loop Damp Coef] (CRDR) | [Motor control] (DRC) [Input Filter] (DCR)
IFI | Use of an input filer | 16#3640 = 13888 | 16#206C/59 | 16#A6/01/59 = 166/01/89 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Input Filter] (IFI) | [Input Filter] (DCR)
IDLM | Delay before Energy Saving | 16#3625 = 13861 | 16#206C/3E | 16#A6/01/3E = 166/01/62 |  | Configuration and settings | R/WS | INT (Signed16) | 1 s | Refer to programming manual | -1 s ... 32400 s | [Energy Saving Delay] (IDLM) | [Stop and Go] (STG)
IDLT | Idle mode timeout | 16#3626 = 13862 | 16#206C/3F | 16#A6/01/3F = 166/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | Refer to programming manual | 1 s ... 999 s | [Egy Saving Timeout] (IDLT) | [Stop and Go] (STG)
TDCA | Time delay control assignment | 16#7274 = 29300 | 16#2107/1 | 16#F3/01/65 = 243/01/101 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [TDC Assignment] (TDCA) | [Time delay control] (TDC)
TCSH | Time delay control activation frequency | 16#7275 = 29301 | 16#2107/2 | 16#F3/01/66 = 243/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [TDC Activate Freq] (TCSH) | [Time delay control] (TDC)
TCSL | Time delay control deactivation frequency | 16#7276 = 29302 | 16#2107/3 | 16#F3/01/67 = 243/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [TDC Deactivate Freq] (TCSL) | [Time delay control] (TDC)
TDCL | Time delay control wire rope length | 16#7277 = 29303 | 16#2107/4 | 16#F3/01/68 = 243/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 m | 0.0 m | 0.0 m ... 20.0 m | [TDC Rope Length] (TDCL) | [Time delay control] (TDC)
ACCT | Time delay control acceleration ramp time | 16#7279 = 29305 | 16#2107/6 | 16#F3/01/6A = 243/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [TDC Acceleration] (ACCT) | [Time delay control] (TDC)
DECT | Time delay control deceleration ramp time | 16#727A = 29306 | 16#2107/7 | 16#F3/01/6B = 243/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [TDC Deceleration] (DECT) | [Time delay control] (TDC)
TDCP | Time delay control pendulum time period | 16#727D = 29309 | 16#2107/A | 16#F3/01/6E = 243/01/110 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 25000 ms | [TDC Pendul. Period] (TDCP) | [Time delay control] (SLCT) [Time delay control] (TDC)
TDCR | Time delay control speed damping coefficient | 16#727E = 29310 | 16#2107/B | 16#F3/01/6F = 243/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 100 % | [TDC Spd Damp Coef] (TDCR) | [Time delay control] (SLCT) [Time delay control] (TDC)
RMPM | Time delay Control : Minimum ACC and DEC possible value | 16#728A = 29322 | 16#2107/17 | 16#F3/01/7B = 243/01/123 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [None] (RMPM) | [Slewing control] (SLC) [Time delay control] (TDC)
PTGT | Reference position | 16#433A = 17210 | 16#208E/B | 16#B7/01/0B = 183/01/11 |  | Actual values parameters | R/W | INT (Signed32) | 1 |  | -2147483647 ... 2147483647
PTG3 | Fieldbus module reference position | 16#4340 = 17216 | 16#208E/11 | 16#B7/01/11 = 183/01/17 |  | Actual values parameters | R/W | INT (Signed32) | 1 |  | -2147483647 ... 2147483647
PDMD | Position trajectory reference | 16#434C = 17228 | 16#208E/1D | 16#B7/01/1D = 183/01/29 |  | Actual values parameters | R/W | INT (Signed32) | 1 |  | -2147483647 ... 2147483647
PACT | Actual position | 16#4350 = 17232 | 16#208E/21 | 16#B7/01/21 = 183/01/33 |  | Actual values parameters | R/W | INT (Signed32) | 1 |  | -2147483647 ... 2147483647
DEP0 | dPAC Exchange 0 | 16#4592 = 17810 | 16#2094/B | 16#BA/01/0B = 186/01/11 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP1 | dPAC Exchange 1 | 16#4593 = 17811 | 16#2094/C | 16#BA/01/0C = 186/01/12 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP2 | dPAC Exchange 2 | 16#4594 = 17812 | 16#2094/D | 16#BA/01/0D = 186/01/13 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP3 | dPAC Exchange 3 | 16#4595 = 17813 | 16#2094/E | 16#BA/01/0E = 186/01/14 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP4 | dPAC Exchange 4 | 16#4596 = 17814 | 16#2094/F | 16#BA/01/0F = 186/01/15 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP5 | dPAC Exchange 5 | 16#4597 = 17815 | 16#2094/10 | 16#BA/01/10 = 186/01/16 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP6 | dPAC Exchange 6 | 16#4598 = 17816 | 16#2094/11 | 16#BA/01/11 = 186/01/17 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP7 | dPAC Exchange 7 | 16#4599 = 17817 | 16#2094/12 | 16#BA/01/12 = 186/01/18 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP8 | dPAC Exchange 8 | 16#459A = 17818 | 16#2094/13 | 16#BA/01/13 = 186/01/19 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEP9 | dPAC Exchange 9 | 16#459B = 17819 | 16#2094/14 | 16#BA/01/14 = 186/01/20 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPA | dPAC Exchange 10 | 16#459C = 17820 | 16#2094/15 | 16#BA/01/15 = 186/01/21 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPB | dPAC Exchange 11 | 16#459D = 17821 | 16#2094/16 | 16#BA/01/16 = 186/01/22 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPC | dPAC Exchange 12 | 16#459E = 17822 | 16#2094/17 | 16#BA/01/17 = 186/01/23 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPD | dPAC Exchange 13 | 16#459F = 17823 | 16#2094/18 | 16#BA/01/18 = 186/01/24 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPE | dPAC Exchange 14 | 16#45A0 = 17824 | 16#2094/19 | 16#BA/01/19 = 186/01/25 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPF | dPAC Exchange 15 | 16#45A1 = 17825 | 16#2094/1A | 16#BA/01/1A = 186/01/26 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPG | dPAC Exchange 16 | 16#45A2 = 17826 | 16#2094/1B | 16#BA/01/1B = 186/01/27 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPH | dPAC Exchange 17 | 16#45A3 = 17827 | 16#2094/1C | 16#BA/01/1C = 186/01/28 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPI | dPAC Exchange 18 | 16#45A4 = 17828 | 16#2094/1D | 16#BA/01/1D = 186/01/29 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DEPJ | dPAC Exchange 19 | 16#45A5 = 17829 | 16#2094/1E | 16#BA/01/1E = 186/01/30 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP0 | dPAC Persistent 0 | 16#45A6 = 17830 | 16#2094/1F | 16#BA/01/1F = 186/01/31 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP1 | DPAC mailbox saved parameter 1 | 16#45A7 = 17831 | 16#2094/20 | 16#BA/01/20 = 186/01/32 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP2 | DPAC mailbox saved parameter 2 | 16#45A8 = 17832 | 16#2094/21 | 16#BA/01/21 = 186/01/33 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP3 | DPAC mailbox saved parameter 3 | 16#45A9 = 17833 | 16#2094/22 | 16#BA/01/22 = 186/01/34 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP4 | DPAC mailbox saved parameter 4 | 16#45AA = 17834 | 16#2094/23 | 16#BA/01/23 = 186/01/35 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP5 | DPAC mailbox saved parameter 5 | 16#45AB = 17835 | 16#2094/24 | 16#BA/01/24 = 186/01/36 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP6 | DPAC mailbox saved parameter 6 | 16#45AC = 17836 | 16#2094/25 | 16#BA/01/25 = 186/01/37 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP7 | DPAC mailbox saved parameter 7 | 16#45AD = 17837 | 16#2094/26 | 16#BA/01/26 = 186/01/38 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP8 | DPAC mailbox saved parameter 8 | 16#45AE = 17838 | 16#2094/27 | 16#BA/01/27 = 186/01/39 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSP9 | DPAC mailbox saved parameter 9 | 16#45AF = 17839 | 16#2094/28 | 16#BA/01/28 = 186/01/40 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPA | dPAC Persistent 10 | 16#45B0 = 17840 | 16#2094/29 | 16#BA/01/29 = 186/01/41 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPB | DPAC mailbox saved parameter 11 | 16#45B1 = 17841 | 16#2094/2A | 16#BA/01/2A = 186/01/42 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPC | DPAC mailbox saved parameter 12 | 16#45B2 = 17842 | 16#2094/2B | 16#BA/01/2B = 186/01/43 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPD | DPAC mailbox saved parameter 13 | 16#45B3 = 17843 | 16#2094/2C | 16#BA/01/2C = 186/01/44 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPE | DPAC mailbox saved parameter 14 | 16#45B4 = 17844 | 16#2094/2D | 16#BA/01/2D = 186/01/45 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPF | DPAC mailbox saved parameter 15 | 16#45B5 = 17845 | 16#2094/2E | 16#BA/01/2E = 186/01/46 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPG | DPAC mailbox saved parameter 16 | 16#45B6 = 17846 | 16#2094/2F | 16#BA/01/2F = 186/01/47 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPH | DPAC mailbox saved parameter 17 | 16#45B7 = 17847 | 16#2094/30 | 16#BA/01/30 = 186/01/48 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPI | DPAC mailbox saved parameter 18 | 16#45B8 = 17848 | 16#2094/31 | 16#BA/01/31 = 186/01/49 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
DSPJ | DPAC mailbox saved parameter 19 | 16#45B9 = 17849 | 16#2094/32 | 16#BA/01/32 = 186/01/50 |  | Actual values parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
FTOR | M/S local torque reference | 16#41D4 = 16852 | 16#208A/35 | 16#B5/01/35 = 181/01/53 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [M/S Local Torq Ref] (FTOR) | [M/S Local Display] (MSO) [M/S System Display] (MSR)
FXT | M/S device torque reference | 16#41D3 = 16851 | 16#208A/34 | 16#B5/01/34 = 181/01/52 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [M/S Device Torq Ref] (FXT) | [M/S System Display] (MSR)
FMTR | M/S master torque reference | 16#41D2 = 16850 | 16#208A/33 | 16#B5/01/33 = 181/01/51 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [M/S Master Torq Ref] (FMTR) | [M/S Local Display] (MSO)
PKVS | Package version | 16#FFD3 = 65491 |  |  |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Package Version] (PKVS) | [Package version] (PFV)
PKTP | Package type | 16#FFD4 = 65492 |  |  | PKTP | Status parameters | R | WORD (Enumeration) | - |  |  | [Package Type] (PKTP) | [Package version] (PFV)
FWCL | Abort firmware update | 16#FFD5 = 65493 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Abort Firmware Update] (FWCL) | [Firmware update] (FWUP)
FWER | Firmware Update error code | 16#FFD6 = 65494 |  |  | FWER | Status parameters | R | WORD (Enumeration) | - |  |  | [Firmware Update Error] (FWER) | [Firmware update diag] (FWUD)
FWAP | Update firmware | 16#FFD7 = 65495 |  |  | N_Y | Configuration and settings | R | WORD (Enumeration) | - | [No] NO |  | [Update Firmware] (FWAP) | [Firmware update] (FWUP)
FWST | Firmware Update Status | 16#FFDB = 65499 |  |  | FWST | Status parameters | R | WORD (Enumeration) | - |  |  | [Firmware Update Status] (FWST) | [Firmware update diag] (FWUD)
MDT | HMI displayed value type | 16#FA20 = 64032 |  |  | MDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Digital values] DEC |  | [Display value type] (MDT) | [Display screen type] (MSC)
EMDT | Energy Dashboard | 16#FA31 = 64049 |  |  | EMDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Instantaneous kW trend] CVE
LAC | Access level | 16#0BBE = 3006 | 16#2000/7 | 16#70/01/07 = 112/01/07 | LAC | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard access] STD |  | [Access Level] (LAC) | [My preferences] (MYP)
CMDC | Command channel | 16#FA28 = 64040 |  |  | CNL | Status parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (CMDC) | [Communication map] (CMM)
RFCC | Channel for reference frequency | 16#FA29 = 64041 |  |  | CNL | Status parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (RFCC) | [Communication map] (CMM)
PVIS | Parameters | 16#FA23 = 64035 |  |  | PVIS | Configuration and settings | R/W | WORD (Enumeration) | - | [Active parameters] ACT |  | [Parameters] (PVIS) | [Visibility] (VIS)
FCSI | Source configuration | 16#FA51 = 64081 |  |  | FCSI | Configuration and settings | R/WS | WORD (Enumeration) | - | [Macro configuration] INI |  | [Config. Source] (FCSI) | [Factory settings] (FCS)
SCSI | Save configuration | 16#FA50 = 64080 |  |  | SCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Save Configuration] (SCSI) | [Factory settings] (FCS)
TOUT | Ethernet timeout | 16#FAD3 = 64211 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 2.0 s | 0.0 s ... 60.0 s | [Ethernet Timeout] (TOUT) | [Eth Module Config] (ETO)
FTTS | nothing | 16#FA10 = 64016 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 50 | 0 ... 100000
KLCK | Display terminal locked | 16#FA12 = 64018 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 5 min | 0 min ... 10 min | [Display Terminal locked] (KLCK) | [LCD settings] (CNL)
BCKL | Red Backlight | 16#FA13 = 64019 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [Red Backlight] (BCKL) | [LCD settings] (CNL)
IPM | IP mode | 16#FAFA = 64250 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [IP mode] (IPM) | [Profinet] (PNC)
IM00 | IP mode Ethernet Embd | 16#FB90 = 64400 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | [DHCP] DHCP |  | [IP Mode Ether. Embd] (IM00) | [Embd Eth Config] (ETE)
IM10 | Ethernet option IP mode | 16#FBC2 = 64450 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | [DHCP] DHCP |  | [ETH Option IP Mode] (IM10) | [Eth Module Config] (ETO)
ARDE | Ethernet rate data | 16#FB9D = 64413 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Ethernet Rate Data] (ARDE) | [Ethernet Emb Diag] (MPE)
ERXE | Ethernet embedded Rx frames | 16#FBA0 = 64416 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb Rx frames] (ERXE) | [Ethernet Emb Diag] (MPE)
ETXE | Ethernet embedded Tx frames | 16#FBA2 = 64418 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb Tx frames] (ETXE) | [Ethernet Emb Diag] (MPE)
EERE | Ethernet embedded error frames | 16#FBA4 = 64420 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb error frames] (EERE) | [Ethernet Emb Diag] (MPE)
ERXO | Ethernet option Rx frames | 16#FBD2 = 64466 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Rx frames] (ERXO) | [Ethernet Module Diag] (MTE)
ETXO | Ethernet option Tx frames | 16#FBD4 = 64468 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Tx frames] (ETXO) | [Ethernet Module Diag] (MTE)
EERO | Ethernet option error frames | 16#FBD6 = 64470 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt error frames] (EERO) | [Ethernet Module Diag] (MTE)
DSTA | Runtime status | 16#458D = 17805 | 16#2094/6 | 16#BA/01/06 = 186/01/06 | DSTA | Status parameters | R | WORD (Enumeration) | - |  |  | [Runtime Status] (DSTA) | [Controller Application] (APPD)
SSTA | Safety module status | 16#3BCA = 15306 | 16#207B/7 | 16#AD/01/6B = 173/01/107 | SSTA | Safety module parameters | R | WORD (Enumeration) | - |  |  | [Safety Module Status] (SSTA) | [Safety Module] (OSM)
SCNA | Safety configuration status | 16#3BCB = 15307 | 16#207B/8 | 16#AD/01/6C = 173/01/108 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Config Status] (SCNA) | [Safety Module] (OSM)
SFCA | Active safety function | 16#3BCC = 15308 | 16#207B/9 | 16#AD/01/6D = 173/01/109 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Active Safety Fct] (SFCA) | [Safety Module] (OSM)
SIWA | Safety input word A | 16#3BD4 = 15316 | 16#207B/11 | 16#AD/01/75 = 173/01/117 |  | Safety module parameters | R | WORD (BitString16) | -
SQWA | Safety output word A | 16#3BD5 = 15317 | 16#207B/12 | 16#AD/01/76 = 173/01/118 |  | Safety module parameters | R | WORD (BitString16) | -
FSCA | Test command activation | 16#3BDE = 15326 | 16#207B/1B | 16#AD/01/7F = 173/01/127 | PSLIN | Safety module parameters | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Test Cmd Activation] (FSCA) | [Safety Config Test] (SCT)
FSRC | Test ramp command | 16#3BDC = 15324 | 16#207B/19 | 16#AD/01/7D = 173/01/125 |  | Safety module parameters | R/W | UINT (Unsigned32) | 0.1 Hz/Sec | 0.0 Hz/Sec | 0.0 Hz/Sec ... 20000.0 Hz/Sec | [Test Ramp Cmd] (FSRC) | [Safety Config Test] (SCT)
SIWB | Safety input word B | 16#3BD6 = 15318 | 16#207B/13 | 16#AD/01/77 = 173/01/119 |  | Safety module parameters | R | WORD (BitString16) | -
SQWB | Safety output word B | 16#3BD7 = 15319 | 16#207B/14 | 16#AD/01/78 = 173/01/120 |  | Safety module parameters | R | WORD (BitString16) | -
SMLE | Safety module error | 16#3BDF = 15327 | 16#207B/1C | 16#AD/01/80 = 173/01/128 | SMLE | Safety module parameters | R | WORD (Enumeration) | - |  |  | [Safety Module Error] (SMLE) | [Safety Module Errors] (SME)
SME0 | Safety module error 0 | 16#3BE0 = 15328 | 16#207B/1D | 16#AD/01/81 = 173/01/129 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 0] (SME0) | [Safety Module Errors] (SME)
SME1 | Safety module error 1 | 16#3BE1 = 15329 | 16#207B/1E | 16#AD/01/82 = 173/01/130 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 1] (SME1) | [Safety Module Errors] (SME)
SME2 | Safety module error 2 | 16#3BE4 = 15332 | 16#207B/21 | 16#AD/01/85 = 173/01/133 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 2] (SME2) | [Safety Module Errors] (SME)
SME3 | Safety module error 3 | 16#3BE5 = 15333 | 16#207B/22 | 16#AD/01/86 = 173/01/134 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 3] (SME3) | [Safety Module Errors] (SME)
SME4 | Safety module error 4 | 16#3BE6 = 15334 | 16#207B/23 | 16#AD/01/87 = 173/01/135 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 4] (SME4) | [Safety Module Errors] (SME)
SME5 | Safety module error 5 | 16#3BE7 = 15335 | 16#207B/24 | 16#AD/01/88 = 173/01/136 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 5] (SME5) | [Safety Module Errors] (SME)
SME6 | Safety module error 6 | 16#3BE8 = 15336 | 16#207B/25 | 16#AD/01/89 = 173/01/137 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 6] (SME6) | [Safety Module Errors] (SME)
SME7 | Safety module error 7 | 16#3BE9 = 15337 | 16#207B/26 | 16#AD/01/8A = 173/01/138 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 7] (SME7) | [Safety Module Errors] (SME)
SME8 | Safety module error 8 | 16#3BEA = 15338 | 16#207B/27 | 16#AD/01/8B = 173/01/139 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 8] (SME8) | [Safety Module Errors] (SME)
SME9 | Safety module error 9 | 16#3BEB = 15339 | 16#207B/28 | 16#AD/01/8C = 173/01/140 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Safety Module Error 9] (SME9) | [Safety Module Errors] (SME)
SFM0 | Safety fast monitoring parameter 0 | 16#465A = 18010 | 16#2096/B | 16#BB/01/0B = 187/01/11 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 0] (SFM0) | [Safety Module] (OSM)
SFM1 | Safety fast monitoring parameter 1 | 16#465B = 18011 | 16#2096/C | 16#BB/01/0C = 187/01/12 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 1] (SFM1) | [Safety Module] (OSM)
SFM2 | Safety fast monitoring parameter 2 | 16#465C = 18012 | 16#2096/D | 16#BB/01/0D = 187/01/13 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 2] (SFM2) | [Safety Module] (OSM)
SFM3 | Safety fast monitoring parameter 3 | 16#465D = 18013 | 16#2096/E | 16#BB/01/0E = 187/01/14 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 3] (SFM3) | [Safety Module] (OSM)
SFM4 | Safety fast monitoring parameter 4 | 16#465E = 18014 | 16#2096/F | 16#BB/01/0F = 187/01/15 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 4] (SFM4) | [Safety Module] (OSM)
SFM5 | Safety fast monitoring parameter 5 | 16#465F = 18015 | 16#2096/10 | 16#BB/01/10 = 187/01/16 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 5] (SFM5) | [Safety Module] (OSM)
SFM6 | Safety fast monitoring parameter 6 | 16#4660 = 18016 | 16#2096/11 | 16#BB/01/11 = 187/01/17 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 6] (SFM6) | [Safety Module] (OSM)
SFM7 | Safety fast monitoring parameter 7 | 16#4661 = 18017 | 16#2096/12 | 16#BB/01/12 = 187/01/18 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 7] (SFM7) | [Safety Module] (OSM)
SFM8 | Safety fast monitoring parameter 8 | 16#4662 = 18018 | 16#2096/13 | 16#BB/01/13 = 187/01/19 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Fast Mon 8] (SFM8) | [Safety Module] (OSM)
SSM0 | Safety supervisor object status | 16#4678 = 18040 | 16#2096/29 | 16#BB/01/29 = 187/01/41 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Supervisor Object] (SSM0) | [Safety Module] (OSM)
SSM1 | PROFIsafe Communication State | 16#4679 = 18041 | 16#2096/2A | 16#BB/01/2A = 187/01/42 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [PROFIsafe Com State] (SSM1) | [Safety Module] (OSM)
SSM2 | Safety slow monitoring parameter 2 | 16#467A = 18042 | 16#2096/2B | 16#BB/01/2B = 187/01/43 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Slow Mon 2] (SSM2) | [Safety Module] (OSM)
SSM3 | Safety slow monitoring parameter 3 | 16#467B = 18043 | 16#2096/2C | 16#BB/01/2C = 187/01/44 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Slow Mon 3] (SSM3) | [Safety Module] (OSM)
SSM4 | Safety slow monitoring parameter 4 | 16#467C = 18044 | 16#2096/2D | 16#BB/01/2D = 187/01/45 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Slow Mon 4] (SSM4) | [Safety Module] (OSM)
SSM5 | Safety slow monitoring parameter 5 | 16#467D = 18045 | 16#2096/2E | 16#BB/01/2E = 187/01/46 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Slow Mon 5] (SSM5) | [Safety Module] (OSM)
SSM6 | Safety slow monitoring parameter 6 | 16#467E = 18046 | 16#2096/2F | 16#BB/01/2F = 187/01/47 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Slow Mon 6] (SSM6) | [Safety Module] (OSM)
SSM7 | Safety slow monitoring parameter 7 | 16#467F = 18047 | 16#2096/30 | 16#BB/01/30 = 187/01/48 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Sfty Slow Mon 7] (SSM7) | [Safety Module] (OSM)
SSW0 | Safety status word bytes 1-0 | 16#468C = 18060 | 16#2096/3D | 16#BB/01/3D = 187/01/61 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Status Word 1-0] (SSW0) | [Safety Com Map] (SCM)
SSW1 | Safety status word bytes 3-2 | 16#468D = 18061 | 16#2096/3E | 16#BB/01/3E = 187/01/62 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Status Word 3-2] (SSW1) | [Safety Com Map] (SCM)
SSW2 | Safety status word bytes 5-4 | 16#468E = 18062 | 16#2096/3F | 16#BB/01/3F = 187/01/63 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Status Word 5-4] (SSW2) | [Safety Com Map] (SCM)
SSW3 | Safety status word bytes 7-6 | 16#468F = 18063 | 16#2096/40 | 16#BB/01/40 = 187/01/64 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Status Word 7-6] (SSW3) | [Safety Com Map] (SCM)
SSW4 | Safety status word bytes 9-8 | 16#4690 = 18064 | 16#2096/41 | 16#BB/01/41 = 187/01/65 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Status Word 9-8] (SSW4) | [Safety Com Map] (SCM)
SSW5 | Safety status word bytes 11-10 | 16#4691 = 18065 | 16#2096/42 | 16#BB/01/42 = 187/01/66 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Status Word 11-10] (SSW5) | [Safety Com Map] (SCM)
SSW6 | Safety status word bytes 13-12 | 16#4692 = 18066 | 16#2096/43 | 16#BB/01/43 = 187/01/67 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Status Word 13-12] (SSW6) | [Safety Com Map] (SCM)
SCW0 | Safety command word bytes 1-0 | 16#4696 = 18070 | 16#2096/47 | 16#BB/01/47 = 187/01/71 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cmd Word 1-0] (SCW0) | [Safety Com Map] (SCM)
SCW1 | Safety command word bytes 3-2 | 16#4697 = 18071 | 16#2096/48 | 16#BB/01/48 = 187/01/72 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cmd Word 3-2] (SCW1) | [Safety Com Map] (SCM)
SCW2 | Safety command word bytes 5-4 | 16#4698 = 18072 | 16#2096/49 | 16#BB/01/49 = 187/01/73 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cmd Word 5-4] (SCW2) | [Safety Com Map] (SCM)
SCW3 | Safety command word bytes 7-6 | 16#4699 = 18073 | 16#2096/4A | 16#BB/01/4A = 187/01/74 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cmd Word 7-6] (SCW3) | [Safety Com Map] (SCM)
SCW4 | Safety command word bytes 9-8 | 16#469A = 18074 | 16#2096/4B | 16#BB/01/4B = 187/01/75 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cmd Word 9-8] (SCW4) | [Safety Com Map] (SCM)
SCW5 | Safety command word bytes 11-10 | 16#469B = 18075 | 16#2096/4C | 16#BB/01/4C = 187/01/76 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cmd Word 11-10] (SCW5) | [Safety Com Map] (SCM)
SCW6 | Safety command word bytes 13-12 | 16#469C = 18076 | 16#2096/4D | 16#BB/01/4D = 187/01/77 |  | Safety module parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Cmd Word 13-12] (SCW6) | [Safety Com Map] (SCM)
LKOR | ON lock response | 16#9A2E = 39470 |  |  | LKON | Configuration and settings | R/W | WORD (Enumeration) | - | [Warning] ALRM |  | [ON Lock Response] (LKOR) | [ON lock settings] (LKON)
LKOD | ON lock time delay | 16#9A2F = 39471 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 300.0 s | [ON Lock Time Delay] (LKOD) | [ON lock settings] (LKON)
LKOS | ON lock assignment | 16#9A30 = 39472 |  |  | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [ON Lock Assignment] (LKOS) | [ON lock settings] (LKON)
CLIB | High start current | 16#9A29 = 39465 |  |  | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [High Start Current] (CLIB) | [Liquid Cooled Drive] (LQDC)

## Enumerations
List ID | Value | Display | Description
ABMF | 15 | [150 kHz] (150K) | 150 kHz
| 30 | [300 kHz] (300K) | 300 kHz
| 50 | [500 kHz] (500K) | 500 kHz
| 100 | [1000 kHz] (1M) | 1000 kHz
ACT | 0 | [Not Done] (TAB) | Not done
| 1 | [Pending] (PEND) | Test is pending
| 2 | [In Progress] (PROG) | Test in progress
| 3 | [Error] (FAIL) | Error detected
| 4 | [Autotuning Done] (DONE) | Autotuning Done
ACTION | 0 | [No Action] (NO) | No action
| 1 | [Apply Autotuning] (YES) | Apply autotuning
| 2 | [Erase Autotuning] (CLR) | Erase autotuning
ADC | 0 | [No] (NO) | No DC injection
| 1 | [Yes] (YES) | DC injection
| 2 | [Continuous] (CT) | Continuous DC injection
AFFL | 0 | [Not Active] (NO) | Not active
| 1 | [Fallback To CH1] (CH1) | Fallback to channel 1
| 2 | [Fallback To CH2] (CH2) | Fallback to channel 2
AIOL | 0 | [0 - 100%] (POS) | Positive only
| 1 | [+/- 100%] (POSNEG) | Positive and negative
AIOT | 1 | [Voltage] (10U) | Voltage
| 2 | [Current] (0A) | Current
| 5 | [Voltage +/-] (N10U) | AI bipolar volts selected
| 7 | [PTC] (PTC) | PTC
| 8 | [KTY] (KTY) | KTY
| 9 | [PT1000] (1PT3) | PT1000
| 10 | [PT100] (1PT2) | PT100
| 12 | [3 PT1000] (3PT3) | 3 PT1000
| 13 | [3 PT100] (3PT2) | 3 PT100
| 14 | [PT1000 in 3 wires] (1PT33) | PT1000 in 3 wires
| 15 | [PT100 in 3 wires] (1PT23) | PT100 in 3 wires
| 16 | [3 PT1000 in 3 wires] (3PT33) | 3 PT1000 in 3 wires
| 17 | [3 PT100 in 3 wires] (3PT23) | 3 PT100 in 3 wires
ALR | 0 | [No Warning stored] (NOA) | No warning stored
| 1 | [Fallback Frequency] (FRF) | Fallback frequency reaction
| 2 | [Speed Maintained] (RLS) | Speed maintained
| 3 | [Type of stop] (STT) | Type of stop
| 4 | [Ref Frequency Warning] (SRA) | Reference frequency warning
| 5 | [Life Cycle Warn 1] (LCA1) | Life cycle warning 1
| 6 | [Life Cycle Warn 2] (LCA2) | Life cycle warning 2
| 13 | [PumpCycle warning] (PCPA) | Pump cycle warning
| 18 | [PID error Warning] (PEE) | PID error warning
| 19 | [PID Feedback Warn] (PFA) | PID feedback warning
| 20 | [PID High Fdbck Warn] (PFAH) | PID high feedback warning
| 21 | [PID Low Fdbck Warn] (PFAL) | PID low feedback warning
| 22 | [Regulation Warning] (PISH) | Regulation warning
| 23 | [Limit Switch Reached] (LSA) | Limit switch reached
| 24 | [Slack Rope Warning] (RSDA) | Slack rope warning
| 25 | [Dynamic Load Warning] (DLDA) | Dynamic load warning
| 27 | [AI3 Th Warning] (TP3A) | AI3 thermal sensor warning
| 28 | [AI4 Th Warning] (TP4A) | AI4 thermal sensor warning
| 29 | [AI5 Th Warning] (TP5A) | AI5 thermal sensor warning
| 30 | [AI1 4-20 Warning] (AP1) | AI1 4-20 loss warning
| 32 | [AI3 4-20 Warning] (AP3) | AI3 4-20 loss warning
| 33 | [AI4 4-20 Warning] (AP4) | AI4 4-20 loss warning
| 34 | [AI5 4-20 Warning] (AP5) | AI5 4-20 loss warning
| 35 | [Device Therm Warn] (THA) | Device thermal state warning
| 36 | [Therm Junction Warn] (TJA) | Thermal junction warning
| 37 | [Fan Counter Warning] (FCTA) | Fan counter warning
| 38 | [Fan Feedback Warning] (FFDA) | Fan feedback warning
| 39 | [BR Thermal Warning] (BOA) | Braking resistor thermal warning
| 40 | [Ext. Error Warning] (EFA) | External error warning
| 41 | [Undervoltage Warning] (USA) | Undervoltage warning
| 42 | [Preventive UnderV Active] (UPA) | Preventive undervoltage active
| 43 | [Forced Run] (ERN) | Device in forced run
| 44 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 45 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 46 | [Pulse Warn Thd Reached] (FQLA) | Pulse warning threshold reached
| 47 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 48 | [High Speed Reached] (FLA) | High speed reached
| 49 | [Ref Freq High Thd reached] (RTAH) | Reference frequency high threshold reached
| 50 | [Ref Freq Low Thd reached] (RTAL) | Reference frequency low threshold reached
| 51 | [2nd Freq Thd Reached] (F2A) | 2nd frequency threshold reached
| 52 | [Current Thd Reached] (CTA) | Current threshold reached
| 53 | [Low Current Reached] (CTAL) | Low current threshold reached
| 54 | [High Torque Warning] (TTHA) | High torque warning
| 55 | [Low Torque Warning] (TTLA) | Low torque warning
| 56 | [Process Undld Warning] (ULA) | Process underload warning
| 57 | [Process Overload Warning] (OLA) | Process overload warning
| 58 | [Torque Limit Reached] (SSA) | Torque limit reached
| 59 | [Torque Control Warning] (RTA) | Torque control warning
| 60 | [Dev Thermal reached] (TAD) | Device thermal threshold reached
| 61 | [Motor Therm Thd reached] (TSA) | Motor thermal threshold reached
| 62 | [Mot2 Therm Thd reached] (TS2) | Motor 2 thermal threshold reached
| 63 | [Mot3 Therm Thd reached] (TS3) | Motor 3 thermal threshold reached
| 64 | [Mot4 Therm Thd reached] (TS4) | Motor 4 thermal threshold reached
| 65 | [Power High Threshold] (PTHA) | Power high threshold reached
| 66 | [Power Low Threshold] (PTHL) | Power low threshold reached
| 67 | [Cust Warning 1] (CAS1) | Customer warning 1
| 68 | [Cust Warning 2] (CAS2) | Customer warning 2
| 69 | [Cust Warning 3] (CAS3) | Customer warning 3
| 70 | [Cust Warning 4] (CAS4) | Customer warning 4
| 71 | [Cust Warning 5] (CAS5) | Customer warning 5
| 72 | [AFE Mains Undervoltage] (URA) | AFE Mains undervoltage
| 73 | [Power Cons Warning] (POWD) | Power Consumption warning
| 83 | [Slipping warn] (ANA) | Slipping warning
| 85 | [Load Mvt Warn] (BSA) | Load movement warning
| 86 | [Brake Cont Warn] (BCA) | Brake contact warning
| 87 | [AI1 Th Warning] (TP1A) | AI1 thermal sensor warning
| 88 | [Backspin Active] (BSC) | Backspin control function is active
| 97 | [MonitorCircuit A Warn] (IWA) | Monitoring circuit A warning
| 98 | [MonitorCircuit B Warn] (IWB) | Monitoring circuit B warning
| 99 | [MonitorCircuit C Warn] (IWC) | Monitoring circuit C warning
| 100 | [MonitorCircuit D Warn] (IWD) | Monitoring circuit D warning
| 101 | [CabinetCircuit A Warn] (CWA) | Cabinet circuit A warning
| 102 | [CabinetCircuit B Warn] (CWB) | Cabinet circuit B warning
| 103 | [CabinetCircuit C Warn] (CWC) | Cabinet circuit C warning
| 104 | [MotorWinding A Warn] (TWA) | Motor winding A warning
| 105 | [MotorWinding B Warn] (TWB) | Motor winding B warning
| 106 | [MotorBearing A Warn] (TWC) | Motor bearing A warning
| 107 | [MotorBearing B Warn] (TWD) | Motor bearing B warning
| 108 | [Circuit Breaker Warn] (CBW) | Circuit breaker warning
| 109 | [Cab I/O 24V Warn] (P24C) | Cabinet I/O 24V missing warning
| 110 | [Fallback Channel] (AFFL) | Fieldbus communication loss fallback channel is active
| 113 | [AFE Motor Limitation] (CLIM) | AFE motor limitation
| 114 | [AFE Generator Limitation] (CLIG) | AFE generator limitation
| 115 | [AFE Sensor thermal state] (THSA) | AFE sensor thermal state
| 116 | [AFE IGBT thermal state] (THJA) | AFE IGBT thermal state
| 117 | [Cabinet Fan Fdbck Warn] (FFCA) | Cabinet fan feedback warning
| 118 | [Cabinet Fan Counter Warn] (FCCA) | Cabinet fan counter warning
| 119 | [Cabinet Overheat Warn] (CHA) | Cabinet overheat warning
| 120 | [CMI Jumper Warn] (CMIJ) | CMI jumper warning
| 121 | [AFE Fan Counter Warn] (FCBA) | AFE fan counter warning
| 122 | [AFE Fan Fdbck Warn] (FFBA) | AFE fan feedback warning
| 124 | [M/S Device Warn] (MSDA) | M/S device warning
| 125 | [Backlash Warn] (BSQA) | Backlash warning
| 126 | [Encoder Thermal Warn] (TPEA) | Encoder module thermal warning
| 127 | [BUO Fan Counter Warn] (FCBB) | BUO fan counter warning
| 128 | [BUO Fan Fdbck Warn] (FFBB) | BUO fan feedback warning
| 129 | [BUO Thermal State Warn] (THWB) | BUO thermal state warning
| 130 | [AFE Bus Ref Warn] (MDW) | AFE bus reference warning
| 133 | [Temp Sens AI1 Warn] (TS1A) | Temperature sensor AI1 warning
| 135 | [Temp Sens AI3 Warn] (TS3A) | Temperature sensor AI3 warning
| 136 | [Temp Sens AI4 Warn] (TS4A) | Temperature sensor AI4 warning
| 137 | [Temp Sens AI5 Warn] (TS5A) | Temperature sensor AI5 warning
| 138 | [DC Bus Ripple Warn] (DCRW) | DC bus ripple warning
| 140 | [Cooling Pump Warn] (COPA) | Cooling pump warning
| 142 | [Module Overheat] (MOA) | Module overheat warning
| 143 | [ON Lock Warning] (LKON) | ON lock warning
| 144 | [Pwr Backup Warn] (RFTA) | Power backup mode warning
| 145 | [Internal Error 22] (INFM) | Internal error 22 (Embedded Ethernet)
| 146 | [Modbus Com Inter.] (SLF1) | Modbus communication interruption warning
APPS | 0 | [Running] (RUN) | Running
| 1 | [Stop] (STOP) | Stop
| 2 | [Local Mode Active] (LOCAL) | Local mode is active
| 3 | [Channel 2 Active] (OVER) | Channel 2 active
| 4 | [Manual Mode Active] (MANU) | Manual mode is active
| 5 | [PID Active] (AUTO) | PID active
| 10 | [Boost In progress] (BOOST) | Boost is in progress
| 11 | [Sleep Active] (SLEEP) | Sleep mode is active
| 14 | [BL In Progress] (BQS) | Backlash in progress
APPT | 0 | [Generic Pump Control] (GPMP) | Generic pump Control
| 4 | [Hoisting] (HOST) | Hoisting
| 5 | [Conveyor] (CONV) | Conveyor
| 255 | [All Applications] (ALL) | All application functions available
ASA | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [Done] (DONE) | Done
AST | 3 | [IPM align.] (IPMA) | IPM alignment
| 4 | [SPM align.] (SPMA) | SPM alignment
| 5 | [PSI align.] (PSI) | Pulse Signal injection
| 6 | [PSIO align.] (PSIO) | Pulse Signal injection - Optimized
| 7 | [Rotational Current Injection] (RCI) | Rotational current injection
| 254 | [No align.] (NO) | NO alignment
ASTS | 0 | [Not Done] (TAB) | Not done
| 1 | [Pending] (PEND) | Pending
| 2 | [In Progress] (PROG) | In progress
| 3 | [Error] (FAIL) | Error detected
| 4 | [Done] (DONE) | Done
| 5 | [Custom Value] (CUS) | Custom Value
ATA | 0 | [No] (NO) | No
| 1 | [Power On] (PON) | Power On
| 2 | [Run Command] (AUTO) | Run command
AUT | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
AVOT | 0 | [+/- 8192] (INEG) | +/- 8192
| 1 | [+/- 100%] (PNEG) | +/- 100%
BDCO | 38 | [50 kbps] (50K) | Baud rate 50kbps
| 52 | [125 kbps] (125K) | Baud rate 125kbps
| 60 | [250 kbps] (250K) | Baud rate 250kbps
| 68 | [500 kbps] (500K) | Baud rate 500kbps
| 76 | [1 Mbps] (1M) | Baud rate 1Mbps
BFR | 0 | [50 Hz] (50Hz) | 50Hz motor frequency
| 1 | [60 Hz] (60Hz) | 60Hz motor frequency
BIP | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Brake impulse Fwd
| 2 | [2 IBR] (2IBR) | Brake impulse Fwd/Rev
BLC | 0 | [No] (NO) | No
| 2 | [R2] (R2) | Relay R2
| 3 | [R3] (R3) | Relay R3
| 4 | [R4] (R4) | Relay R4
| 5 | [R5] (R5) | Relay R5
| 6 | [R6] (R6) | Relay R6
| 64 | [DQ1 Digital Output] (DO1) | DQ1 digital output
| 66 | [DQ11 Digital Output] (DO11) | DQ11 digital output
| 67 | [DQ12 Digital Output] (DO12) | DQ12 digital output
| 68 | [R61] (R61) | Relay R61
| 69 | [R62] (R62) | Relay R62
| 70 | [R63] (R63) | Relay R63
| 71 | [R64] (R64) | Relay R64
| 72 | [R65] (R65) | Relay R65
| 73 | [R66] (R66) | Relay R66
BMP | 0 | [Stop On Switching] (STOP) | Stop on switching
| 1 | [Bumpless] (BUMP) | Bumpless
| 2 | [Disabled] (DIS) | Disabled
BOA | 0 | [Inactive] (NO) | Inactive
| 1 | [Dynamic] (DYNA) | Dynamic
| 2 | [Static] (STAT) | Static
| 3 | [Constant] (CSTE) | Constant
| 4 | [Conical Motor] (CMOT) | Conical motor
BQM | 0 | [Not Configured] (NO) | Not configured
| 1 | [On Start] (START) | On start
| 2 | [On Start + Dir Change] (CHGDIR) | On Start + direction change
| 3 | [On Master Request] (MS) | On Master request
BQMM | 0 | [Sequential] (SEQ) | Sequential
| 1 | [Simultaneous] (SIMUL) | Simultaneous
BRA | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [High Torque] (DYNA) | High torque
BRC | 0 | [None] (NO)
| 1 | [None] (ALL)
| 2 | [None] (RUN)
BRO | 0 | [Ignore] (NO) | Ignore monitoring
| 1 | [Warning] (YES) | Warning triggered
| 2 | [Error] (FLT) | Error triggered
BSP | 0 | [Standard] (BSD) | Standard ref template
| 1 | [Pedestal] (BLS) | Pedestal at LSP
| 2 | [Deadband] (BNS) | Deadband at LSP
| 4 | [Deadband at 0%] (BNS0) | Deadband at 0 speed
BST | 0 | [Traveling] (HOR) | Cross traverse motion
| 1 | [Hoisting] (VER) | Hoisting motion
CAR | 0 | [No Warning Clearing] (NO) | No warning clearing
| 1 | [Clear Event 1 Warning] (RA1) | Clear Event 1 warning
| 2 | [Clear Event 2 Warning] (RA2) | Clear Event 2 warning
| 3 | [Clear Event 3 Warning] (RA3) | Clear Event 3 warning
| 4 | [Clear Event 4 Warning] (RA4) | Clear Event 4 warning
| 5 | [Clear Event 5 Warning] (RA5) | Clear Event 5 warning
CBS | 0 | [CB Not Configured] (NO) | Circuit breaker not configured
| 1 | [CB Invalid Config] (CBCI) | Circuit breaker configuration invalid
| 2 | [CB In Start Pulse] (CBST) | Circuit breaker in start pulse
| 3 | [CB Not Closed] (CBNC) | Circuit breaker not closed
| 4 | [CB Open] (CBOS) | Circuit breaker open
| 5 | [CB In Stop Pulse] (CBSP) | Circuit breaker in stop pulse
| 6 | [CB Not Open] (CBNO) | Circuit breaker not open
| 7 | [CB Closed] (CBCS) | Circuit breaker closed
| 8 | [CB stop disable] (CBSD) | Circuit breaker stop is disable
CBSR | 0 | [Error] (FLT) | Error
| 1 | [Warning] (WAR) | warning
CCA | 0 | [Not Configured] (NO) | Not Configured
| 1 | [Counter] (CPT) | Counter
| 2 | [Date and Time] (DT) | Date and time
CCS | 0 | [Mains/Control ON] (0) | Mains or Control Supply ON
| 1 | [Mains Supply ON] (1) | Mains Supply ON
| 2 | [Drive is Running] (2) | Drive in running State
CDX | 1 | [Terminals] (TER) | Terminal block
| 3 | [HMI] (LCC) | Local HMI
| 10 | [Modbus] (MDB) | Modbus communication
| 20 | [CANopen] (CAN) | CANopen communication
| 30 | [Com. Module] (NET) | Ext. communication module
| 40 | [Ethernet Embedded] (ETH) | Ethernet Embedded
CFPS | 0 | [None] (NO) | Not Assigned
| 1 | [Set No.1] (CFP1) | Parameter set 1
| 2 | [Set No.2] (CFP2) | Parameter set 2
| 3 | [Set No.3] (CFP3) | Parameter set 3
CHCF | 1 | [Not separ.] (SIM) | Combined channel mode
| 2 | [Separate] (SEP) | Separated channel mode
| 3 | [I/O profile] (IO) | I/O mode
CHR | 0 | [No] (NO) | No
| 1 | [Warning] (ALRM) | warning
| 2 | [Error] (FLT) | Error
| 3 | [Warning Then Error] (ALFLT) | Warning then error with time delay
CINR | 20 | [0.001] (0001) | 0.001
| 30 | [0.01] (001) | 0.01
| 40 | [0.1] (01) | 0.1
| 50 | [1] (1) | 1
| 60 | [10] (10) | 10
CIOA | 0 | [20/70] (20) | 20/70
| 1 | [21/71] (21) | 21/71
| 2 | [100/101] (100) | 100/101
| 3 | [Unconfig.] (UNCG) | Unconfigured
CNFS | 0 | [In progress] (NO) | In progress
| 1 | [Config. No.0] (CNF0) | Configuration 0 active
| 2 | [Config. No.1] (CNF1) | Configuration 1 active
| 3 | [Config. No.2] (CNF2) | Configuration 2 active
| 4 | [Config. No.3] (CNF3) | Configuration 3 active
CNL | 0 | [Terminals] (TER) | Terminal block
| 2 | [HMI] (LCC) | Local HMI
| 3 | [Modbus] (MDB) | Modbus communication 1
| 6 | [CANopen] (CAN) | CANopen communication
| 9 | [Com. Module] (NET) | Ext. communication module
| 11 | [Ethernet Embedded] (ETH) | Ethernet embedded
| 15 | [PC tool] (PWS) | PC tool
COFM | 0 | [Measured] (HWCOF) | Measured
| 1 | [Computed] (SWCOF) | Computed
COM1 | 0 | [R0T0] (R0T0) | R0T0
| 1 | [R0T1] (R0T1) | R0T1
| 2 | [R1T0] (R1T0) | R1T0
| 3 | [R1T1] (R1T1) | R1T1
COP | 0 | [No] (NO) | No copy
| 1 | [Reference Frequency] (SP) | Copy reference frequency
| 2 | [Command] (CD) | Copy command
| 3 | [Cmd + Ref Frequency] (ALL) | Copy command & reference frequency
CSA | 0 | [No] (NO) | Not assigned
| 1 | [AQ1] (AO1) | Analog output AQ1
| 2 | [AQ2] (AO2) | Analog output AQ2
| 32 | [PTO] (PTO) | PTO
| 129 | [Ref Frequency 1] (AIFR1) | Reference frequency 1
| 130 | [Ref Frequency 2] (AIFR2) | Reference frequency 2
| 131 | [Ref Frequency 2 Summing] (AISA2) | Reference frequency 2 Summing
| 132 | [PID feedback] (AIPIF) | PI controller feedback
| 136 | [Torque limitation] (AITAA) | Torque limitation
| 137 | [Subtract Ref Freq 2] (AIDA2) | Subtract reference frequency 2
| 138 | [Manual PID ref.] (AIPIM) | Manual PID reference
| 139 | [PID Ref Frequency] (AIFPI) | PID reference frequency
| 160 | [Ref Frequency 3 Summing] (AISA3) | Reference frequency 3 Summing
| 161 | [Ref Frequency 1B] (AIFR1B) | Reference frequency 1B
| 162 | [Subtract Ref Freq 3] (AIDA3) | Subtract reference frequency 3
| 163 | [Forced local] (AIFLOC) | Forced loc mode channel
| 164 | [Ref Frequency 2 multiplier] (AIMA2) | Reference frequency 2 multiplier
| 165 | [Ref Frequency 3 multiplier] (AIMA3) | Reference frequency 3 multiplier
| 166 | [Torque reference] (AITR1) | Torque reference 1
| 167 | [Weight input] (AIPES) | Weight sensor input
| 168 | [Virtual AI1 Channel] (AIAIC1) | Virtual AI1 channel
| 200 | [Torque Ref Offset] (AITQO) | Torque reference offset
| 201 | [Torque Ref Ratio] (AITQR) | Torque ref ratio
| 202 | [Torque limitation 2] (AITAA2) | Torque limitation 2
| 203 | [Torque reference 2] (AITR2) | Torque reference 2
| 204 | [Frequency Meter] (FQF) | Frequency meter
| 205 | [External Feed Forward] (AITEFF) | External feed forward
| 206 | [AFE Bus Ref Assign] (VREF) | AFE bus ref assignment
| 345 | [M/S Speed Ref In] (MSSI) | M/S Master speed reference input
| 346 | [M/S Trq Ref In] (MSTI) | M/S Master torque reference input
CSLFN | 0 | [No] (NO) | No
| 180 | [Jog] (FNJOG) | Jog
| 181 | [Preset Speed 1] (FNPS1) | Preset speed 1
| 182 | [Preset Speed 2] (FNPS2) | Preset speed 2
| 183 | [PID Ref Freq 1] (FNPR1) | PID reference frequency 1
| 184 | [PID Ref Freq 2] (FNPR2) | PID reference frequency 2
| 185 | [+speed] (FNUSP) | Increase speed
| 186 | [-speed] (FNDSP) | Decrease speed
CSLOUT | 0 | [No] (NO) | No
| 146 | [R2] (R2) | Relay R2
| 147 | [R3] (R3) | Relay R3
| 148 | [R4] (R4) | Relay R4
| 149 | [R5] (R5) | Relay R5
| 150 | [R6] (R6) | Relay R6
| 161 | [DQ1] (DO1) | Digital ouptut DQ1
| 163 | [DQ11 Digital Output] (DO11) | DQ11 digital output
| 164 | [DQ12 Digital Output] (DO12) | DQ12 digital output
| 209 | [R60] (R60) | Relay R60
| 210 | [R61] (R61) | Relay R61
| 211 | [R62] (R62) | Relay R62
| 212 | [R63] (R63) | Relay R63
| 213 | [R64] (R64) | Relay R64
| 214 | [R65] (R65) | Relay R65
| 215 | [R66] (R66) | Relay R66
CTT | 0 | [SVC V] (VVC) | Sensorless flux vector V
| 2 | [FVC] (FVC) | Full flux vector
| 4 | [U/F VC 5pts] (UF5) | U/F VC 5 point voltage/frequency
| 5 | [Sync. mot.] (SYN) | Synchronous motor
| 7 | [Energy Sav.] (NLD) | Energy Saving
| 9 | [Sync.CL] (FSY) | Sync.CL
| 10 | [SYN_U VC] (SYNU) | SYN_U VC law
| 12 | [Reluctance Motor] (SRVC) | Reluctance motor
DCBS | 0 | [Not Configured] (NO) | Not configured
| 1 | [Supply Unit REC] (SUREC) | Supply Unit REC
| 2 | [Supply Unit AFE] (SUAFE) | Supply Unit AFE
| 3 | [Drive with AFE] (MCELH) | Drive with AFE
| 4 | [Drive with REC] (MCPE) | Drive with REC
DCRC | 0 | [Ignore] (NO) | Ignore monitoring
| 1 | [Warning] (WARN) | Warning triggered
| 2 | [Error] (FLT) | Error triggered
DLR | 0 | [Locked drv] (DLR0) | Drive Locked
| 1 | [Unlock. drv] (DLR1) | Drive unlocked
| 2 | [Not allowed] (DLR2) | Download not allowed
| 3 | [Lock/unlock] (DLR3) | Combined Lock/Unlock
DOTD | 0 | [Freewheel Stop] (NST) | Drive freewheel stop
| 1 | [Ramp Stop] (RMP) | Ramp stop
DPMA | 1 | [Master 1] (1) | Master 1
| 2 | [Master 2] (2) | Master 2
DRT | 0 | [Normal Duty] (NORMAL) | Normal duty
| 1 | [Heavy Duty] (HIGH) | High duty
DSF | 0 | [Standard] (STD) | Standard
| 1 | [Optimized] (OPT) | Optimized
DSTA | 0 | [Stopped] (RTSTP) | Stopped
| 1 | [Cold Starting] (RTCST) | Cold starting
| 2 | [Warm Starting] (RTWST) | Warm starting
| 3 | [Parsing] (RTPAR) | Parsing
| 4 | [Cleaning] (RTCLN) | Cleaning
| 5 | [Ready] (RTRDY) | Ready
| 6 | [Running] (RTRUN) | Running
| 7 | [Preparing OC] (RTPPO) | Preparing for online change
| 8 | [Parsing OC] (RTPSO) | Parsing online change data
| 9 | [Swapping OC] (RTSWO) | Online change swap
| 10 | [Cleaning OC] (RTCLO) | Cleaning after online change
| 11 | [RollingBack OC] (RTRBO) | Rolling back online change
| 12 | [Error Stopped] (RTESP) | Error stopped
| 13 | [Clean Stopped] (RTCSP) | Clean stopped
| 14 | [Persistent Data] (RTPSD) | Removing and restoring persistent data
| 15 | [Unknown] (RTNKW) | Unknown
DUR | 0 | [5 minutes] (5) | 5 minutes
| 1 | [10 minutes] (10) | 10 minutes
| 2 | [30 minutes] (30) | 30 minutes
| 3 | [1 hour] (1H) | 1 hour
| 4 | [2 hours] (2H) | 2 hours
| 5 | [3 hours] (3H) | 3 hours
| 6 | [Unlimited] (CT) | Unlimited
ECFG | 0 | [Ignore] (NO) | Ignore
| 1 | [Freewheel Stop] (YES) | Freewheel stop
| 2 | [Configured Stop] (STT) | Configured stop [STT] parameter
| 4 | [Fallback Speed] (LFF) | Fallback speed
| 5 | [Speed maintained] (RLS) | Speed maintained
| 6 | [Ramp stop] (RMP) | Ramp stop
| 7 | [Fast stop] (FST) | Fast stop
| 8 | [DC injection] (DCI) | DC injection
EFAP | 0 | [Standard] (LINF1) | Standard
| 2 | [Saturation] (SATF) | Saturation
EFDR | 0 | [No Error] (NO) | No error
| 1 | [Server Timeout] (TOUT) | Server timeout
| 2 | [Server No File] (SNF) | Server no file
| 3 | [Server Corrupt File] (CRPT) | Server corrupt file
| 4 | [Server Empty File] (EPTY) | Server empty file
| 5 | [Device Invalid File] (HINV) | Device invalid file
| 6 | [CRC Error] (CRC) | CRC error
| 7 | [Version Incompatibility] (VRM) | Version incompatibility
| 9 | [Device No File] (HNF) | Device no file
| 10 | [Server Reading Size] (SIZE) | Server reading Size
| 11 | [Device Opening File] (OPEN) | Device opening file
| 12 | [Device Reading File] (READ) | Device reading file
| 13 | [Incompatibility] (SCNT) | Incompatibility
| 14 | [Device Invalid Name] (NINV) | Device invalid name
| 15 | [Server Incorrect File Size] (FSIZ) | Server incorrect file size
| 16 | [Device Writing File] (HWF) | Device writing file
| 17 | [Server Writing File] (SWF) | Server writing file
EMDT | 0 | [KW Counter] (KWCT) | KW counter
| 1 | [Instant. kW trend] (CVE) | Instantaneous kW trend
| 2 | [Daily kWh report] (HSD) | Daily kWh report
| 3 | [Weekly kWh report] (HSW) | Weekly kWh report
| 4 | [Monthly kWh report] (HSM) | Monthly kWh report
| 5 | [Yearly kWh report] (HSY) | Yearly kWh report
ENC | 0 | [Not done] (NO) | Encoder check not done
| 1 | [Yes] (YES) | Encoder check requested
| 2 | [Done] (DONE) | Encoder check completed
ENS | 1 | [AABB] (AABB) | For signals A/A-/B/B-
| 2 | [AB] (AB) | For signals A/B
| 3 | [A] (A) | For signal A
ENSP | 1 | [200 kHz] (200k) | 200 kHz
| 9 | [1 MHz] (1M) | 1 MHz
ENU | 0 | [No] (NO) | Inactive
| 1 | [Speed Monitoring] (SEC) | Speed feedback monitoring
| 2 | [Speed Regulation] (REG) | Speed feedback regulation
| 3 | [Speed Reference] (PGR) | Encoder as speed ref
ERRD | 16#0000 | [No Error] (NOF) | No error detected
| 16#1000 | [Precharge Capacitor] (CRF1) | Precharge capacitor
| 16#1000 | [Motor Overspeed] (SOF) | Motor overspeed
| 16#1000 | [DB unit sh. circuit] (BUF) | DB unit sh. circuit
| 16#1000 | [Internal Error 14] (INFE) | Internal error 14 (CPU)
| 16#1000 | [Braking Resistor ovld] (BOF) | Braking resistor overload
| 16#1000 | [Channel Switch Error] (CSF) | Channel switching detected error
| 16#1000 | [Angle error] (ASF) | Angle error
| 16#2130 | [AFE ShortCircuit error] (SCF6) | AFE ShortCircuit error
| 16#2230 | [IGBT Short Circuit] (SCF4) | IGBT short circuit
| 16#2310 | [Overcurrent] (OCF) | Overcurrent
| 16#2310 | [BUO Overcurrent error] (BUOC) | BUO overcurrent error
| 16#2311 | [Process Overload] (OLC) | Process overload
| 16#2320 | [Motor short circuit] (SCF1) | Motor short circuit
| 16#2320 | [Motor Short Circuit] (SCF5) | Motor short circuit
| 16#2330 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 16#2350 | [Motor Overload] (OLF) | Motor overload
| 16#3110 | [Supply Mains Overvoltage] (OSF) | Supply mains overvoltage
| 16#3120 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 16#3130 | [Input Phase Loss] (PHF) | Input phase loss
| 16#3280 | [AFE Bus unbalancing] (OBF2) | AFE Bus unbalancing
| 16#3300 | [Single output phase loss] (OPF1) | Single output phase loss
| 16#3310 | [DC Bus Overvoltage] (OBF) | DC bus overvoltage
| 16#3310 | [Output Phase Loss] (OPF2) | Output phase loss
| 16#4210 | [Input Overheating] (IHF) | Input Overheating
| 16#4210 | [Device Overheating] (OHF) | Device overheating
| 16#4210 | [Device Overheating] (TJF) | Device overheating
| 16#4210 | [Fan Feedback Error] (FFDF) | Fan feedback error
| 16#4210 | [Module Overheat] (MOF) | Module overheat error
| 16#4210 | [AI3 Th Level Error] (TH3F) | AI3 thermal level error
| 16#4210 | [AI4 Th Level Error] (TH4F) | AI4 thermal level error
| 16#4210 | [AI5 Th Level Error] (TH5F) | AI5 thermal level error
| 16#4210 | [AI1 Th Level Error] (TH1F) | AI1 thermal level error
| 16#4210 | [Encoder Th Level Error] (THEF) | Encoder module thermal level error
| 16#4210 | [BUO Overheat error] (BUHF) | BUO overheat error
| 16#4210 | [Cooling Pump Error] (COPF) | Cooling pump error
| 16#5000 | [Out Contact Closed Error] (FCF1) | Output contactor closed error
| 16#5000 | [Out Contact Opened Error] (FCF2) | Output contactor opened error
| 16#5000 | [Input Contactor] (LCF) | input contactor
| 16#5000 | [Egy Saving Exit Error] (IDLF) | Idle mode exit error
| 16#5100 | [Internal Error 8] (INF8) | Internal error 8 (Switching Supply)
| 16#5100 | [Internal Error 10] (INFA) | Internal error 10 (Mains)
| 16#5210 | [Internal Error 9] (INF9) | Internal error 9 (Measure)
| 16#5210 | [Internal Error 11] (INFB) | Internal error 11 (Temperature)
| 16#5210 | [Internal Error 12] (INFC) | Internal error 12 (Internal current supply)
| 16#5210 | [Internal Error 13] (INFD) | Internal error 13 (Diff current)
| 16#5500 | [Internal Error 15] (INFF) | Internal error 15 (Flash)
| 16#5530 | [Control Memory Error] (EEF1) | Control memory error
| 16#5530 | [Power Memory Error] (EEF2) | Power memory error
| 16#6100 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 16#6100 | [Internal Error 1] (INF1) | Internal error 1 (Rating)
| 16#6100 | [Internal Error 2] (INF2) | Internal error 2 (Soft)
| 16#6100 | [Internal Error 3] (INF3) | Internal error 3 (Intern Comm)
| 16#6100 | [Internal Error 4] (INF4) | Internal error 4 (Manufacturing)
| 16#6100 | [Internal Error 7] (INF7) | Internal error 7 (Init)
| 16#6100 | [Internal Error 6] (INF6) | Internal error 6 (Option)
| 16#6100 | [Boards Compatibility] (HCF) | Boards compatibility
| 16#6100 | [Internal Error 0] (INF0) | Internal error 0 (IPC)
| 16#6100 | [Internal Error 21] (INFL) | Internal error 21 (RTC)
| 16#6100 | [Internal Error 22] (INFM) | Internal error 22 (Embedded Ethernet)
| 16#6100 | [Internal Error 25] (INFP) | Internal error 25 (Incompatibility CB & SW)
| 16#6100 | [Internal Error 20] (INFK) | Internal error 20 (option interface PCBA)
| 16#6100 | [Internal Error 27] (INFR) | Internal error 27 (Diagnostics CPLD)
| 16#6100 | [MonitorCircuit A Error] (IFA) | Monitoring circuit A error
| 16#6100 | [MonitorCircuit B Error] (IFB) | Monitoring circuit B error
| 16#6100 | [MonitorCircuit C Error] (IFC) | Monitoring circuit C error
| 16#6100 | [MonitorCircuit D Error] (IFD) | Monitoring circuit D error
| 16#6100 | [CabinetCircuit A Error] (CFA) | Cabinet circuit A error
| 16#6100 | [CabinetCircuit B Error] (CFB) | Cabinet circuit B error
| 16#6100 | [CabinetCircuit C Error] (CFC) | Cabinet circuit C error
| 16#6100 | [MotorWinding A Error] (TFA) | Motor winding A error
| 16#6100 | [MotorWinding B Error] (TFB) | Motor winding B error
| 16#6100 | [MotorBearing A Error] (TFC) | Motor bearing A error
| 16#6100 | [MotorBearing B Error] (TFD) | Motor bearing B error
| 16#6100 | [Cabinet Overheat Error] (CHF) | Cabinet overheat error
| 16#6100 | [AFE Mains Undervoltage] (URF) | AFE Mains undervoltage
| 16#6100 | [Internal Error 31] (INFV) | Internal error 31 (Missing brick)
| 16#6100 | [Internal Error 29] (INFT) | Internal error 29 (Inverter)
| 16#6100 | [Internal Error 30] (INFU) | Internal error 30 (Rectifier)
| 16#6100 | [AFE IGBT over-heat error] (TJF2) | AFE IGBT over-heat error
| 16#6100 | [AFE contactor feedback error] (CRF3) | AFE contactor feedback error
| 16#6100 | [AFE DC-Caps Error] (ACF1) | AFE DC-capacitors error
| 16#6100 | [AFE Current Control Error] (ACF2) | AFE current control error
| 16#6100 | [Mains Freq Out Of Range] (MFF) | Mains frequency out of range
| 16#6100 | [Internal Error 32] (INFW) | Internal error 32 (Firmware Update)
| 16#6100 | [AFE Line Filter Error] (ACF3) | AFE Line filter error
| 16#6300 | [Incorrect Config] (CFF) | Incorrect configuration
| 16#6300 | [Invalid Configuration] (CFI) | Invalid configuration
| 16#6300 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 16#6300 | [Pre-settings Transfer Error] (CFI3) | Pre-settings transfer error
| 16#6300 | [Circuit Breaker Error] (CBF) | Circuit breaker error
| 16#6300 | [Empty Configuration] (CFI4) | Empty configuration
| 16#6300 | [SD Error] (SDFT) | Synchro to drive error
| 16#7000 | [Internal Error 16] (INFG) | Internal error 16 (IO module - relay)
| 16#7000 | [Internal Error 17] (INFH) | Internal error 17 (IO module - Standard)
| 16#7000 | [Internal Error 18] (INFI) | Internal error 18 (Safety function module)
| 16#7000 | [Firmware Update Error] (FWER) | Firmware Update error
| 16#7000 | [Internal Error 19] (INFJ) | Internal error 19 (Encoder module)
| 16#7110 | [Brake Feedback] (BRF) | Brake feedback
| 16#7110 | [Load Mvt Error] (MDCF) | Load movement error
| 16#7121 | [Motor Stall Error] (STF) | Motor stall detected error
| 16#7300 | [Load slipping] (ANF) | Load slipping
| 16#7300 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 16#7300 | [AI4 4-20mA loss] (LFF4) | AI4 4-20mA loss
| 16#7300 | [AI5 4-20 mA loss] (LFF5) | AI5 4-20 mA loss
| 16#7300 | [AI1 4-20 mA loss] (LFF1) | AI1 4-20 mA loss
| 16#7300 | [AI3 Thermal Sensor Error] (T3CF) | Thermal sensor error on AI3
| 16#7300 | [AI4 Thermal Sensor Error] (T4CF) | Thermal sensor error on AI4
| 16#7300 | [AI5 Thermal Sensor Error] (T5CF) | Thermal sensor error on AI5
| 16#7300 | [DB unit op. circuit] (BUFO) | DB unit open circuit
| 16#7300 | [Drive Overload] (TLOF) | Drive overload
| 16#7300 | [AI1 Thermal Sensor Error] (T1CF) | Thermal sensor error on AI1
| 16#7300 | [Encoder Th Sensor Error] (TECF) | Thermal sensor error on encoder module
| 16#7310 | [Encoder Feedback Loss] (SPF) | Encoder feedback loss
| 16#7310 | [Encoder Coupling] (ECF) | Encoder coupling
| 16#7310 | [Encoder] (ENF) | Encoder
| 16#7400 | [Program Loading Error] (PGLF) | Program loading detected error
| 16#7400 | [Program Running Error] (PGRF) | Program running detected error
| 16#7500 | [PID Feedback Error] (PFMF) | PID feedback detected error
| 16#7510 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 16#7510 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 16#7520 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 16#7530 | [PC Com Interruption] (SLF2) | PC communication interruption
| 16#7540 | [Embd Eth Com Interrupt] (ETHF) | Embedded Ethernet communication interruption
| 16#7810 | [Security Files Corrupt] (SPFC) | Security files corrupt
| 16#8100 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 16#8800 | [Internal Error 23] (INFN) | Internal error 23 (Module link)
| 16#9000 | [External Error] (EPF1) | External detected error
| 16#9000 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 16#9000 | [FDR 1 Error] (FDR1) | FDR Eth embedded error
| 16#9000 | [FDR 2 Error] (FDR2) | FDR Eth module error
| 16#FF00 | [Autotuning Error] (TNF) | Autotuning detected error
| 16#FF01 | [Brake Control] (BLF) | Brake control
| 16#FF02 | [Torque Limitation Error] (SSF) | Torque limitation error
| 16#FF02 | [Torque timeout] (SRF) | Torque timeout
| 16#FF03 | [Process Underload] (ULF) | Process underload
| 16#FF03 | [Safety Function Error] (SAFF) | Safety function detected error
| 16#FF03 | [Safety Violation] (SAVF) | Safety violation
| 16#FF03 | [Safety Config Error] (SCFF) | Safety configuration error
| 16#FF03 | [Safety IO Error] (SIOF) | Safety IO error
| 16#FF11 | [PumpCycle start Error] (PCPF) | Pump cycle start error
| 16#FF20 | [ON Lock Error] (LKON) | ON lock error
| 16#FF80 | [Dynamic Load Error] (DLF) | Dynamic load detected error
| 16#FFFF | [Internal Error 28] (INFS) | Internal error 28 (AFE)
| 16#FFFF | [MultiDrive Link Error] (MDLF) | MultiDrive Link error
| 16#FFFF | [Backlash Error] (BSQF) | Backlash error
| 16#FFFF | [M/S Device Error] (MSDF) | M/S device error
| 16#FFFF | [AFE Bus Ref Error] (MDF) | AFE bus reference error
| 16#FFFF | [Cab I/O 24V Error] (P24C) | Cabinet I/O 24V missing error
| 16#FFFF | [DC Bus Ripple Error] (DCRE) | DC Bus ripple error
ETST | 1 | [Init] (INIT) | Init
| 2 | [PreOp] (PROP) | PreOp
| 3 | [Boot] (BOOT) | Boot
| 4 | [SafeOp] (SFOP) | SafeOp
| 8 | [Op] (OP) | Op
FCS | 0 | [No] (NO) | No
| 1 | [Recall customer parameter set 0] (REC0) | Recall customer parameter set 0
| 2 | [Recall customer parameter set 1] (REC1) | Recall customer parameter set 1
| 3 | [Recall customer parameter set 2] (REC2) | Recall customer parameter set 2
| 4 | [Recall customer parameter set 3] (REC3) | Recall customer parameter set 3
| 64 | [Recall default parameter set] (INI) | Recall default parameter set
| 71 | [Recall OEM default parameter set] (INI1) | Recall OEM default parameter set
FCSI | 0 | [Macro Config] (INI) | Macro configuration
| 2 | [Config 1] (CFG1) | Configuration 1
| 3 | [Config 2] (CFG2) | Configuration 2
| 4 | [Config 3] (CFG3) | Config 3
FDRA | 0 | [NOT ACTIVE] (IDLE) | NOT ACTIVE
| 1 | [SAVE] (SAVE) | SAVE
| 2 | [REST] (REST) | REST
FFM | 0 | [Standard] (STD) | Standard
| 1 | [Always] (RUN) | Always
| 2 | [Never] (STP) | Never
| 3 | [Economy] (ECO) | Economy
FLR | 0 | [Not Configured] (NO) | Not configured
| 1 | [Yes On Freewheel] (YES) | Yes on freewheel
| 2 | [Yes Always] (ALL) | Yes always
FLU | 0 | [Not continuous] (FNC) | Not continuous
| 1 | [Continuous] (FCT) | Continuous
| 2 | [No] (FNO) | No
FOR | 2 | [8-O-1] (8O1) | 8bit odd parity 1stop bit
| 3 | [8-E-1] (8E1) | 8 bits even parity 1 stop bit
| 4 | [8-N-1] (8N1) | 8bit no parity 1stop bit
| 5 | [8-N-2] (8N2) | 8bit no parity 2stop bits
FRES | 0 | [4kHz] (4K) | 4kHz
| 1 | [8kHz] (8K) | 8kHz
| 2 | [12kHz] (12K) | 12kHz
FWER | 0 | [No Error] (NO) | No error
| 1 | [Lock Error] (LOCK) | Lock error
| 2 | [Package Error] (MD5) | Package error
| 3 | [Package compatibility error] (COMP) | Package compatibility error
| 4 | [Ask error] (ASK) | Ask error
| 5 | [Reset Device Error] (RESET) | Reset device error
| 6 | [Conf Saving Warning] (SAVE) | Configuration saving warning
| 7 | [Conf Loading Warning] (LOAD) | Conf loading warning
| 8 | [Post Script Warning] (SCP) | Post Script warning
| 9 | [Package Description Error] (DES) | Package Description error
| 10 | [Package not found] (PKG) | Package not found
| 11 | [Power Supply error] (SPWR) | Power Supply error
| 12 | [Boot M3 error] (BTM3) | Boot M3 error
| 13 | [Boot C28 error] (BTC28) | Boot C28 error
| 14 | [M3 Error] (M3) | M3 error
| 15 | [C28 error] (C28) | C28 error
| 16 | [CPLD error] (CPLD) | CPLD error
| 17 | [Boot Power Error] (PWR) | Boot power error
| 18 | [Emb. Eth Boot Error] (EMBT) | Embedded ethernet boot error
| 19 | [Emb. Eth Error] (EMIL) | Embedded ethernet error
| 20 | [Emb. Eth Web Error] (EMWB) | Embedded ethernet WebServer error
| 21 | [Module Eth Boot Error] (OPTBT) | Module ethernet boot error
| 22 | [Module Eth Error] (OPTIL) | Module ethernet error
| 23 | [Module Eth Web Error] (OPTWB) | Module ethernet WebServer error
| 24 | [Password enabled] (PSWD) | Password enabled
| 25 | [Flash Error] (MEM) | Flash error
| 26 | [Package error] (IFO) | Package error
| 27 | [Wait] (WAIT) | Wait
FWST | 0 | [Inactive] (CHECK) | Firmware update inactive
| 1 | [PwrUpd in progress] (POWER) | Power update in progress
| 2 | [PwrUpd Pending] (PEND) | Power update pending
| 3 | [Ready] (RDY) | Firmware update ready
| 4 | [Inactive] (NO) | Firmware update inactive
| 5 | [Succeeded] (SUCCD) | Firmware update succeded
| 6 | [Update Error] (FAILED) | Update error
| 7 | [In Progress] (PROG) | Firmware update in progress
| 8 | [Requested] (RQSTD) | Firmware update requested
| 9 | [Transfer In Progress] (TRLD) | Transfer In Progress
| 10 | [Transfer Done] (TROK) | Transfer Done
| 11 | [Package cleared] (CLEAR) | Package cleared
| 12 | [Warning] (SUCWR) | Firmware update succeded with warnings
| 13 | [Device State Error] (FLSTA) | Device state error
| 14 | [Package Error] (FLPKG) | Package error
| 15 | [Saving conf] (SAVE) | Saving current configuration
| 16 | [Post Script] (POST) | Post Script
HMIS | 0 | [Autotuning] (TUN) | Drive automatic tuning
| 1 | [In DC inject.] (DCB) | DC injection
| 2 | [Ready] (RDY) | Ready
| 3 | [Freewheel] (NST) | Freewheel stop
| 4 | [Running] (RUN) | Running
| 5 | [Accelerating] (ACC) | Accelerating
| 6 | [Decelerating] (DEC) | Decelerating
| 7 | [Current Limitation] (CLI) | In current limitation
| 8 | [Fast stop] (FST) | Fast stop
| 9 | [Mot. fluxing] (FLU) | Motor fluxing
| 11 | [No Mains Voltage] (NLP) | No mains voltage
| 13 | [control.stop] (CTL) | Control stopping
| 14 | [Dec. adapt.] (OBR) | Dec ramp adaptation
| 15 | [Output cut] (SOC) | Output cut
| 17 | [Undervoltage Warning] (USA) | Undervoltage warning
| 18 | [TC Mode Active] (TC) | TC mode active
| 19 | [In autotest] (ST) | In autotest
| 20 | [Autotest error] (FA) | Autotest error
| 21 | [Autotest OK] (OK) | Autotest OK
| 22 | [EEprom test] (EP) | EEprom test
| 23 | [Operating State "Fault"] (FLT) | Operating state "Fault"
| 25 | [DCP Flashing Mode] (DCP) | DCP Flashing mode
| 28 | [SS1 Active] (SS1) | SS1 active
| 29 | [SLS Active] (SLS) | SLS active
| 30 | [STO active] (STO) | STO active
| 35 | [Energy Saving] (IDLE) | Energy Saving
| 36 | [Firmware Update] (FWUP) | Firmware Update
| 37 | [AFE Mains Undervoltage] (URA) | AFE Mains undervoltage
| 38 | [Angle test] (ASA) | Angle test
| 39 | [Backspin Active] (BSC) | Backspin control function is active
| 40 | [SOS Active] (SOS) | SOS active
| 41 | [SS2 Active] (SS2) | SS2 active
| 42 | [SMS Active] (SMS) | SMS active
| 43 | [Safety Config Test] (SCTP) | Safety configuration test
| 44 | [Safety Function] (SFTY) | Safety function
| 56 | [Synchro. To Mains] (SYTM) | Synchro to mains
| 57 | [Rdy Transfer To Mains] (RTTM) | Ready to transfer to mains
| 58 | [Transfer In Progress] (TTMI) | Transfer in progress
HSO | 0 | [No] (NO) | Inactive
| 1 | [Reference Frequency] (SSO) | Reference frequency
| 2 | [Current Limit] (CSO) | Current limit
HSOM | 0 | [Not Configured] (NO) | Not configured
| 1 | [Forward] (UP) | Forward
| 2 | [Reverse] (DOWN) | Reverse
| 3 | [Forward and Reverse] (ALL) | Forward and Reverse
IFM | 0 | [Always Active] (ALL) | Always active
| 1 | [Ready & Run State] (RRY) | Ready and Run state
| 2 | [Run State] (RUN) | Run state
INCPER | 0 | [0.01%] (001) | 0.01%
| 1 | [0.1%] (01) | 0.1%
| 2 | [1%] (1) | 1%
INHS | 0 | [Disabled] (NO) | Disabled
| 1 | [Forced Run FW] (FRD) | Forced Run in forward direction
| 2 | [Forced Run RV] (RRS) | Forced Run in reverse direction
INR | 0 | [0.01] (001) | hundredths of seconds
| 1 | [0.1] (01) | Tenths of seconds
| 2 | [1] (1) | seconds
IPAA | 0 | [Inactive] (DEAC) | Inactive
| 1 | [Save] (SAVE) | Save
| 2 | [Restore] (REST) | Restore
IPAC | 0 | [In Progress] (EXEC) | In Progress
| 1 | [Save - Success] (SASU) | Save - Success
| 2 | [Save - Error] (SAER) | Save - Error
| 3 | [Restore - Success] (RESU) | Restore - Success
| 4 | [Restore - Error] (REER) | Restore - Error
IPAE | 0 | [Idle State] (IDLE) | Idle State
| 1 | [Init] (INIT) | Init
| 2 | [Configuration] (CONF) | Configuration
| 3 | [Ready] (RDY) | Ready
| 4 | [Operational] (OPE) | Operational
| 5 | [Not Configured] (UCFG) | Not Configured
| 6 | [Unrecoverable Error] (UREC) | Unrecoverable error
IPAM | 0 | [Active Drive Config] (ACTI) | Active drive configuration
| 1 | [All Drive Config] (FULL) | All drive configurations
IPM | 0 | [Fixed] (MANU) | Fixed address
| 1 | [BOOTP] (BOOTP) | BOOTP
| 2 | [DHCP] (DHCP) | DHCP
| 3 | [DCP] (DCP) | DCP
LAC | 0 | [Basic] (BAS) | Basic access
| 1 | [Standard] (STD) | Standard access
| 3 | [Expert] (EPR) | Expert access
| 4 | [Services] (SER) | Services
LDD | 0 | [Distrib. Log. DISABLE] (NO) | Distribution logging disable
| 1 | [Motor Frequency] (RFR) | Motor frequency
| 2 | [Motor Current] (LCR) | Motor current
| 3 | [Motor Speed] (SPD) | Motor speed
| 4 | [Motor Voltage] (UOP) | Motor voltage
| 5 | [Motor Mech. Power] (OPRW) | Motor mechanical power
| 6 | [Input Elec. Power] (IPRW) | Input Electrical power
| 7 | [Output Elec. Power] (EPRW) | Output Electrical power
| 8 | [Motor Torque] (OTR) | Motor torque
| 9 | [Mains Voltage] (ULN) | Mains Voltage
| 10 | [DC BUS Voltage] (VBUS) | DC BUS Voltage
| 11 | [PID feedback] (RPF) | PID feedback
| 12 | [AI2 Th Value] (TH2V) | AI2 thermal value
| 13 | [AI3 Th Value] (TH3V) | AI3 thermal value
| 14 | [AI4 Th Value] (TH4V) | AI4 thermal value
| 15 | [AI5 Th Value] (TH5V) | AI5 thermal value
| 16 | [Drive Thermal State] (THD) | Drive Thermal State
| 17 | [Motor Thermal State] (THR) | Motor Thermal State
| 18 | [Installation Flow] (FS1V) | Installation flow
| 19 | [Pump Flow] (FS2V) | Pump flow
| 20 | [Inlet Pressure] (PS1V) | Inlet pressure
| 21 | [Outlet Pressure] (PS2V) | Outlet pressure
| 22 | [Energy Consum. Ind.] (ECI) | Energy consumption indicator
| 23 | [Pump efficiency] (EFY) | Pump efficiency
| 24 | [Energy Perf. Ind.] (EPI) | Energy Performance Indicator
| 25 | [Mains Current] (ILN) | Mains current
| 26 | [Input Reactive Power] (IQRW) | Input reactive power
| 27 | [Input Power Factor] (PWF) | Input power factor
| 28 | [AI1 Th Value] (TH1V) | AI1 thermal value
| 29 | [DBR Thermal State] (THB) | DBR thermal state
LDEN | 0 | [Stop] (STOP) | Stop
| 1 | [Start] (START) | Start
| 2 | [Always] (ALWAYS) | Always
| 3 | [Reset] (RESET) | Reset
| 4 | [Clear] (CLEAR) | Clear
| 5 | [Error] (ERROR) | Error
LDST | 2 | [200 ms] (200MS) | 200 ms
| 10 | [1 second] (1S) | 1 second
| 20 | [2 seconds] (2S) | 2 seconds
| 50 | [5 seconds] (5S) | 5 seconds
LFT | 0 | [No Error] (NOF) | No error detected
| 2 | [Control Memory Error] (EEF1) | Control memory error
| 3 | [Incorrect Config] (CFF) | Incorrect configuration
| 4 | [Invalid Configuration] (CFI) | Invalid configuration
| 5 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 6 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 7 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 8 | [External Error] (EPF1) | External detected error
| 9 | [Overcurrent] (OCF) | Overcurrent
| 10 | [Precharge Capacitor] (CRF1) | Precharge capacitor
| 11 | [Encoder Feedback Loss] (SPF) | Encoder feedback loss
| 12 | [Load slipping] (ANF) | Load slipping
| 15 | [Input Overheating] (IHF) | Input Overheating
| 16 | [Device Overheating] (OHF) | Device overheating
| 17 | [Motor Overload] (OLF) | Motor overload
| 18 | [DC Bus Overvoltage] (OBF) | DC bus overvoltage
| 19 | [Supply Mains Overvoltage] (OSF) | Supply mains overvoltage
| 20 | [Single output phase loss] (OPF1) | Single output phase loss
| 21 | [Input Phase Loss] (PHF) | Input phase loss
| 22 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 23 | [Motor short circuit] (SCF1) | Motor short circuit
| 24 | [Motor Overspeed] (SOF) | Motor overspeed
| 25 | [Autotuning Error] (TNF) | Autotuning detected error
| 26 | [Internal Error 1] (INF1) | Internal error 1 (Rating)
| 27 | [Internal Error 2] (INF2) | Internal error 2 (Soft)
| 28 | [Internal Error 3] (INF3) | Internal error 3 (Intern Comm)
| 29 | [Internal Error 4] (INF4) | Internal error 4 (Manufacturing)
| 30 | [Power Memory Error] (EEF2) | Power memory error
| 32 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 33 | [Output Phase Loss] (OPF2) | Output phase loss
| 34 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 35 | [Brake Control] (BLF) | Brake control
| 37 | [Internal Error 7] (INF7) | Internal error 7 (Init)
| 38 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 40 | [Internal Error 8] (INF8) | Internal error 8 (Switching Supply)
| 41 | [Brake Feedback] (BRF) | Brake feedback
| 42 | [PC Com Interruption] (SLF2) | PC communication interruption
| 43 | [Encoder Coupling] (ECF) | Encoder coupling
| 44 | [Torque Limitation Error] (SSF) | Torque limitation error
| 45 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 51 | [Internal Error 9] (INF9) | Internal error 9 (Measure)
| 52 | [Internal Error 10] (INFA) | Internal error 10 (Mains)
| 53 | [Internal Error 11] (INFB) | Internal error 11 (Temperature)
| 54 | [Device Overheating] (TJF) | Device overheating
| 55 | [IGBT Short Circuit] (SCF4) | IGBT short circuit
| 56 | [Motor Short Circuit] (SCF5) | Motor short circuit
| 57 | [Torque timeout] (SRF) | Torque timeout
| 58 | [Out Contact Closed Error] (FCF1) | Output contactor closed error
| 59 | [Out Contact Opened Error] (FCF2) | Output contactor opened error
| 60 | [Internal Error 12] (INFC) | Internal error 12 (Internal current supply)
| 62 | [Encoder] (ENF) | Encoder
| 64 | [Input Contactor] (LCF) | input contactor
| 65 | [DB unit sh. circuit] (BUF) | DB unit sh. circuit
| 68 | [Internal Error 6] (INF6) | Internal error 6 (Option)
| 69 | [Internal Error 14] (INFE) | Internal error 14 (CPU)
| 70 | [Braking Resistor ovld] (BOF) | Braking resistor overload
| 71 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 72 | [AI4 4-20mA loss] (LFF4) | AI4 4-20mA loss
| 73 | [Boards Compatibility] (HCF) | Boards compatibility
| 76 | [Dynamic Load Error] (DLF) | Dynamic load detected error
| 77 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 79 | [AI5 4-20 mA loss] (LFF5) | AI5 4-20 mA loss
| 80 | [Fan Feedback Error] (FFDF) | Fan feedback error
| 81 | [Module Overheat] (MOF) | Module overheat error
| 82 | [ON Lock Error] (LKON) | ON lock error
| 99 | [Channel Switch Error] (CSF) | Channel switching detected error
| 100 | [Process Underload] (ULF) | Process underload
| 101 | [Process Overload] (OLC) | Process overload
| 105 | [Angle error] (ASF) | Angle error
| 106 | [AI1 4-20 mA loss] (LFF1) | AI1 4-20 mA loss
| 107 | [Safety Function Error] (SAFF) | Safety function detected error
| 112 | [AI3 Th Level Error] (TH3F) | AI3 thermal level error
| 113 | [AI3 Thermal Sensor Error] (T3CF) | Thermal sensor error on AI3
| 114 | [PumpCycle start Error] (PCPF) | Pump cycle start error
| 120 | [AI4 Th Level Error] (TH4F) | AI4 thermal level error
| 121 | [AI4 Thermal Sensor Error] (T4CF) | Thermal sensor error on AI4
| 122 | [AI5 Th Level Error] (TH5F) | AI5 thermal level error
| 123 | [AI5 Thermal Sensor Error] (T5CF) | Thermal sensor error on AI5
| 127 | [PID Feedback Error] (PFMF) | PID feedback detected error
| 128 | [Program Loading Error] (PGLF) | Program loading detected error
| 129 | [Program Running Error] (PGRF) | Program running detected error
| 133 | [Safety Violation] (SAVF) | Safety violation
| 134 | [Safety Config Error] (SCFF) | Safety configuration error
| 135 | [Safety IO Error] (SIOF) | Safety IO error
| 142 | [Internal Error 16] (INFG) | Internal error 16 (IO module - relay)
| 143 | [Internal Error 17] (INFH) | Internal error 17 (IO module - Standard)
| 144 | [Internal Error 0] (INF0) | Internal error 0 (IPC)
| 146 | [Internal Error 13] (INFD) | Internal error 13 (Diff current)
| 147 | [Internal Error 18] (INFI) | Internal error 18 (Safety function module)
| 148 | [Motor Stall Error] (STF) | Motor stall detected error
| 149 | [Internal Error 21] (INFL) | Internal error 21 (RTC)
| 150 | [Embd Eth Com Interrupt] (ETHF) | Embedded Ethernet communication interruption
| 151 | [Internal Error 15] (INFF) | Internal error 15 (Flash)
| 152 | [Firmware Update Error] (FWER) | Firmware Update error
| 153 | [Internal Error 22] (INFM) | Internal error 22 (Embedded Ethernet)
| 154 | [Internal Error 25] (INFP) | Internal error 25 (Incompatibility CB & SW)
| 155 | [Internal Error 20] (INFK) | Internal error 20 (option interface PCBA)
| 156 | [Internal Error 19] (INFJ) | Internal error 19 (Encoder module)
| 157 | [Internal Error 27] (INFR) | Internal error 27 (Diagnostics CPLD)
| 158 | [Internal Error 23] (INFN) | Internal error 23 (Module link)
| 159 | [AFE ShortCircuit error] (SCF6) | AFE ShortCircuit error
| 160 | [AFE Bus unbalancing] (OBF2) | AFE Bus unbalancing
| 161 | [Internal Error 28] (INFS) | Internal error 28 (AFE)
| 162 | [MonitorCircuit A Error] (IFA) | Monitoring circuit A error
| 163 | [MonitorCircuit B Error] (IFB) | Monitoring circuit B error
| 164 | [MonitorCircuit C Error] (IFC) | Monitoring circuit C error
| 165 | [MonitorCircuit D Error] (IFD) | Monitoring circuit D error
| 166 | [CabinetCircuit A Error] (CFA) | Cabinet circuit A error
| 167 | [CabinetCircuit B Error] (CFB) | Cabinet circuit B error
| 168 | [CabinetCircuit C Error] (CFC) | Cabinet circuit C error
| 169 | [MotorWinding A Error] (TFA) | Motor winding A error
| 170 | [MotorWinding B Error] (TFB) | Motor winding B error
| 171 | [MotorBearing A Error] (TFC) | Motor bearing A error
| 172 | [MotorBearing B Error] (TFD) | Motor bearing B error
| 173 | [Cabinet Overheat Error] (CHF) | Cabinet overheat error
| 174 | [AFE Mains Undervoltage] (URF) | AFE Mains undervoltage
| 175 | [Internal Error 31] (INFV) | Internal error 31 (Missing brick)
| 176 | [Internal Error 29] (INFT) | Internal error 29 (Inverter)
| 177 | [Internal Error 30] (INFU) | Internal error 30 (Rectifier)
| 179 | [AFE IGBT over-heat error] (TJF2) | AFE IGBT over-heat error
| 180 | [AFE contactor feedback error] (CRF3) | AFE contactor feedback error
| 181 | [Pre-settings Transfer Error] (CFI3) | Pre-settings transfer error
| 182 | [Circuit Breaker Error] (CBF) | Circuit breaker error
| 184 | [DB unit op. circuit] (BUFO) | DB unit open circuit
| 185 | [Drive Overload] (TLOF) | Drive overload
| 186 | [MultiDrive Link Error] (MDLF) | MultiDrive Link error
| 187 | [AI1 Th Level Error] (TH1F) | AI1 thermal level error
| 188 | [AI1 Thermal Sensor Error] (T1CF) | Thermal sensor error on AI1
| 189 | [Backlash Error] (BSQF) | Backlash error
| 190 | [M/S Device Error] (MSDF) | M/S device error
| 191 | [AFE DC-Caps Error] (ACF1) | AFE DC-capacitors error
| 192 | [AFE Current Control Error] (ACF2) | AFE current control error
| 193 | [Mains Freq Out Of Range] (MFF) | Mains frequency out of range
| 194 | [Encoder Th Level Error] (THEF) | Encoder module thermal level error
| 195 | [Encoder Th Sensor Error] (TECF) | Thermal sensor error on encoder module
| 196 | [Empty Configuration] (CFI4) | Empty configuration
| 197 | [Internal Error 32] (INFW) | Internal error 32 (Firmware Update)
| 198 | [BUO Overheat error] (BUHF) | BUO overheat error
| 199 | [BUO Overcurrent error] (BUOC) | BUO overcurrent error
| 200 | [FDR 1 Error] (FDR1) | FDR Eth embedded error
| 201 | [FDR 2 Error] (FDR2) | FDR Eth module error
| 202 | [AFE Bus Ref Error] (MDF) | AFE bus reference error
| 203 | [Cab I/O 24V Error] (P24C) | Cabinet I/O 24V missing error
| 206 | [DC Bus Ripple Error] (DCRE) | DC Bus ripple error
| 208 | [Egy Saving Exit Error] (IDLF) | Idle mode exit error
| 209 | [Load Mvt Error] (MDCF) | Load movement error
| 211 | [Security Files Corrupt] (SPFC) | Security files corrupt
| 212 | [AFE Line Filter Error] (ACF3) | AFE Line filter error
| 213 | [Cooling Pump Error] (COPF) | Cooling pump error
| 221 | [SD Error] (SDFT) | Synchro to drive error
LKON | 0 | [Warning] (ALRM) | Warning
| 1 | [Error] (FLT) | Error
| 2 | [Warning Then Error] (ALFLT) | Warning then error with time delay
MDCM | 0 | [Disabled] (NO) | Disabled
| 2 | [PTO] (WPTO) | PTO
| 3 | [Modbus] (WMDB) | Modbus RTU
MDT | 0 | [Digital] (DEC) | Digital values
| 1 | [Bar graph] (BAR) | Bar graph
| 2 | [List] (LIST) | List of values
| 3 | [Vu Meter] (VUMET) | Vu Meter
MPC | 0 | [Mot Power] (NPR) | Nominal motor power
| 1 | [Mot Cosinus] (COS) | Nominal motor cosinus Phi
MSCM | 0 | [No] (NO) | Inactive
| 1 | [MultiDrive Link] (MDL) | MultiDrive link
| 2 | [Analog] (ANA) | Analog
MSCT | 1 | [Torque Direct] (TRQD) | Direct torque control
| 2 | [Torque Reverse] (TRQR) | Reverse torque control
| 3 | [Torque Custom] (TRQC) | Custom torque control
| 4 | [Speed Direct] (SPDD) | Direct speed control
| 5 | [Speed Reverse] (SPDR) | Reverse speed control
MSDT | 0 | [Master] (MSTER) | Master
| 1 | [Slave] (SLAVE) | Slave
MSID | 1 | [Master] (MSTER) | Master
| 2 | [Slave 1] (SLV1) | Slave 1
| 3 | [Slave 2] (SLV2) | Slave 2
| 4 | [Slave 3] (SLV3) | Slave 3
| 5 | [Slave 4] (SLV4) | Slave 4
| 6 | [Slave 5] (SLV5) | Slave 5
| 7 | [Slave 6] (SLV6) | Slave 6
| 8 | [Slave 7] (SLV7) | Slave 7
| 9 | [Slave 8] (SLV8) | Slave 8
| 10 | [Slave 9] (SLV9) | Slave 9
| 11 | [Slave 10] (SLV10) | Slave 10
MSMC | 1 | [Rigid] (RIGID) | Rigid coupling
| 2 | [Elastic] (ELAST) | Elastic coupling
MSS | 0 | [None] (NONE) | Not configured
| 1 | [M/S Local Control] (NACT) | M/S local control
| 2 | [M/S Not Ready] (NRDY) | M/S not ready
| 3 | [M/S Ready] (READY) | M/S ready
| 4 | [M/S Running] (RUN) | M/S running
| 5 | [M/S Warning] (ALARM) | M/S warning
MSSS | 0 | [Not Applied] (NO) | Not applied
| 1 | [Before Ramp] (BRMP) | Before ramp
| 2 | [After Ramp] (ARMP) | After ramp
| 3 | [Before Control Loop] (BCTRL) | Before speed control loop
MSTS | 0 | [Not Applied] (NO) | Not applied
| 1 | [Before Advanced Filter] (BFILT) | Before advanced filter
| 2 | [After Advanced Filter] (AFILT) | After advanced filter
NCV | 0 | [Unknown rating] (NO) | Unknown rating
| 1 | [0.12kW] (U010) | 0.10kW - 0.2HP
| 2 | [0.18kW / 0.25Hp] (U018) | 0.18 kW / 0.25 Hp
| 3 | [0.25kW] (U025) | 0.25kW - 0.37HP
| 4 | [0.37 kW / 0.5 Hp] (U037) | 0.37 kW / 0.5 Hp
| 5 | [0.55 kW /0.75 Hp] (U055) | 0.55 kW / 0.75 Hp
| 6 | [0.75 kW / 1 Hp] (U075) | 0.75 kW / 1 Hp
| 7 | [5.5kW / 7.5HP] (U090) | 5.5kW - 7.5HP
| 8 | [1.1 kW / 1.5 Hp] (U110) | 1.1 kW / 1.5 Hp
| 9 | [1.5 kW / 2 Hp] (U150) | 1.5 kW / 2 Hp
| 10 | [1.85kW] (U185) | 1.85kW - 3HP
| 11 | [2.2 kW / 3 Hp] (U220) | 2.2 kW / 3 Hp
| 12 | [3 kW / 4HP] (U300) | 3 kW / 4HP
| 13 | [4kW / 5HP] (U370) | 3.7kW - 5HP
| 14 | [4kW / 5HP] (U400) | 4kW - 5HP
| 15 | [5.5 kW / 7.5 Hp] (U550) | 5.5 kW / 7.5 Hp
| 16 | [7.5 kW / 10 Hp] (U750) | 7.5 kW / 10 Hp
| 17 | [9kW] (U900) | 9kW - 11HP
| 18 | [11 kW / 15 Hp] (D110) | 11 kW / 15 HP
| 19 | [15 kW / 20 Hp] (D150) | 15 kW / 20 HP
| 20 | [18,5kW / 25HP] (D185) | 18.5kW - 25HP
| 21 | [22kW / 30HP] (D220) | 22kW - 30HP
| 22 | [30kW / 40HP] (D300) | 30kW - 40HP
| 23 | [37kW / 50HP] (D370) | 37kW - 50HP
| 24 | [45kW / 60HP] (D450) | 45kW - 60HP
| 25 | [55kW / 75HP] (D550) | 55kW - 75HP
| 26 | [75kW / 100HP] (D750) | 75kW - 100HP
| 27 | [90kW / 125HP] (D900) | 90kW - 125HP
| 28 | [110 kW / 150HP] (C110) | 110kW - 150HP
| 29 | [132kW / 200 HP] (C132) | 132kW - 200HP
| 30 | [160kW / 250HP] (C160) | 160kW - 250HP
| 31 | [200kW / 300HP] (C200) | 200kW - 300HP
| 32 | [220kW / 350HP] (C220) | 220kW - 350HP
| 33 | [250kW / 400HP] (C250) | 250kW - 400HP
| 34 | [280kW / 450HP] (C280) | 280kW - 450HP
| 35 | [315kW / 500HP] (C315) | 315kW - 500HP
| 36 | [355 kW / 450HP] (C355) | 355kW - 450HP
| 37 | [400kW / 600HP] (C400) | 400kW - 600HP
| 38 | [450kW / 750HP] (C450) | 450kW - 750HP
| 39 | [500kW / 800HP] (C500) | 500kW - 800HP
| 40 | [560kW / 850HP] (C560) | 560kW - 850HP
| 41 | [630kW / 900HP] (C630) | 630kW -900HP
| 42 | [710kW / 950HP] (C710) | 710kW -950HP
| 43 | [800kW / 1000HP] (C800) | 800kW - 1000HP
| 44 | [900kW / 900HP] (C900) | 900kW - 900HP
| 45 | [1000kW / 1000HP] (M100) | 1000kW - 1000HP
| 46 | [1100kW / 1100HP] (M110) | 1100kW - 1100HP
| 47 | [1200kW / 1200HP] (M120) | 1200kW - 1200HP
| 48 | [1300kW / 1300HP] (M130) | 1300kW - 1300HP
| 49 | [1400kW / 1400HP] (M140) | 1400kW - 1400HP
| 50 | [1500kW / 1500HP] (M150) | 1500kW - 1500HP
| 51 | [1600kW / 1600HP] (M160) | 1600kW - 1600HP
| 52 | [1700kW / 1700HP] (M170) | 1700kW - 1700HP
| 53 | [1800kW / 1800HP] (M180) | 1800kW - 1800HP
| 54 | [1900kW / 1900HP] (M190) | 1900kW - 1900HP
| 55 | [2000kW / 2000HP] (M200) | 2000kW - 2000HP
| 56 | [2100kW / 2100HP] (M210) | 2100kW - 2100HP
| 57 | [2200kW / 2200HP] (M220) | 2200kW - 2200HP
| 58 | [2300kW / 2300HP] (M230) | 2300kW - 2300HP
| 59 | [2400kW / 2400HP] (M240) | 2400kW - 2400HP
| 60 | [2500 kW / 3333 Hp] (M250) | 2500 kW / 3333 Hp
| 61 | [2600 kW / 3467 Hp] (M260) | 2600 kW / 3467 Hp
NFL | 0 | [No] (NO) | No
| 1 | [First] (1ST) | First
| 2 | [Second] (2ND) | Second
| 3 | [All] (ALL) | All
NMTS | 0 | [Boot] (BOOT) | On boot up
| 2 | [Stopped] (STOP) | Stopped
| 1 | [Operation] (OPE) | Operational
| 4 | [Pre-op] (POPE) | Pre operation
NPL | 0 | [High Level] (POS) | High level
| 1 | [Low Level] (NEG) | Low level
N_Y | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
OFI | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [Optimized] (OPT) | Optimized
OPL | 0 | [Function Inactive] (NO) | Function inactive
| 1 | [OPF Error Triggered] (YES) | OPF error Triggered
| 2 | [No Error Triggered] (OAC) | No error triggered
OVMA | 0 | [Default] (DEFAULT) | Default
| 255 | [Full] (FULL) | Full
PCPM | 0 | [No] (NO) | Pump cycle monitoring disabled
| 1 | [Mode 1] (NORM) | Pump cycle monitoring mode 1
| 2 | [Mode 2] (RTC) | Pump cycle monitoring mode 2
PGA | 0 | [Encoder] (ENC) | Encoder
| 1 | [Frequency Generator] (PTG) | Frequency generator
PHR | 0 | [ABC] (ABC) | A - B - C phase rotation
| 1 | [ACB] (ACB) | A - C - B phase rotation
PKTP | 0 | [Product] (PRD) | Product package
| 1 | [Module] (OPT) | Module package
| 2 | [Spare parts] (SPR) | Spare parts package
| 3 | [Customized] (CUS) | Customized package
| 4 | [Indus] (IND) | Indus package
| 5 | [None] (NONE) | No package
PNU | 0 | [Conformance Mode] (PROF) | Conformance mode
| 1 | [Manufacturer Mode] (COMP) | Manufacturer Mode
PRFL | 0 | [Not Configured] (UNCG) | Not configured
| 1 | [1] (1) | 1
| 100 | [100] (100) | 100
| 101 | [101] (101) | 101
| 102 | [102] (102) | 102
| 106 | [106] (106) | 106
| 107 | [107] (107) | 107
PSA | 0 | [Not Configured] (NO) | Not configured
| 1 | [AI1] (AI1) | AI1 Analog input
| 2 | [AI2] (AI2) | AI2 Analog input
| 3 | [AI3] (AI3) | AI3 Analog input
| 4 | [AI4] (AI4) | AI4 Analog input
| 5 | [AI5] (AI5) | AI5 Analog input
| 129 | [Motor Current] (OCR) | Motor current
| 130 | [Motor Frequency] (OFR) | Motor frequency
| 131 | [Ramp Out.] (ORP) | Ramp output
| 132 | [Motor Torq.] (TRQ) | Motor torque
| 133 | [Sign. Torque] (STQ) | Signed torque
| 134 | [sign Ramp] (ORS) | Signed ramp
| 135 | [PID Ref.] (OPS) | PID reference
| 136 | [PID Feedbk] (OPF) | PID feedback
| 137 | [PID Error] (OPE) | PID error
| 138 | [PID Output] (OPI) | PID output
| 139 | [Mot Mech Power in %] (OPR) | Motor power in %
| 140 | [Mot Thermal] (THR) | Motor thermal state
| 141 | [Drv Thermal] (THD) | Drive thermal state
| 142 | [Torque 4Q] (TR4Q) | Torque 4Q
| 143 | [Measured Motor Freq] (OFRR) | Measured motor frequency
| 145 | [Motor Freq w/o Filter] (OFR1) | Motor frequency without filter
| 160 | [Ref Frequency via DI] (UPDT) | Reference frequency via DI
| 163 | [HMI] (LCC) | Local HMI
| 164 | [Ref. Freq-Modbus] (MDB) | Reference frequency via Modbus
| 167 | [Ref. Freq-CANopen] (CAN) | Reference frequency via CANopen
| 169 | [Ref. Freq-Com. Module] (NET) | Reference frequency via Com module
| 171 | [Embedded Ethernet] (ETH) | Embedded Ethernet
| 173 | [Sig. O/P Frq.] (OFS) | Signed output frequency
| 174 | [Mot Therm2] (THR2) | Motor thermal 2 state
| 175 | [Mot Therm3] (THR3) | Motor thermal 3 state
| 176 | [Mot therm4] (THR4) | Motor thermal 4 state
| 177 | [Unsigned Trq Ref] (UTR) | Unsigned torque reference
| 178 | [Signed Trq Ref] (STR) | Signed torque reference
| 179 | [Torque Lim.] (TQL) | Torque limit
| 180 | [Motor volt.] (UOP) | Motor voltage
| 183 | [AI Virtual 1] (AIV1) | AI Virtual 1
| 184 | [DQ1] (DO1) | Digital output 1
| 188 | [DI7 PulseInput] (PI7) | DI7 pulseInput
| 189 | [DI8 PulseInput] (PI8) | DI8 pulseInput
| 190 | [DC Bus voltage] (VBUS) | DC Bus voltage
| 196 | [Copy PI8] (COPY) | Copy pulse input 8
| 182 | [Encoder] (PG) | Encoder reference
| 344 | [M/S Out Speed Reference] (MSSO) | M/S output speed reference
| 345 | [M/S Out Torque Reference] (MSTO) | M/S output torque reference
| 510 | [Mixing Valve] (MVCO) | External mixing valve
PSL | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Device in operating state "Fault"
| 2 | [Device Running] (RUN) | Device running
| 3 | [Output cont] (OCC) | Ouput contactor control
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 5 | [High Speed Reached] (FLA) | High speed reached
| 6 | [Current Thd Reached] (CTA) | Current threshold reached
| 7 | [Ref Freq Reached] (SRA) | Reference frequency reached
| 8 | [Motor Therm Thd reached] (TSA) | Motor thermal threshold reached
| 9 | [Brake Sequence] (BLC) | Brake sequence
| 10 | [PID error Warning] (PEE) | PID error warning
| 11 | [PID Feedback Warn] (PFA) | PID feedback warning
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 14 | [Dev Thermal reached] (TAD) | Device thermal threshold reached
| 16 | [Ref Freq High Thd reached] (RTAH) | Reference frequency high threshold reached
| 17 | [Ref Freq Low Thd reached] (RTAL) | Reference frequency low threshold reached
| 18 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 19 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 20 | [Low Current Reached] (CTAL) | Low current threshold reached
| 21 | [Process Undld Warn] (ULA) | Process underload warning
| 22 | [Process Overload Warning] (OLA) | Process overload warning
| 23 | [PID High Fdbck Warn] (PFAH) | PID high feedback warning
| 24 | [PID Low Fdbck Warn] (PFAL) | PID low feedback warning
| 25 | [Regulation Warning] (PISH) | Regulation warning
| 26 | [Forced Run] (ERN) | Forced Run
| 27 | [Slack Rope Warning] (RSDA) | Slack rope warning
| 28 | [High Torque Warning] (TTHA) | High torque warning
| 29 | [Low Torque Warning] (TTLA) | Low torque warning
| 30 | [Run Forward] (MFRD) | Run forward
| 31 | [Run Reverse] (MRRS) | Run reverse
| 34 | [Ramp switching] (RP2) | Ramp switching
| 37 | [Mot2 Therm Thd reached] (TS2) | Motor 2 thermal threshold reached
| 38 | [Mot3 Therm Thd reached] (TS3) | Motor 3 thermal threshold reached
| 39 | [Mot4 Therm Thd reached] (TS4) | Motor 4 thermal threshold reached
| 42 | [HMI L/R cmd] (BMP) | HMI local/remote command
| 47 | [Neg Torque] (ATS) | Negative torque
| 48 | [Cnfg.0 act.] (CNF0) | Configuration 0 active
| 49 | [Cnfg.1 act.] (CNF1) | Configuration 1 active
| 50 | [Cnfg.2 act.] (CNF2) | Configuration 2 active
| 51 | [Cnfg.3 act.] (CNF3) | Configuration 3 active
| 52 | [set 1 active] (CFP1) | Parameter set 1 active
| 53 | [set 2 active] (CFP2) | Parameter set 2 active
| 54 | [set 3 active] (CFP3) | Parameter set 3 active
| 64 | [DC charged] (DBL) | DC bus charged
| 65 | [In braking] (BRS) | In braking sequence
| 66 | [Power Removal State] (PRM) | Power Removal state
| 72 | [Pulse Warn Thd Reached] (FQLA) | Pulse warning threshold reached
| 73 | [Mains Contactor] (LLC) | Mains contactor control
| 77 | [I present] (MCP) | I present
| 78 | [Limit Switch Reached] (LSA) | Limit switch reached
| 79 | [Dynamic Load Warning] (DLDA) | Dynamic load warning
| 80 | [Warning Grp 1] (AG1) | Warning group 1
| 81 | [Warning Grp 2] (AG2) | Warning group 2
| 82 | [Warning Grp 3] (AG3) | Warning group 3
| 87 | [External Error Warning] (EFA) | External error warning
| 88 | [Undervoltage Warning] (USA) | Undervoltage warning
| 89 | [Preventive UnderV Active] (UPA) | Preventive undervoltage active
| 90 | [Slipping warn] (ANA) | Slipping warning
| 91 | [Device Therm Warn] (THA) | Device thermal state warning
| 92 | [AFE Mains Undervoltage] (URA) | AFE Mains undervoltage
| 93 | [Load Mvt Warn] (BSA) | Load movement warning
| 94 | [Brake Contact Warn] (BCA) | Brake contact warning
| 95 | [Lim T/I Reached] (SSA) | Limit torque / I reached
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 2
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 103 | [Trq ctrl Warning] (RTA) | Torque control timeout warning
| 104 | [Therm Junction Warn] (TJA) | Thermal junction warning
| 105 | [BR Thermal Warning] (BOA) | Braking resistor thermal warning
| 107 | [AI3 4-20 Warning] (AP3) | AI3 4-20 Loss warning
| 108 | [AI4 4-20 Warning] (AP4) | AI4 4-20 Loss warning
| 109 | [DC charging] (DCO) | DC charging
| 116 | [Function key 1] (FN1) | Graphic display terminal function key 1
| 117 | [Function key 2] (FN2) | Graphic display terminal function key 2
| 118 | [Function key 3] (FN3) | Graphic display terminal function key 3
| 119 | [Function key 4] (FN4) | Graphic display terminal function key 4
| 123 | [AI1 4-20 Warning] (AP1) | AI1 4-20 loss warning
| 127 | [Ready] (RDY) | Ready
| 128 | [Yes] (YES) | Yes
| 129 | [DI1] (LI1) | Digital input 1
| 130 | [DI2] (LI2) | Digital input 2
| 131 | [DI3] (LI3) | Digital input 3
| 132 | [DI4] (LI4) | Digital input 4
| 133 | [DI5] (LI5) | Digital input 5
| 134 | [DI6] (LI6) | Digital input 6
| 135 | [DI7] (LI7) | Digital input 7
| 136 | [DI8] (LI8) | Digital input 8
| 139 | [DI11] (LI11) | Digital input 11
| 140 | [DI12] (LI12) | Digital input 12
| 141 | [DI13] (LI13) | Digital input 13
| 142 | [DI14] (LI14) | Digital input 14
| 143 | [DI15] (LI15) | Digital input 15
| 144 | [DI16] (LI16) | Digital input 16
| 158 | [Time Delay Control] (TDC) | Time delay control
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 176 | [C100] (C100) | Bit 0 Modbus ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 192 | [C200] (C200) | Bit 0 CANopen ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 208 | [C300] (C300) | Bit 0 Com module ctrl word
| 209 | [C301] (C301) | Bit 1 Com module ctrl word
| 210 | [C302] (C302) | Bit 2 Com module ctrl word
| 211 | [C303] (C303) | Bit 3 Com module ctrl word
| 212 | [C304] (C304) | Bit 4 Com module ctrl word
| 213 | [C305] (C305) | Bit 5 Com module ctrl word
| 214 | [C306] (C306) | Bit 6 Com module ctrl word
| 215 | [C307] (C307) | Bit 7 Com module ctrl word
| 216 | [C308] (C308) | Bit 8 Com module ctrl word
| 217 | [C309] (C309) | Bit 9 Com module ctrl word
| 218 | [C310] (C310) | Bit 10 Com module ctrl word
| 219 | [C311] (C311) | Bit 11 Com module ctrl word
| 220 | [C312] (C312) | Bit 12 Com module ctrl word
| 221 | [C313] (C313) | Bit 13 Com module ctrl word
| 222 | [C314] (C314) | Bit 14 Com module ctrl word
| 223 | [C315] (C315) | Bit 15 Com module ctrl word
| 240 | [C500] (C500) | Bit 0 Eth embd ctrl word
| 241 | [C501] (C501) | Bit 1 Eth embd ctrl word
| 242 | [C502] (C502) | Bit 2 Eth embd ctrl word
| 243 | [C503] (C503) | Bit 3 Eth embd ctrl word
| 244 | [C504] (C504) | Bit 4 Eth embd ctrl word
| 245 | [C505] (C505) | Bit 5 Eth embd ctrl word
| 246 | [C506] (C506) | Bit 6 Eth embd ctrl word
| 247 | [C507] (C507) | Bit 7 Eth embd ctrl word
| 248 | [C508] (C508) | Bit 8 Eth embd ctrl word
| 249 | [C509] (C509) | Bit 9 Eth embd ctrl word
| 250 | [C510] (C510) | Bit 10 Eth embd ctrl word
| 251 | [C511] (C511) | Bit 11 Eth embd ctrl word
| 252 | [C512] (C512) | Bit 12 Eth embd ctrl word
| 253 | [C513] (C513) | Bit 13 Eth embd ctrl word
| 254 | [C514] (C514) | Bit 14 Eth embd ctrl word
| 255 | [C515] (C515) | Bit 15 Eth embd ctrl word
| 272 | [DI1 (Low level)] (L1L) | Digital input DI1 (low level)
| 273 | [DI2 (Low level)] (L2L) | Digital input DI2 (low level)
| 274 | [DI3 (Low level)] (L3L) | Digital input DI3 (low level)
| 275 | [DI4 (Low level)] (L4L) | Digital input DI4 (low level)
| 276 | [DI5 (Low level)] (L5L) | Digital input DI5 (low level)
| 277 | [DI6 (Low level)] (L6L) | Digital input DI6 (low level)
| 278 | [DI7 (Low level)] (L7L) | Digital input DI7 (low level)
| 279 | [DI8 (Low level)] (L8L) | Digital input DI8 (low level)
| 282 | [DI11 (Low level)] (L11L) | Digital input DI11 (low level)
| 283 | [DI12 (Low level)] (L12L) | Digital input DI12 (low level)
| 284 | [DI13 (Low level)] (L13L) | Digital input DI13 (low level)
| 285 | [DI14 (Low level)] (L14L) | Digital input DI14 (low level)
| 286 | [DI15 (Low level)] (L15L) | Digital input DI15 (low level)
| 287 | [DI16 (Low level)] (L16L) | Digital input DI16 (low level)
| 302 | [DI50 (High Level)] (D50H) | Digital input DI50 (High level)
| 303 | [DI51 (High Level)] (D51H) | Digital input DI51 (High level)
| 304 | [DI52 (High Level)] (D52H) | Digital input DI52 (High level)
| 305 | [DI53 (High Level)] (D53H) | Digital input DI53 (High level)
| 306 | [DI54 (High Level)] (D54H) | Digital input DI54 (High level)
| 307 | [DI55 (High Level)] (D55H) | Digital input DI55 (High level)
| 308 | [DI56 (High Level)] (D56H) | Digital input DI56 (High level)
| 309 | [DI57 (High Level)] (D57H) | Digital input DI57 (High level)
| 310 | [DI58 (High Level)] (D58H) | Digital input DI58 (High level)
| 311 | [DI59 (High Level)] (D59H) | Digital input DI59 (High level)
| 312 | [DI50 (Low level)] (D50L) | Digital input DI50 (low level)
| 313 | [DI51 (Low level)] (D51L) | Digital input DI51 (low level)
| 314 | [DI52 (Low level)] (D52L) | Digital input DI52 (low level)
| 315 | [DI53 (Low level)] (D53L) | Digital input DI53 (low level)
| 316 | [DI54 (Low level)] (D54L) | Digital input DI54 (low level)
| 317 | [DI55 (Low level)] (D55L) | Digital input DI55 (low level)
| 318 | [DI56 (Low level)] (D56L) | Digital input DI56 (low level)
| 319 | [DI57 (Low level)] (D57L) | Digital input DI57 (low level)
| 320 | [DI58 (Low level)] (D58L) | Digital input DI58 (low level)
| 321 | [DI59 (Low level)] (D59L) | Digital input DI59 (low level)
| 336 | [DC Bus Ripple Warn] (DCRW) | DC bus ripple warning
| 337 | [Modbus Com Inter.] (SLF1) | Modbus communication interruption warning
| 338 | [STO fct status] (STOS) | Safe torque Off function Status
| 352 | [Pump Cycle Warning] (PCPA) | Pump cycle warning
| 369 | [M/S Device Warn] (MSDA) | M/S device warning
| 384 | [Rdy Or Run State] (RYRN) | Device in ready or running state
| 385 | [Idle Or Rdy State] (IDRY) | Device in energy saving or ready state
| 386 | [Idle Rdy Or Run State] (IDRR) | Device in energy saving or ready or running state
| 387 | [Idle State] (IDLE) | Device in energy saving state
| 419 | [None] (SLRN)
| 470 | [Internal Error 22] (INFM) | Internal error 22 (Embedded Ethernet)
| 471 | [Pwr Backup Warn] (RFTA) | Power backup mode warning
| 474 | [Temp Sens AI1 Warn] (TS1A) | Temperature sensor AI1 warning
| 476 | [Temp Sens AI3 Warn] (TS3A) | Temperature sensor AI3 warning
| 477 | [Temp Sens AI4 Warn] (TS4A) | Temperature sensor AI4 warning
| 478 | [Temp Sens AI5 Warn] (TS5A) | Temperature sensor AI5 warning
| 479 | [Transfer To Mains In Progress] (TTMI) | Transfer to mains in progress
| 480 | [SM Ready To Transfer] (RTTM) | Ready to transfer to mains
| 483 | [DBR Active] (BRAS) | DBR active
| 484 | [Cust Warning 5] (CAS5) | Customer warning 5
| 485 | [AI1 Th Warning] (TP1A) | AI1 thermal sensor warning
| 486 | [Torque ref. channel] (TR1) | Torque reference channel
| 487 | [Torque ref. 2 channel] (TR2) | Torque reference channel 2
| 488 | [Cabinet Fan Command] (FCC) | Cabinet fan command
| 489 | [CB Start Pulse] (CBEP) | Circuit breaker start pulse
| 490 | [CB Stop Pulse] (CBDP) | Circuit breaker stop pulse
| 491 | [Power Cons Warning] (POWD) | Power Consumption warning
| 492 | [Warning Grp 4] (AG4) | Warning group 4
| 493 | [Warning Grp 5] (AG5) | Warning group 5
| 494 | [Fallback speed] (FRF) | Fallback speed
| 495 | [Speed Maintained] (RLS) | Speed maintained
| 496 | [Per Type of Stop] (STT) | Per type of stop
| 497 | [Life Cycle Warn 1] (LCA1) | Life cycle warning 1
| 498 | [Life Cycle Warn 2] (LCA2) | Life cycle warning 2
| 500 | [AI3 Th Warning] (TP3A) | AI3 thermal sensor warning
| 501 | [AI4 Th Warning] (TP4A) | AI4 thermal sensor warning
| 502 | [AI5 Th Warning] (TP5A) | AI5 thermal sensor warning
| 503 | [AI5 4-20 Warning] (AP5) | AI5 4-20 Loss warning
| 504 | [Fan Counter Warning] (FCTA) | Fan counter warning
| 505 | [Fan Feedback Warn] (FFDA) | Fan feedback warning
| 506 | [Power High Threshold] (PTHA) | Power high threshold
| 507 | [Power Low Threshold] (PTHL) | Power low threshold
| 508 | [Cust Warning 1] (CAS1) | Customer warning 1
| 509 | [Cust Warning 2] (CAS2) | Customer warning 2
| 510 | [Cust Warning 3] (CAS3) | Customer warning 3
| 511 | [Cust Warning 4] (CAS4) | Customer warning 4
PSLIN | 0 | [Not Assigned] (NO) | Not assigned
| 123 | [AI1 4-20 Warning] (AP1) | AI1 4-20 loss warning
| 107 | [AI3 4-20 Warning] (AP3) | AI3 4-20 Loss warning
| 108 | [AI4 4-20 Warning] (AP4) | AI4 4-20 Loss warning
| 503 | [AI5 4-20 Warning] (AP5) | AI5 4-20 Loss warning
| 1 | [Operating State Fault] (FLT) | Device in operating state "Fault"
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 486 | [Torque ref. channel] (TR1) | Torque reference channel
| 487 | [Torque ref. 2 channel] (TR2) | Torque reference channel 2
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 2
| 128 | [Yes] (YES) | Yes
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 18 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 19 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 129 | [DI1] (LI1) | Digital input 1
| 130 | [DI2] (LI2) | Digital input 2
| 131 | [DI3] (LI3) | Digital input 3
| 132 | [DI4] (LI4) | Digital input 4
| 133 | [DI5] (LI5) | Digital input 5
| 134 | [DI6] (LI6) | Digital input 6
| 135 | [DI7] (LI7) | Digital input 7
| 136 | [DI8] (LI8) | Digital input 8
| 139 | [DI11] (LI11) | Digital input 11
| 140 | [DI12] (LI12) | Digital input 12
| 141 | [DI13] (LI13) | Digital input 13
| 142 | [DI14] (LI14) | Digital input 14
| 143 | [DI15] (LI15) | Digital input 15
| 144 | [DI16] (LI16) | Digital input 16
| 272 | [DI1 (Low level)] (L1L) | Digital input DI1 (low level)
| 273 | [DI2 (Low level)] (L2L) | Digital input DI2 (low level)
| 274 | [DI3 (Low level)] (L3L) | Digital input DI3 (low level)
| 275 | [DI4 (Low level)] (L4L) | Digital input DI4 (low level)
| 276 | [DI5 (Low level)] (L5L) | Digital input DI5 (low level)
| 277 | [DI6 (Low level)] (L6L) | Digital input DI6 (low level)
| 278 | [DI7 (Low level)] (L7L) | Digital input DI7 (low level)
| 279 | [DI8 (Low level)] (L8L) | Digital input DI8 (low level)
| 282 | [DI11 (Low level)] (L11L) | Digital input DI11 (low level)
| 283 | [DI12 (Low level)] (L12L) | Digital input DI12 (low level)
| 284 | [DI13 (Low level)] (L13L) | Digital input DI13 (low level)
| 285 | [DI14 (Low level)] (L14L) | Digital input DI14 (low level)
| 286 | [DI15 (Low level)] (L15L) | Digital input DI15 (low level)
| 287 | [DI16 (Low level)] (L16L) | Digital input DI16 (low level)
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 209 | [C301] (C301) | Bit 1 Com module ctrl word
| 210 | [C302] (C302) | Bit 2 Com module ctrl word
| 211 | [C303] (C303) | Bit 3 Com module ctrl word
| 212 | [C304] (C304) | Bit 4 Com module ctrl word
| 213 | [C305] (C305) | Bit 5 Com module ctrl word
| 214 | [C306] (C306) | Bit 6 Com module ctrl word
| 215 | [C307] (C307) | Bit 7 Com module ctrl word
| 216 | [C308] (C308) | Bit 8 Com module ctrl word
| 217 | [C309] (C309) | Bit 9 Com module ctrl word
| 218 | [C310] (C310) | Bit 10 Com module ctrl word
| 219 | [C311] (C311) | Bit 11 Com module ctrl word
| 220 | [C312] (C312) | Bit 12 Com module ctrl word
| 221 | [C313] (C313) | Bit 13 Com module ctrl word
| 222 | [C314] (C314) | Bit 14 Com module ctrl word
| 223 | [C315] (C315) | Bit 15 Com module ctrl word
| 241 | [C501] (C501) | Bit 1 Eth embd ctrl word
| 242 | [C502] (C502) | Bit 2 Eth embd ctrl word
| 243 | [C503] (C503) | Bit 3 Eth embd ctrl word
| 244 | [C504] (C504) | Bit 4 Eth embd ctrl word
| 245 | [C505] (C505) | Bit 5 Eth embd ctrl word
| 246 | [C506] (C506) | Bit 6 Eth embd ctrl word
| 247 | [C507] (C507) | Bit 7 Eth embd ctrl word
| 248 | [C508] (C508) | Bit 8 Eth embd ctrl word
| 249 | [C509] (C509) | Bit 9 Eth embd ctrl word
| 250 | [C510] (C510) | Bit 10 Eth embd ctrl word
| 251 | [C511] (C511) | Bit 11 Eth embd ctrl word
| 252 | [C512] (C512) | Bit 12 Eth embd ctrl word
| 253 | [C513] (C513) | Bit 13 Eth embd ctrl word
| 254 | [C514] (C514) | Bit 14 Eth embd ctrl word
| 255 | [C515] (C515) | Bit 15 Eth embd ctrl word
| 302 | [DI50 (High Level)] (D50H) | Digital input DI50 (High level)
| 303 | [DI51 (High Level)] (D51H) | Digital input DI51 (High level)
| 304 | [DI52 (High Level)] (D52H) | Digital input DI52 (High level)
| 305 | [DI53 (High Level)] (D53H) | Digital input DI53 (High level)
| 306 | [DI54 (High Level)] (D54H) | Digital input DI54 (High level)
| 307 | [DI55 (High Level)] (D55H) | Digital input DI55 (High level)
| 308 | [DI56 (High Level)] (D56H) | Digital input DI56 (High level)
| 309 | [DI57 (High Level)] (D57H) | Digital input DI57 (High level)
| 310 | [DI58 (High Level)] (D58H) | Digital input DI58 (High level)
| 311 | [DI59 (High Level)] (D59H) | Digital input DI59 (High level)
| 312 | [DI50 (Low level)] (D50L) | Digital input DI50 (low level)
| 313 | [DI51 (Low level)] (D51L) | Digital input DI51 (low level)
| 314 | [DI52 (Low level)] (D52L) | Digital input DI52 (low level)
| 315 | [DI53 (Low level)] (D53L) | Digital input DI53 (low level)
| 316 | [DI54 (Low level)] (D54L) | Digital input DI54 (low level)
| 317 | [DI55 (Low level)] (D55L) | Digital input DI55 (low level)
| 318 | [DI56 (Low level)] (D56L) | Digital input DI56 (low level)
| 319 | [DI57 (Low level)] (D57L) | Digital input DI57 (low level)
| 320 | [DI58 (Low level)] (D58L) | Digital input DI58 (low level)
| 321 | [DI59 (Low level)] (D59L) | Digital input DI59 (low level)
PSS | 0 | [Not locked] (NACT) | Pre-settings not locked
| 1 | [Locked] (ACT) | Pre-settings locked
PSST | 0 | [No password defined] (NO) | No password defined
| 1 | [Password is unlocked] (ULK) | Password is unlocked
| 2 | [Password is locked] (LOCK) | Password is locked
PST | 0 | [Stop Key No Priority] (NO) | Stop key no priority
| 1 | [Stop Key Priority] (YES) | Stop key priority
| 2 | [Stop Key Priority All] (ALL) | Stop key priority all CMD channels
PVIS | 0 | [Active] (ACT) | Active parameters
| 1 | [All] (ALL) | All parameters
QSTD | 2 | [Fast stop then disable voltage] (FST2) | Fast stop then disable voltage
| 6 | [Fast stop then stay in quick stop state] (FST6) | Fast stop then stay in quick stop state
RDS | 0 | [Auto] (AUTO) | Auto detected
| 1 | [10M. full] (10F) | 10Mbps full duplex
| 2 | [10M. half] (10H) | 10Mbps half duplex
| 3 | [100M. full] (100F) | 100Mbps full duplex
| 4 | [100M. half] (100H) | 100Mbps half duplex
REFQ | 3 | [3 kHz] (3K) | 3 kHz
| 4 | [4 kHz] (4K) | 4 kHz
| 5 | [5 kHz] (5K) | 5 kHz
| 6 | [6 kHz] (6K) | 6 kHz
| 7 | [7 kHz] (7K) | 7 kHz
| 8 | [8 kHz] (8K) | 8 kHz
| 9 | [9 kHz] (9K) | 9 kHz
| 10 | [10 kHz] (10K) | 10 kHz
| 11 | [11 kHz] (11K) | 11 kHz
| 12 | [12 kHz] (12K) | 12 kHz
RIN | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [Absolute] (ABS) | Absolute
RPPN | 0 | [2 poles] (2P) | 2 poles
| 1 | [4 poles] (4P) | 4 poles
| 2 | [6 poles] (6P) | 6 poles
| 3 | [8 poles] (8P) | 8 poles
RPR | 0 | [No] (NO) | No
| 2 | [Reset Run Time] (RTH) | Reset run time
| 3 | [Reset Tot Run Time] (RTHI) | Reset total run time
| 4 | [Reset Power On Time] (PTH) | Reset power ON time
| 7 | [Reset Fan Counter] (FTH) | Reset fan counter
| 8 | [Reset Tot Pw On Time] (PTHI) | Reset total power ON time
| 9 | [Clear GTHI] (GTHI) | Clear GTHI
| 10 | [Clear LTHI] (LTHI) | Clear LTHI
| 11 | [Reset Start Count] (NSM) | Reset start counter
| 12 | [Reset Start Total] (NSMI) | Reset total start counter
| 13 | [Clear AFE Fan] (FBAT) | Clear AFE fan operation time
| 14 | [Clear Cabinet Fan] (FCT) | Clear cabinet fan operation time
| 30 | [Clear BRTH] (BRTH) | Clear BRTH
| 31 | [Clear BRTI] (BRTI) | Clear BRTI
| 32 | [Clear AFE Power ON Time] (BPTH) | Clear AFE power ON time
| 33 | [Clear BPTI] (BPTI) | Clear BPTI
| 34 | [Clear AFE Nb. start] (BNSA) | Clear AFE brick number of start
| 35 | [Clear BNSI] (BNSI) | Clear BNSI
| 36 | [Clear AFE Regen Time] (BGTH) | Clear AFE regen time
| 37 | [Clear BGTI] (BGTI) | Clear BGTI
| 38 | [Clear BLMI] (BLMI) | Clear BLMI
| 39 | [Clear BLGI] (BLGI) | Clear BLGI
| 40 | [Clear BUO Run Time] (RRTH) | Clear BUO run time
| 41 | [Clear RRTI] (RRTI) | Clear RRTI
| 42 | [Clear BUO Power On Time] (RPTH) | Clear BUO power ON time
| 43 | [Clear RPTI] (RPTI) | Clear RPTI
| 44 | [Clear BUO Fan Time] (FBBT) | Clear BUO fan operating time
| 64 | [Reset All (Service)] (ALL) | Reset all counters including service
RPT | 0 | [Linear] (LIN) | Linear ramp
| 1 | [S-Ramp] (S) | S-Ramp
| 2 | [U-Ramp] (U) | U-Ramp
| 3 | [Customized] (CUS) | Ramp customized
RSD | 0 | [No] (NO) | No
| 1 | [Weight Estimation] (DRI) | Weight estimation
| 2 | [Ext Weight Sensor] (PES) | External weight sensor
SCS | 0 | [No] (NO) | No
| 1 | [Config 0] (STR0) | Save configuration 0
| 2 | [Config 1] (STR1) | Save configuration 1
| 3 | [Config 2] (STR2) | Save configuration 2
| 4 | [Config 3] (STR3) | Config 3
SFDR | 0 | [Initialization] (INIT) | Initialization
| 1 | [Not Active] (IDLE) | Not active
| 2 | [Operational] (OPE) | Operational
| 4 | [Ready] (RDY) | Ready
| 5 | [IP Configuration] (IPC) | IP configuration
| 7 | [Not Configured] (UNCF) | Not configured
| 8 | [Reading Configuration] (GET) | Reading configuration
| 9 | [Writing Configuration] (SET) | Writing configuration
| 10 | [Applying Configuration] (APP) | Applying configuration
SFT | 1 | [SFR type 1] (HF1) | Switch.frequency type 1
| 2 | [SFR type 2] (HF2) | Switch.frequency type 2
SLCA | 0 | [Not Configured] (NO) | Not configured
| 1 | [Speed Control] (SPD) | Speed control
SLPM | 0 | [No] (NO) | No
| 1 | [Switch] (SW) | Switch
| 3 | [Speed] (SPD) | Speed
| 4 | [Power] (PWR) | Power
| 6 | [Multiple] (OR) | Multiple
SMLE | 0 | [No Error] (NO) | No error
| 1 | [Internal Com Error 2] (CRCC) | Internal communication error 2
| 2 | [Internal Com Error 1] (CRCA) | Internal communication error 1
| 3 | [Internal Com Error 3] (WTB) | Internal communication error 3
| 4 | [Conf Download Error1] (DSEQ) | Configuration download error 1
| 5 | [Conf Download Error2] (VSEQ) | Configuration download error 2
| 6 | [Internal Com Error 4] (TUNN) | Internal communication error 4
| 7 | [Cfg Readback Error] (RBAK) | Configuration readback error
| 17 | [Conf Download Error3] (DCNF) | Configuration download error 3
| 18 | [Partial Conf Transfer 2] (NSCF) | Partial configuration transferred 2
| 19 | [Pairing Error 2] (WSCF) | Pairing error 2
| 20 | [Partial Conf Transfer 1] (NOCF) | Partial configuration transferred 1
| 21 | [Pairing Error 1] (WCF) | Pairing error 1
| 22 | [Internal Conf Error] (PCNF) | Internal configuration error
| 23 | [Invalid Motor Conf] (WCCF) | Invalid motor configuration
SMOT | 0 | [No info.] (NO) | No information
| 1 | [Low salient] (LLS) | Low saliency
| 2 | [Med salient] (MLS) | Medium saliency
| 3 | [High salient] (HLS) | High saliency
SOP | 6 | [6 µs] (6) | 6 µs
| 8 | [8 µs] (8) | 8 µs
| 10 | [10 µs] (10) | 10 µs
SRT | 0 | [Motor Speed] (NO) | Motor speed
| 1 | [Reference Speed] (YES) | Reference speed
SSCD | 0 | [Undefined] (UND) | Undefined
| 1 | [Binary code] (BIN) | Binary code
| 2 | [Gray code] (GRAY) | Gray code
SSCP | 0 | [Undefined] (UND) | Undefined
| 1 | [No parity] (NO) | No parity
| 3 | [Even parity] (EVEN) | Even parity
SSL | 0 | [Standard] (STD) | Standard
| 1 | [High Perf] (HPF) | High performance
SSTA | 0 | [Starting] (STRT) | Starting
| 1 | [Not Rdy To Switch On] (NRSO) | Not ready to switch On
| 2 | [Switch On Disabled] (SOD) | Switch On disabled
| 3 | [Ready To Switch On] (RTSO) | Ready to switch On
| 5 | [Operation Enabled] (OPEN) | Operation Enabled
| 7 | [Fault Reaction Active] (FRAC) | Fault reaction active
| 8 | [Fault] (FLT) | Fault
| 10 | [SS1 Active] (SS1) | SS1 active
| 11 | [STO Active] (STO) | STO active
STAC | 0 | [Not Supported] (UNSP) | Not supported
| 1 | [Enabled] (EN) | Enabled
| 2 | [Disabled] (DIS) | Disabled
STOS | 0 | [Not active] (IDLE) | Not active
| 1 | [Active] (STO) | Active
| 2 | [Error] (FLT) | Error
STP | 0 | [Inactive] (NO) | Inactive
| 1 | [Maintain DC Bus] (MMS) | Maintain DC Bus
| 2 | [Ramp Stop] (RMP) | Ramp Stop
| 4 | [Freewheel Stop] (LNF) | Locked in freewheel stop without error
| 5 | [None] (ABM)
STR | 0 | [No Save] (NO) | No save
| 1 | [Save to RAM] (RAM) | Save to RAM
| 2 | [Save to EEPROM] (EEP) | Save to EEPROM
STS | 0 | [Not Supported] (UNSP) | Not supported
| 1 | [Active] (RUN) | Active
| 2 | [Not Active] (STP) | Not active
| 3 | [Error] (ERR) | Error
STT | 0 | [On Ramp] (RMP) | On ramp
| 1 | [Fast stop] (FST) | Fast stop
| 2 | [Freewheel Stop] (NST) | Freewheel stop
| 3 | [DC injection] (DCI) | DC injection
STUN | 0 | [Default] (TAB) | Default
| 1 | [Measure] (MEAS) | Measure
| 2 | [Custom] (CUS) | Custom
STV | 0 | [Not Supported] (UNSP) | Not supported
| 1 | [Pending] (PEND) | Pending
| 2 | [Error] (ERR) | Error
| 3 | [Done] (DONE) | Done
SUCU | 0 | [Euro] (EURO) | Euro
| 1 | [$] (DOLLAR) | $
| 2 | [£] (POUND) | £
| 3 | [Krone] (KR) | Krone
| 4 | [Renminbi] (RMB) | Renminbi
| 5 | [Other] (OTHER) | Other
SUTP | 0 | [0.1°C] (01C) | 0.1°C
| 1 | [0.1°F] (01F) | 0.1°F
SYTM | 0 | [Inactive] (NOSM) | Function inactive
| 1 | [SM in SoftStart] (SMSS) | Synchro to mains in SoftStart
TBR | 4 | [Automatic] (AUTO) | Automatic
| 8 | [300 bps] (300) | 300 bps
| 12 | [600 bps] (600) | 600 bps
| 16 | [1.2 Kbps] (1200) | 1.2 Kbps
| 20 | [2.4 Kbps] (2400) | 2.4 Kbps
| 24 | [4800 bps] (4800) | 4800 bps
| 28 | [9600 bps] (9600) | 9600 bps
| 30 | [10 Kbps] (10000) | 10 Kbps
| 32 | [19200 bps] (19200) | 19200 bps
| 34 | [20 Kbps] (20000) | 20 Kbps
| 35 | [28.8 Kbps] (28800) | 28.8 Kbps
| 36 | [38.4 Kbps] (38400) | 38.4 Kbps
| 37 | [45.45 Kbps] (45450) | 45.45 Kbps
| 38 | [50 Kbps] (50000) | 50 Kbps
| 40 | [57.6 Kbps] (57600) | 57.6 Kbps
| 41 | [76.8 Kbps] (76800) | 76.8 Kbps
| 42 | [93.75 Kbps] (93750) | 93.75 Kbps
| 44 | [100 Kbps] (100K) | 100 Kbps
| 48 | [115.2 Kbps] (115K2) | 115.2 Kbps
| 52 | [125 Kbps] (125K) | 125 Kbps
| 53 | [156 Kbps] (156K) | 156 Kbps
| 54 | [187.5 Kbps] (187K5) | 187.5 Kbps
| 56 | [230.4 Kbps] (230K4) | 230.4 Kbps
| 60 | [250 Kbps] (250K) | 250 Kbps
| 64 | [460.8 Kbps] (460K8) | 460.8 Kbps
| 68 | [500 Kbps] (500K) | 500 Kbps
| 69 | [625 Kbps] (625K) | 625 Kbps
| 70 | [800 Kbps] (800K) | 800 Kbps
| 72 | [921.6 Kbps] (921K6) | 921.6 Kbps
| 76 | [1 Mbps] (1M) | 1 Mbps
| 80 | [1.5 Mbps] (1M5) | 1.5 Mbps
| 81 | [2.5 Mbps] (2M5) | 2.5 Mbps
| 82 | [3 Mbps] (3M) | 3 Mbps
| 83 | [6 Mbps] (6M) | 6 Mbps
| 84 | [10 Mbps] (10M) | 10 Mbps
| 86 | [5 Mbps] (5M) | 5 Mbps
| 88 | [12 Mbps] (12M) | 12 Mbps
| 92 | [100 Mbps] (100M) | 100 Mbps
TCC | 0 | [2-Wire Control] (2C) | 2-wire control
| 1 | [3-Wire Control] (3C) | 3-wire control
TCT | 0 | [Level] (LEL) | Level
| 1 | [Transition] (TRN) | Transition
| 2 | [Level With Fwd Priority] (PFO) | Level with forward priority
THET | 0 | [None] (NONE) | None
| 1 | [PTC] (PTC) | PTC
| 2 | [PT100] (1PT2) | PT100
| 3 | [PT1000] (1PT3) | PT1000
| 4 | [KTY] (KTY) | KTY
| 5 | [Klixon] (KLIX) | Klixon
THT | 0 | [No] (NO) | No thermal monitoring
| 1 | [Self cooled] (ACL) | Self cooled motor
| 2 | [Force-cool] (FCL) | Force cooled motor
TLOL | 0 | [Disabled] (DIS) | Disabled
| 1 | [Error Triggered] (TRIP) | Error triggered
| 2 | [Reduce to I Nom Drive] (LIM) | Reduce to drive nominal current
TOB | 0 | [Warning] (ALRM) | warning
| 1 | [Error] (FLT) | Error
TOCT | 0 | [Not Available] (NA) | Not available
| 3 | [OTHER] (OTHER) | OTHER
TQNC | 0 | [Expert] (OPTI) | Expert
| 1 | [Nameplate] (NAMP) | Nameplate
TRES | 0 | [0.3] (03) | 0.3
| 1 | [0.5] (05) | 0.5
| 2 | [0.8] (08) | 0.8
| 3 | [1.0] (10) | 1.0
TST | 0 | [Speed] (SPD) | Speed
| 1 | [Freewheel] (NST) | Freewheel stop
| 2 | [Spin] (SPN) | Spin
TUNT | 2 | [Standard] (STD) | Standard
| 3 | [Rotation] (ROT) | Rotation
TUNU | 0 | [No] (NO) | No
| 1 | [Therm mot] (TM) | Use the motor thermal evolution
TWO | 0 | [OFF] (LOW) | ModBus Word Order OFF
| 1 | [ON] (HIGH) | Modbus Word Order ON
UECP | 0 | [Undefined] (UND) | Undefined
| 2 | [Hiperface] (SCHP) | SinCos Hiperface
| 3 | [SinCos] (SC) | SinCos
| 4 | [SSI] (SSI) | SSI
| 8 | [AB] (AB) | AB
| 9 | [Resolver] (RES) | Resolver
| 10 | [BiSS] (BISS) | BiSS
| 11 | [EnDat 2.2] (EN22) | EnDat 2.2
| 12 | [HTL] (HTL) | HTL encoder
UECV | 0 | [Undefined] (UND) | Undefined
| 5 | [5 Vdc] (5V) | 5 Vdc
| 12 | [12 Vdc] (12V) | 12 Vdc
| 15 | [15 Vdc] (15V) | 15 Vdc
| 24 | [24 Vdc] (24V) | 24 Vdc
ULR | 0 | [Permitted] (ULR0) | Upload access allowed
| 1 | [Not allowed] (ULR1) | Upload access not allow
URES | 20 | [200 Vac] (200) | 200 Vac
| 22 | [220 Vac] (220) | 220 Vac
| 23 | [230 Vac] (230) | 230 Vac
| 24 | [240 Vac] (240) | 240 Vac
| 38 | [380 Vac] (380) | 380 Vac
| 40 | [400 Vac] (400) | 400 Vac
| 44 | [440 Vac] (440) | 440 Vac
| 46 | [460 Vac] (460) | 460 Vac
| 48 | [480 Vac] (480) | 480 Vac
| 50 | [500Vac] (500) | 500Vac
| 52 | [525 Vac] (525) | 525 Vac
| 57 | [575 Vac] (575) | 575 Vac
| 60 | [600 Vac] (600) | 600 Vac
| 69 | [690 Vac] (690) | 690 Vac
USB | 0 | [Error Triggered] (0) | Error triggered
| 1 | [Error Triggered w/o Relay] (1) | Error triggered w/o relay
| 2 | [Warning Triggered] (2) | Warning Triggered
VCAL | 0 | [Unknown Voltage] (NO) | Unkown voltage
| 1 | [100-120(1)] (110M) | 100-120 V single phase
| 2 | [100-120(3)] (110T) | 100-120 V three phase
| 3 | [200-240 V single] (220M) | 200-240 V single
| 4 | [200-240 V Three] (220T) | 200-240 V three phase
| 5 | [380-500(1)] (480M) | 380-500 V single phase
| 6 | [380-500 V Three] (480T) | 380-500 V three phase
| 7 | [500-690(1)] (690M) | 500-690 V single phase
| 8 | [500-690 V Three] (690T) | 500-690 V three phase
| 9 | [600(1)] (600M) | 600 V single phase
| 10 | [600 V Three] (600T) | 600 V three phase
WUPM | 0 | [Feedback] (FBK) | Feedback
| 1 | [Error] (ERR) | Error

## Registers
CMI |  | Bit 0 | Factory setting command (active at 1).
|  | Bit 1 | Save configuration to EEPROM non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | Bit 2 | Reserved (= 0).
|  | Bit 3 | Reserved (= 0).
|  | Bit 4 | Reserved (= 0).
|  | Bit 5 | Reserved (= 0).
|  | Bit 6 | Reserved (= 0).
|  | Bit 7 | Reserved (= 0).
|  | Bit 8 | Reserved (= 0).
|  | Bit 9 | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
= 0: 0.1 Hz
= 1: Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz.
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | Bit 10 | Reserved (= 0).
|  | Bit 11 | Reserved (= 0).
|  | Bit 12 | Reserved (= 0).
|  | Bit 13 | Reserved (= 0).
|  | Bit 14 | Reserved (= 0).
|  | Bit 15 | Parameter consistency check
= 0: The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr).
= 1: The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
CMD | Possible values in CiA402 profile, separate or not separate mode:
CMP0 |  | Bit 0 | Switch on/Contactor command.
CMP1 |  | Bit 1 | Disable voltage/Authorization to supply AC power.
CMP2 |  | Bit 2 | Quick stop.
CMP3 |  | Bit 3 | Enable operation/Run command.
CMP4 |  | Bit 4 | Reserved (set to 0).
CMP5 |  | Bit 5 | Reserved (set to 0).
CMP6 |  | Bit 6 | Reserved (set to 0).
CMP7 |  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
CMP8 |  | Bit 8 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
CMP9 |  | Bit 9 | Reserved (set to 0).
CMPA |  | Bit 10 | Reserved (set to 0).
CMPB |  | Bit 11 to 15 | Can be assigned to commands.
CMPC | Possible values in the IO profile on state command [2 wire] (2C).
CMPD |  | Bit 0 | Forward (on state) command
CMPE |  |  | = 0: No forward command
CMPF |  |  | = 1: Forward command
The assignment of Bit 0 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bit 0 (Cd00) is only active if the channel of this control word is active.
|  | Bit 1 to 15 | Can be assigned to commands.
Possible values in the IO profile on edge command [3 wire] (3C).
|  | Bit 0 | Stop (run authorization).
= 0: Stop
= 1: Run is authorized on a forward or reverse command
|  | Bit 1 | Forward (on 0 to 1 rising edge) command.
The assignment of Bits 0 and 1 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bits 0 (Cd00) and 1 (Cd01) are only active if the channel of this control word is active.
|  | Bit 2 to 15 | can be assigned to commands.
ETA | Possible values in CiA402 profile, separate or not separate mode:
EP0 |  | Bit 0 | = 1: "Ready to switch on", awaiting power section line supply
EP1 |  | Bit 1 | = 1: "Switched on", ready
EP2 |  | Bit 2 | = 1: "Operation enabled", running
EP3 |  | Bit 3 | = 1: Fault detection
EP4 |  | Bit 4 | "Voltage enabled", power part connected to supply mains
EP5 |  |  | = 0: Power part not connected to supply mains
EP6 |  |  | = 1: Power part connected to supply mains
EP7 |  |  | When the drive is powered by the power section only, this bit is always at 1.
EP8 |  | Bit 5 | Bit 5: = 0: Quick stop
EP9 |  | Bit 6 | Bit 6: = 1: "Switched on disabled", power section line supply locked
EPA |  | Bit 7 | Bit 7: Warning
EPB |  |  | = 0: No warning
EPC |  |  | = 1: Warning active
EPD |  | Bit 8 | Bit 8: Reserved (= 0)
EPE |  | Bit 9 | Bit 9: Remote: command or reference via fieldbus
EPF |  |  | = 0: Command or reference given via the graphic display terminal or remote display terminal
ETAD |  |  | = 1: Command or reference via fieldbus
|  | Bit 10 | Bit 10: Target reference reached
= 0: The reference is not reached
= 1: The reference has been reached
When the drive is in speed mode, this is the reference frequency.
|  | Bit 11 | Bit 11: "Internal limit active", reference outside limits
= 0: The reference is within the limits
= 1: The reference is not within the limits
When the drive is in speed mode, the limits are defined by the [Low speed] (LSP) and [High speed] (HSP) parameters.
|  | Bit 12 | Bit 12: Reserved (= 0)
|  | Bit 13 | Bit 13: Reserved (= 0)
|  | Bit 14 | Bit 14: "Stop key", STOP via stop key
= 0: STOP key not active
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15 | Bit 15: "Direction", direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (refer to fieldbus manuals).
ETI |  | Bit 0 | = 1: Access to the EEPROM non-volatile memory in progress
IP0 |  | Bit 1 | = 0: No parameter consistency check
IP1 |  |  | = 1: Parameter consistency check
IP2 |  | Bit 2 | = 0: The drive is not in operating state "Fault" or in operating state "Fault" and the error is active
IP3 |  |  | = 1: The drive is in operating state "Fault" and the error is no longer active (not reset))
IP4 |  | Bit 3 | Bit 3: Reserved (= 0).
IP5 |  | Bit 4 | = 1: The drive is in speed mode
IP6 |  | Bit 5 | = 1: DC injection active
IP7 |  | Bit 6 | = 0: Drive in steady state
IP8 |  |  | = 1: Drive in transient state
IP9 |  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
IPA |  | Bit 8 | = 1: DC bus overvoltage
IPB |  | Bit 9 | = 1: Acceleration active
IPC |  | Bit 10 | = 1: Deceleration active
IPD |  | Bit 11 | = 1: Current limit active
IPE |  | Bit 12 | = 1: Fast stop active
IPF |  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: Drive controled by terminal
bit 13 = 1 and bit 14 = 0: Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1: Drive controled by Modbus
bit 13 = 1 and bit 14 = 1: Drive controled by CANopen or the network card
|  | Bit 15 | = 0: Forward operation applied before the ramp
= 1: Reverse operation applied before the ramp
CRC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | Reserved
|  | Bit 11 | = 1 : Embedded Ethernet
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
CCC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | Reserved
|  | Bit 11 | = 1 : Embedded Ethernet
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
IL1R |  | Bit 0 | "LI1" logic inputs real image
|  | Bit 1 | "LI2" logic inputs real image
|  | Bit 2 | "LI3" logic inputs real image
|  | Bit 3 | "LI4" logic inputs real image
|  | Bit 4 | "LI5" logic inputs real image
|  | Bit 5 | "LI6" logic inputs real image
|  | Bit 6 | "LI7" logic inputs real image
|  | Bit 7 | "LI8" logic inputs real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs real image
|  | Bit 11 | "LI12" logic inputs real image
|  | Bit 12 | "LI13" logic inputs real image
|  | Bit 13 | "LI14" logic inputs real image
|  | Bit 14 | "LI15" logic inputs real image
|  | Bit 15 | "LI16" logic inputs real image
OL1R |  | Bit 0 | "R1" relay real image
|  | Bit 1 | "R2" relay real image
|  | Bit 2 | "R3" relay real image
|  | Bit 3 | "R4" relay real image
|  | Bit 4 | "R5" relay real image
|  | Bit 5 | "R6" relay real image
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | "DO1" logic outputs real image
|  | Bit 9 | "DO2" logic outputs real image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | "DO11" logic outputs real image
|  | Bit 13 | "DO12" logic outputs real image
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CIC |  | Bit 0 | = 1: Change of rating.
|  | Bit 1 | = 1: The fielbus module has been added.
|  | Bit 2 | = 1: The fielbus module has been removed.
|  | Bit 3 | = 1: Loaded config invalid.
|  | Bit 4 | = 1: The fielbus module has been changed.
|  | Bit 5 | Reserved (=0).
|  | Bit 6 | Reserved (=0).
|  | Bit 7 | Reserved (=0).
|  | Bit 8 | = 1: The IO module has been added.
|  | Bit 9 | = 1: The IO module has been removed.
|  | Bit 10 | = 1: The IO module has been changed.
|  | Bit 11 | = 1: The encoder module has been added.
|  | Bit 12 | = 1: The encoder module has been removed.
|  | Bit 13 | = 1: The encoder module has been changed.
|  | Bit 14 | = 1: The control board has been changed.
If one of these events occurs, the drive will trigger an error [Invalid configiguration] (CFI) and then automatically restore the factory settings.
CRP0 | Bit 0 to Bit 7: Active command channels
CRP1 |  |  | =0 : The terminal board is the active channel.
CRP2 |  |  | =1 : The local keypad is the active channel.
CRP3 |  |  | =2 : The remote keypad is the active channel.
CRP4 |  |  | =3 : Modbus is the active channel.
CRP5 |  |  | =4 : Reserved
CRP6 |  |  | =5 : Reserved
CRP7 |  |  | =6 : CANopen is the active channel.
CRP8 |  |  | =7 : The terminals are the active channel in the +/- speed reference.
CRP9 |  |  | =8 : The remote keypad is the active channel (up-down speed)
CRPA |  |  | =9 : The fieldbus module is the active channel.
CRPB |  |  | =10 : Reserved
CRPC |  |  | =11 : Reserved
CRPD |  |  | =12 : Reserved
CRPE |  |  | =13 : Reserved
CRPF |  |  | =14 : Reserved
=15 : SoMove software is the active channel.
Bit 8 to Bit 15: Active reference channels
=0 : The terminals are the active channel via an analog input.
=1 : The local keypad is the active channel.
=2 : The remote keypad is the active channel.
=3 : Modbus is the active channel.
=4 : Reserved
=5 : Reserved
=6 : CANopen is the active channel.
=7 : The terminals are the active channel in the +/- speed reference.
=8 : The remote keypad is the active channel (up-down speed)
=9 : The fieldbus module is the active channel.
=10 : Reserved
=11 : Reserved
=12 : Reserved
=13 : Reserved
=14 : Reserved
=15 : SoMove software is the active channel.
FRY |  | Bit 0 | = 1 : All parameters
|  | Bit 1 | = 1 : Drive configuration
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : Motor parameters
|  | Bit 4 | = 1 : Communication menu
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Display menu
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | = 1 : Communication option parameters
IL1I |  | Bit 0 | "LI1" logic inputs physical image
|  | Bit 1 | "LI2" logic inputs physical image
|  | Bit 2 | "LI3" logic inputs physical image
|  | Bit 3 | "LI4" logic inputs physical image
|  | Bit 4 | "LI5" logic inputs physical image
|  | Bit 5 | "LI6" logic inputs physical image
|  | Bit 6 | "LI7" logic inputs physical image
|  | Bit 7 | "LI8" logic inputs physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs physical image
|  | Bit 11 | "LI12" logic inputs physical image
|  | Bit 12 | "LI13" logic inputs physical image
|  | Bit 13 | "LI14" logic inputs physical image
|  | Bit 14 | "LI15" logic inputs physical image
|  | Bit 15 | "LI16" logic inputs physical image
PEV1 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV2 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV3 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV4 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST00 |  | Bit 4 | (SLM) : Stop asked by a "sleeping" function
|  | Bit 8 | (SLPP) : Sleep is pending
|  | Bit 9 | (SLPB) : Sleep Boost phase is running
|  | Bit 10 | (SLP) : Application Sleeping
ST01 |  | Bit 3 | (INFM) : INFM Warning
|  | Bit 4 | (SLF1) : Modbus local serial communication alarm
ST02 |  | Bit 0 | (CNF0) : Configuration 1 is used
|  | Bit 1 | (CNF1) : Configuration 2 is used
|  | Bit 2 | (CNF2) : Configuration 3 is used
|  | Bit 3 | (CNF3) : Configuration 4 is used
|  | Bit 8 | (CFP1) : Parameter set 1 is used
|  | Bit 9 | (CFP2) : Parameter set 2 is used
|  | Bit 10 | (CFP3) : Parameter set 3 is used
ST03 |  | Bit 0 | (FLO) : Drive in forced local mode
|  | Bit 1 | (FR2) : Reference channel is channel 2
|  | Bit 2 | (FR1B) : Reference channel is channel 1, and FR1B is used
|  | Bit 3 | (FR1) : Reference channel is channel 1 (FR1 or FR1B is used)
|  | Bit 4 | (CD1) : Command channel is channel 1
|  | Bit 5 | (CD2) : Command channel is channel 2
|  | Bit 6 | (RFC) : Reference channel : 0-> channel1, 1-> channel 2
|  | Bit 7 | (RCB) : 0: FR1, FR1B ?
|  | Bit 8 | (CCS) : Command channel : 0-> channel 1, 1-> channel 2
|  | Bit 9 | (BMP) : Bump Less Channel
|  | Bit 10 | (RTTM) : Synchronization to main status Affesctation on Relay
|  | Bit 11 | (TTMI) : Transfer to main in progress
|  | Bit 14 | (AFFL) : Automatic Channel Fallback Active
ST04 |  | Bit 0 | (FLT) : Drive is in fault state
|  | Bit 1 | (AUTO) : Automatic restart attempts in progress
|  | Bit 2 | (RDY) : Drive is in ready state
|  | Bit 3 | (RUN) : A gating order is set (there is potentially current in the motor)
|  | Bit 4 | (DBL) : Powerstage is supply (DC bus charged)
|  | Bit 5 | (CTL) : Controlled stop on power loss in progress
|  | Bit 6 | (STO) : STO function activated
|  | Bit 7 | (FST) : A fast stop request is on going
|  | Bit 8 | (FRF) : Reaction on event / fallback speed
|  | Bit 9 | (RLS) : Reaction on event / maintain speed
|  | Bit 10 | (STT) : Reaction on event / Stop on STT without tripping in fault
|  | Bit 11 | (IDLE) : Stop and Go idle state (FF343)
|  | Bit 12 | (ICC) : Drive is locked when encoder configuration is not complete
ST05 |  | Bit 0 | (LLC) : The drive asks to close the line contactor
|  | Bit 1 | (OCC) : The drive asks to close the output contactor (Controlled downstream contactor)
|  | Bit 2 | (SOC) : The drive has detected that the output contactor is open (Uncontrolled downstream contactor)
|  | Bit 3 | (BLC) : The drive asks to close the brake
|  | Bit 4 | (BRS) : The braking resitor is used
|  | Bit 5 | (DCO) : DC Bus charge option state (FF153)
|  | Bit 6 | (CBEP) : The drive asks to close the circuit breaker
|  | Bit 7 | (CBDP) : The drive asks to open the circuit breaker
|  | Bit 8 | (BSA) : Brake speed alarm
|  | Bit 9 | (BCA) : Brake contact alarm
|  | Bit 10 | (BSC) : Back Spin Control is active
|  | Bit 11 | (DCRW) : DC Bus Ripple Warning
|  | Bit 12 | (RFTA) : Rescue Function Alarm
ST06 |  | Bit 0 | (ACC) : Drive in acceleration
|  | Bit 1 | (DEC) : Drive in deceleration
|  | Bit 2 | (SRA) : Frequency reference reached
|  | Bit 3 | (MFRD) : Motor running in Forward
|  | Bit 4 | (MRRS) : Motor running in Reverse
|  | Bit 5 | (ATS) : Torque on the motor is negative
|  | Bit 6 | (IDC) : DC injection is running (automatic or by order)
|  | Bit 7 | (FLU) : Motor fluxing in progress
|  | Bit 8 | (FLX) : Motor fluxed
|  | Bit 9 | (TUN) : Autotune in progress
|  | Bit 10 | (MCP) : Motor current present
|  | Bit 11 | (RP2) : Ramp switching state : 0-> ramp 1, 1-> ramp 2
|  | Bit 12 | (CL2) : Current switching state : 0-> current limit 1, 1-> current limit 2
|  | Bit 13 | (TL2) : Torque switching state : 0-> Torque limit 1, 1-> Torque limit 2
ST07 |  | Bit 0 | (AG1) : One of the alarm of alarm group 1 is active
|  | Bit 1 | (AG2) : One of the alarm of alarm group 2 is active
|  | Bit 2 | (AG3) : One of the alarm of alarm group 3 is active
|  | Bit 3 | (AG4) : One of the alarm of alarm group 4 is active
|  | Bit 4 | (AG5) : One of the alarm of alarm group 5 is active
|  | Bit 8 | (LCA1) : Life Cycle Alarm 1 alarm
|  | Bit 9 | (LCA2) : Life Cycle Alarm 2 alarm
ST08 |  | Bit 6 | (PCPA) : Cyclic Start Protection Alarm
ST09 |  | Bit 0 | (PFA) : alarm on PID Feedback
|  | Bit 1 | (PFAH) : PID feedback high threshold reached
|  | Bit 2 | (PFAL) : PID feedback low threshold reached
|  | Bit 3 | (PISH) : PI feedback monitoring alarm is raised
|  | Bit 11 | (PEE) : alarm on PID error
ST10 |  | Bit 0 | (LSA) : A limit switch has been reached
|  | Bit 1 | (RSDA) : Rope slack detection
|  | Bit 2 | (DLDA) : High Speed Hoisiting, dynamic load detection
ST11 |  | Bit 1 | (TP3A) : Temperature Protection AI3 Alarm
|  | Bit 2 | (TP4A) : Temperature Protection AI4 Alarm
|  | Bit 3 | (TP5A) : Temperature Protection AI5 Alarm
|  | Bit 4 | (TP1A) : Temperature Protection AI1 Alarm
|  | Bit 7 | (TPEA) : Temperature Protection Encoder board Alarm
|  | Bit 8 | (TS1A) : Temperature Sensor AI1 Alarm
|  | Bit 10 | (TS3A) : Temperature Sensor AI3 Alarm
|  | Bit 11 | (TS4A) : Temperature Sensor AI4 Alarm
|  | Bit 12 | (TS5A) : Temperature Sensor AI5 Alarm
ST12 |  | Bit 0 | (AP1) : 4-20 loss alarm on AI1
|  | Bit 2 | (AP3) : 4-20 loss alarm on AI3
|  | Bit 3 | (AP4) : 4-20 loss alarm on AI4
|  | Bit 4 | (AP5) : 4-20 loss alarm on AI5
ST13 |  | Bit 0 | (THA) : drive overheating alarm is raised
|  | Bit 1 | (TJA) : alarm on IGBT thermal state
|  | Bit 2 | (FCTA) : Fan Counter Speed alarm
|  | Bit 3 | (FFDA) : Fan feedback alarm is raised
|  | Bit 4 | (BOA) : Braking resistor overload alarm is raised (FF156)
|  | Bit 5 | (EFA) : external alarm is raised
|  | Bit 6 | (USA) : undervoltage alarm is raised
|  | Bit 7 | (UPA) : controlled stop on power loss threshold id reached
|  | Bit 8 | (OBR) : Impossible to follow the customer ramp during deceleration
|  | Bit 9 | (URA) : Intelligent Rectifier alarm is raised
|  | Bit 10 | (ERN) : Emergency
ST14 |  | Bit 0 | (FTA) : Motor frequency high threshold 1 reached
|  | Bit 1 | (FTAL) : Motor frequency low threshold 1 reached
|  | Bit 2 | (FQLA) : Frequency level reached (frequency meter)
|  | Bit 3 | (F2AL) : Motor frequency low threshold 2 reached
|  | Bit 4 | (FLA) : HighSpeedReached function result
|  | Bit 5 | (RTAH) : Reference frequency high threshold reached
|  | Bit 6 | (RTAL) : Reference frequency low threshold reached
|  | Bit 7 | (F2A) : Motor frequency high threshold 2 reached
ST15 |  | Bit 0 | (CTA) : Motor current high threshold reached
|  | Bit 1 | (CTAL) : Motor current low threshold reached
|  | Bit 2 | (TTHA) : Motor torque high threshold reached
|  | Bit 3 | (TTLA) : Motor torque low threshold reached
|  | Bit 4 | (ULA) : Underload is detected
|  | Bit 5 | (OLA) : Overload is detected
|  | Bit 6 | (CLI) : current or torque limitation is running
|  | Bit 7 | (SSA) : Timeout on current or torque limitation is reached
|  | Bit 8 | (RTA) : Torque regulation alarm
|  | Bit 9 | (POWD) : Electrical Power Drift alarm
|  | Bit 10 | (PTHA) : Power high threshold reached
|  | Bit 11 | (PTHL) : Power Low threshold reached
|  | Bit 12 | (ANA) : Anti-veering alarm
ST16 |  | Bit 1 | (TAD) : DriveThermalThresholdReached function result
|  | Bit 2 | (TSA) : MotorThermalThresholdReached function result (motor 1)
|  | Bit 3 | (TS2) : MotorThermalThresholdReached function result (motor 2)
|  | Bit 4 | (TS3) : MotorThermalThresholdReached function result (motor 3)
|  | Bit 5 | (TS4) : MotorThermalThresholdReached function result (motor 4)
ST17 |  | Bit 0 | (CAS1) : Customer Alarm 1 active
|  | Bit 1 | (CAS2) : Customer Alarm 2 active
|  | Bit 2 | (CAS3) : Customer Alarm 3 active
|  | Bit 3 | (CAS4) : Customer Alarm 4 active
|  | Bit 4 | (CAS5) : Customer Alarm 5 active
ST18 |  | Bit 0 | (FCBA) : AFE : Fan running time
|  | Bit 1 | (FFBA) : AFE : Fan frequency
|  | Bit 2 | (CLIM) : AFE : Current or power limitation is running in motor mode
|  | Bit 3 | (CLIG) : AFE : Current or power limitation is running in generator mode
|  | Bit 4 | (THSA) : AFE : Sensor thermal state
|  | Bit 5 | (THJA) : AFE : IGBT thermal state
|  | Bit 6 | (FFCA) : MCE : Cabinet fan alarm state
|  | Bit 7 | (FCCA) : MCE : Cabinet fan alarm running time
|  | Bit 8 | (CHA) : MCE : Cabinet over-heating alarm
|  | Bit 9 | (CMIJ) : MCE : CMI jumper is closed
|  | Bit 10 | (FCBB) : BU: Fan Running Time
|  | Bit 11 | (FFBB) : BU: Fan Frequency
|  | Bit 12 | (THWB) : BU: Sensor Thermal State
|  | Bit 13 | (COPA) : Liquid Cooled: Cooling Pump Alarm
|  | Bit 14 | (MOA) : Module Overheat Alarm
|  | Bit 15 | (LKON) : On Lock Alarm
ST19 |  | Bit 0 | (IWA) : IO function : Digital warning A
|  | Bit 1 | (IWB) : IO function : Digital warning B
|  | Bit 2 | (IWC) : IO function : Digital warning C
|  | Bit 3 | (IWD) : IO function : Digital warning D
|  | Bit 4 | (CWA) : IO function : Cabinet warning A
|  | Bit 5 | (CWB) : IO function : Cabinet warning B
|  | Bit 6 | (CWC) : IO function : Cabinet warning C
|  | Bit 7 | (TWA) : IO function : Thermal input warning A
|  | Bit 8 | (TWB) : IO function : Thermal input warning B
|  | Bit 9 | (TWC) : IO function : Thermal input warning C
|  | Bit 10 | (TWD) : IO function : Thermal input warning D
|  | Bit 11 | (CBW) : Circuit breaker : Error state (not in accordance to the start and stop pulse)
|  | Bit 12 | (P24C) : Cabinet IO supply (24V) missing
ILCI |  | Bit 0 | "DI50" logic inputs physical image
|  | Bit 1 | "DI51" logic inputs physical image
|  | Bit 2 | "DI52" logic inputs physical image
|  | Bit 3 | "DI53" logic inputs physical image
|  | Bit 4 | "DI54" logic inputs physical image
|  | Bit 5 | "DI55" logic inputs physical image
|  | Bit 6 | "DI56" logic inputs physical image
|  | Bit 7 | "DI57" logic inputs physical image
|  | Bit 8 | "DI58" logic inputs physical image
|  | Bit 9 | "DI59" logic inputs physical image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ILCR |  | Bit 0 | "DI50" logic inputs real image
|  | Bit 1 | "DI51" logic inputs real image
|  | Bit 2 | "DI52" logic inputs real image
|  | Bit 3 | "DI53" logic inputs real image
|  | Bit 4 | "DI54" logic inputs real image
|  | Bit 5 | "DI55" logic inputs real image
|  | Bit 6 | "DI56" logic inputs real image
|  | Bit 7 | "DI57" logic inputs real image
|  | Bit 8 | "DI58" logic inputs real image
|  | Bit 9 | "DI59" logic inputs real image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLCI |  | Bit 0 | "R60" relay physical image
|  | Bit 1 | "R61" relay physical image
|  | Bit 2 | "R62" relay physical image
|  | Bit 3 | "R63" relay physical image
|  | Bit 4 | "R64" relay physical image
|  | Bit 5 | "R65" relay physical image
|  | Bit 6 | "R66" relay physical image
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLCR |  | Bit 0 | "R60" relay real image
|  | Bit 1 | "R61" relay real image
|  | Bit 2 | "R62" relay real image
|  | Bit 3 | "R63" relay real image
|  | Bit 4 | "R64" relay real image
|  | Bit 5 | "R65" relay real image
|  | Bit 6 | "R66" relay real image
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
BPI0 |  | Bit 0 | Fault in power brick 1
|  | Bit 1 | Fault in power brick 2
|  | Bit 2 | Fault in power brick 3
|  | Bit 3 | Fault in power brick 4
|  | Bit 4 | Fault in power brick 5
|  | Bit 5 | Fault in power brick 6
|  | Bit 6 | Fault in power brick 7
|  | Bit 7 | Fault in power brick 8
|  | Bit 8 | Fault in power brick 9
|  | Bit 9 | Fault in power brick 10
|  | Bit 10 | Fault in power brick 11
|  | Bit 11 | Fault in power brick 12
BFI0 |  |  | Bit0 : Fault in AFE brick 1
Bit1 : Fault in AFE brick 2
Bit2 : Fault in AFE brick 3
Bit3 : Fault in AFE brick 4
Bit4 : Fault in AFE brick 5
Bit5 : Fault in AFE brick 6
Bit6 : Fault in AFE brick 7
Bit7 : Fault in AFE brick 8
Bit8 : Fault in AFE brick 9
Bit9 : Fault in AFE brick 10
Bit10 : Fault in AFE brick 11
Bit11 : Fault in AFE brick 12
BUI0 |  |  | Bit0 : Fault in BU brick 1
Bit1 : Fault in BU brick 2
Bit2 : Fault in BU brick 3
Bit3 : Fault in BU brick 4
Bit4 : Fault in BU brick 5
Bit5 : Fault in BU brick 6
Bit6 : Fault in BU brick 7
Bit7 : Fault in BU brick 8
Bit8 : Fault in BU brick 9
Bit9 : Fault in BU brick 10
Bit10 : Fault in BU brick 11
Bit11 : Fault in BU brick 12
CIC2 |  |  | On power-up, read CIC :
If CIC and CIC2 = 0 -> Ok
If CIC or CIC2 not 0 -> malfunction
Write FCS = "INI" to return to factory setting
|  | Bit 0 | = 1 : SFTY option card added
|  | Bit 1 | = 1 : SFTY option card removed
|  | Bit 2 | = 1 : SFTY option card changed
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST20 |  | Bit 1 | (MSDA) : Master Slave : Device loss
|  | Bit 2 | (BSQA) : Backlash Sequence : Alarm
|  | Bit 3 | (MDW) : MultiDrive : Communication link between SU AFE and drive loss (PWM disable)
SIWA |  | Bit 0 | = 1 : SI1_A
|  | Bit 1 | = 1 : SI2_A
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : SI3_A
|  | Bit 4 | = 1 : SI4_A
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : SI6_A (GUARDACK)
|  | Bit 7 | Reserved
|  | Bit 8 | = 1 : SI5_A (SMSTART)
|  | Bit 9 | = 1 : SI7_A (INTERLOCK_IN)
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SQWA |  | Bit 0 | = 1 : CCM24V_OUT_A
|  | Bit 1 | Reserved
|  | Bit 2 | = 1 : SQ1_A
|  | Bit 3 | = 1 : SQ2_A
|  | Bit 4 | = 1 : SQ3_A (INTERLOCK_OUT)
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SIWB |  | Bit 0 | = 1 : SI1_B
|  | Bit 1 | = 1 : SI2_B
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : SI3_B
|  | Bit 4 | = 1 : SI4_B
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : SI6_B (GUARDACK)
|  | Bit 7 | Reserved
|  | Bit 8 | = 1 : SI5_B (SMSTART)
|  | Bit 9 | = 1 : SI7_B (INTERLOCK_IN)
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
SQWB |  | Bit 0 | = 1 : CCM24V_OUT_B
|  | Bit 1 | Reserved
|  | Bit 2 | = 1 : SQ1_B
|  | Bit 3 | = 1 : SQ2_B
|  | Bit 4 | = 1 : SQ3_B (INTERLOCK_OUT)
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved