{"text_format":"2","workbook":"xls","n_sheets":6,"sheets":["Introduction","Courier, LCD & MODBUS Database","Data Types","DDBSignals","Events & Other Text","IEC60870-5-103"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":26,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Introduction","index":0,"n_rows":43,"n_cols":1,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[]
[]
["RELAY MENU DATABASE"]
[]
[]
["Models Covered:"]
[]
["P141****3**41**"]
["P142****3**41**"]
["P143****3**41**"]
["P144****3**41**"]
["P145****3**41**"]
[]
[]
["Courier Database"]
[]
["This database defines the structure of the relay menu for the courier interface and the front panel user interface. "]
["This includes all of the relay settings and measurements. Datatypes for indexed strings for Courier and the user interface are cross-referenced to the Menu Datatype Definition section (using a G Number). For all settable cells the setting limits and default value are also defined within this database."]
[]
["Data Types"]
[]
["This table defines the datatypes used for Courier and user interface. This section also defines the indexed string setting options for all interfaces. The datatypes defined within this section are cross-referenced to from the menu Database using a G number."]
[]
["DDB Signals"]
[]
["This table defines all of the relay internal digital signals (opto inputs, output contacts and protection inputs and outputs). A relay may have up to 512 internal signals each referenced by a numeric index as shown in this table. This numeric index is used to select a signal for the commissioning monitor port. It is also used to explicitly define protection events produced by the relay (see the Event Data section of this Appendix)."]
[]
["Event data"]
[]
["This section of the appendix specifies all the event information that can be produced by the relay. It details exactly how each event will be presented via the Courier and User interfaces."]
[]
["IEC 870 Monitor, IEC 870 Control, IEC 870 Generic Measurements & Extended Fault Data"]
[]
["These sections fully define the operation of the IEC 60870-5-103 (VDEW) interface for the relay. They should be read in conjunction with the relevant section of the SCADA Communications chapter (Px4x/EN SC)."]
[]
["References"]
[]
["Px4x/EN IT - Introduction: User Interface operation and connections to the relay"]
["Px4x/EN SC - Communications: Overview of communication interfaces"]
["Courier User Guide Courier_R6512"]
["IEC 60870-5-103 Telecontrol Equipment and Systems – Transmission Protocols –"]
["Companion Standard for the informative interface of Protection Equipment."]

{"sheet":"Courier, LCD & MODBUS Database","index":1,"n_rows":2530,"n_cols":31,"rows_kept":2530,"cut":false,"hidden":false,"merged":[[1921,30,1922,30],[2390,22,2390,26],[2326,22,2326,25],[2324,22,2324,25],[2322,22,2322,25],[1921,22,1922,25],[1921,26,1922,26],[1921,27,1922,27],[1921,28,1922,28],[2035,22,2035,25],[1921,19,1922,19],[1921,20,1922,20],[1921,21,1922,21],[1921,29,1922,29],[1921,15,1922,15],[1921,16,1922,16],[1921,17,1922,17],[1921,18,1922,18],[1921,11,1922,11],[1921,12,1922,12],[1921,13,1922,13],[1921,14,1922,14],[1921,7,1922,7],[1921,8,1922,8],[1921,9,1922,9],[1921,10,1922,10],[1921,3,1922,3],[1921,4,1922,4],[1921,5,1922,5],[1921,6,1922,6],[1858,22,1858,25],[2325,0,2326,0],[2325,1,2326,1],[2325,2,2325,3],[2326,2,2326,3],[2323,0,2324,0],[2323,1,2324,1],[2323,2,2323,3],[2324,2,2324,3],[2321,0,2322,0],[2321,1,2322,1],[2321,2,2321,3],[2322,2,2322,3],[1847,22,1847,25],[1848,22,1848,25],[1850,22,1850,25],[2034,22,2034,25],[1855,22,1855,25],[1856,22,1856,25],[1923,22,1923,25],[1924,22,1924,25],[1859,22,1859,25],[1837,30,1838,30],[1841,22,1841,25],[1842,22,1842,25],[1844,22,1844,25],[1837,26,1838,26],[1837,27,1838,27],[1837,28,1838,28],[1837,29,1838,29],[1837,19,1838,19],[1837,20,1838,20],[1837,21,1838,21],[1837,22,1838,25],[1837,15,1838,15],[1837,16,1838,16],[1837,17,1838,17],[1837,18,1838,18],[1837,11,1838,11],[1837,12,1838,12],[1837,13,1838,13],[1837,14,1838,14],[1837,7,1838,7],[1837,8,1838,8],[1837,9,1838,9],[1837,10,1838,10],[1837,3,1838,3],[1837,4,1838,4],[1837,5,1838,5],[1837,6,1838,6],[1819,22,1819,25],[1820,22,1820,25],[1821,22,1821,25],[1826,22,1826,25],[1851,22,1851,25],[1822,22,1822,25],[1824,22,1824,25],[1825,22,1825,25],[1831,22,1831,25],[1832,22,1832,25],[1833,22,1833,25],[1835,22,1835,25],[1836,22,1836,25],[1845,22,1845,25],[1804,22,1804,25],[1809,22,1809,25],[1813,30,1814,30],[1805,22,1805,25],[1806,22,1806,25],[1807,22,1807,25],[1808,22,1808,25],[1812,22,1812,25],[1813,3,1814,3],[1813,4,1814,4],[1813,5,1814,5],[1813,6,1814,6],[1813,7,1814,7],[1813,8,1814,8],[1813,9,1814,9],[1813,10,1814,10],[1813,11,1814,11],[1813,12,1814,12],[1813,13,1814,13],[1813,14,1814,14],[1813,15,1814,15],[1813,16,1814,16],[1813,17,1814,17],[1813,18,1814,18],[1813,19,1814,19],[1797,22,1797,25],[1813,20,1814,20],[1813,21,1814,21],[1813,22,1814,25],[1798,22,1798,25],[1800,22,1800,25],[1810,22,1810,25],[1811,22,1811,25],[1802,22,1802,25],[2033,22,2033,25],[1788,22,1788,25],[1789,22,1789,25],[1790,22,1790,25],[1791,22,1791,25],[1792,22,1792,25],[1793,22,1793,25],[1794,22,1794,25],[1799,22,1799,25],[1801,22,1801,25],[1779,22,1779,25],[2032,22,2032,25],[1780,22,1780,25],[1781,22,1781,25],[1782,22,1782,25],[1783,22,1783,25],[1784,22,1784,25],[1785,22,1785,25],[1787,22,1787,25],[1803,22,1803,25],[1773,22,1773,25],[1774,22,1774,25],[1775,22,1775,25],[1778,22,1778,25],[1769,22,1769,25],[1770,22,1770,25],[1771,22,1771,25],[1772,22,1772,25],[1764,22,1764,25],[1765,22,1765,25],[1766,22,1766,25],[1768,22,1768,25],[1760,22,1760,25],[1761,22,1761,25],[1762,22,1762,25],[1763,22,1763,25],[1755,30,1756,30],[1759,22,1759,25],[1755,26,1756,26],[1755,27,1756,27],[1755,28,1756,28],[1755,29,1756,29],[1755,19,1756,19],[1755,20,1756,20],[1755,21,1756,21],[1755,22,1756,25],[1755,15,1756,15],[1755,16,1756,16],[1755,17,1756,17],[1755,18,1756,18],[1755,11,1756,11],[1755,12,1756,12],[1755,13,1756,13],[1755,14,1756,14],[1755,7,1756,7],[1755,8,1756,8],[1755,9,1756,9],[1755,10,1756,10],[1755,3,1756,3],[1755,4,1756,4],[1755,5,1756,5],[1755,6,1756,6],[1751,8,1752,8],[1751,9,1752,9],[1751,10,1752,10],[1751,22,1751,25],[1752,22,1752,25],[1751,4,1752,4],[1751,5,1752,5],[1751,6,1752,6],[1751,7,1752,7],[1751,0,1752,0],[1751,1,1752,1],[1751,2,1752,2],[1751,3,1752,3],[1749,8,1750,8],[1749,9,1750,9],[1749,10,1750,10],[1750,22,1750,25],[1749,4,1750,4],[1749,5,1750,5],[1749,6,1750,6],[1749,7,1750,7],[1749,0,1750,0],[1749,1,1750,1],[1749,2,1750,2],[1749,3,1750,3],[1744,22,1744,25],[1745,22,1745,25],[1813,28,1814,28],[1813,29,1814,29],[1748,22,1748,25],[1749,22,1749,25],[1753,22,1753,25],[1754,22,1754,25],[1813,26,1814,26],[1813,27,1814,27],[1742,8,1743,8],[1742,9,1743,9],[1742,10,1743,10],[1742,22,1742,25],[1743,22,1743,25],[1740,8,1741,8],[1740,9,1741,9],[1740,10,1741,10],[1740,22,1740,25],[1736,22,1736,25],[1739,22,1739,25],[1740,0,1741,0],[1740,1,1741,1],[1740,2,1741,2],[1740,3,1741,3],[1740,4,1741,4],[1740,5,1741,5],[1740,6,1741,6],[1740,7,1741,7],[1733,8,1734,8],[1733,9,1734,9],[1733,10,1734,10],[1735,22,1735,25],[1733,4,1734,4],[1733,5,1734,5],[1733,6,1734,6],[1733,7,1734,7],[1733,0,1734,0],[1733,1,1734,1],[1733,2,1734,2],[1733,3,1734,3],[1731,8,1732,8],[1731,9,1732,9],[1731,10,1732,10],[1742,0,1743,0],[1742,1,1743,1],[1742,2,1743,2],[1742,3,1743,3],[1742,4,1743,4],[1742,5,1743,5],[1742,6,1743,6],[1731,0,1732,0],[1731,1,1732,1],[1731,2,1732,2],[1731,3,1732,3],[1742,7,1743,7],[1725,3,1726,3],[1725,4,1726,4],[1725,5,1726,5],[1725,6,1726,6],[1725,7,1726,7],[1731,4,1732,4],[1731,5,1732,5],[1731,6,1732,6],[1731,7,1732,7],[1723,30,1724,30],[1725,0,1726,0],[1725,1,1726,1],[1725,2,1726,2],[1725,8,1726,8],[1725,9,1726,9],[1725,10,1726,10],[1723,26,1724,26],[1723,27,1724,27],[1723,28,1724,28],[1723,29,1724,29],[1723,19,1724,19],[1723,20,1724,20],[1723,21,1724,21],[1723,22,1724,25],[1723,15,1724,15],[1723,16,1724,16],[1723,17,1724,17],[1723,18,1724,18],[1723,11,1724,11],[1723,12,1724,12],[1723,13,1724,13],[1723,14,1724,14],[1721,22,1721,25],[1722,22,1722,25],[1723,3,1724,3],[1723,4,1724,4],[1723,5,1724,5],[1723,6,1724,6],[1723,7,1724,7],[1723,8,1724,8],[1723,9,1724,9],[1723,10,1724,10],[1717,22,1717,25],[1718,22,1718,25],[1719,22,1719,25],[1720,22,1720,25],[1709,30,1710,30],[1711,22,1711,25],[1712,22,1712,25],[1713,22,1713,25],[1709,26,1710,26],[1709,27,1710,27],[1709,28,1710,28],[1709,29,1710,29],[1709,19,1710,19],[1709,20,1710,20],[1709,21,1710,21],[1709,22,1710,25],[1709,15,1710,15],[1709,16,1710,16],[1709,17,1710,17],[1709,18,1710,18],[1551,10,1552,10],[1551,7,1552,7],[1551,8,1552,8],[1709,3,1710,3],[1709,4,1710,4],[1709,5,1710,5],[1709,6,1710,6],[1709,7,1710,7],[1709,8,1710,8],[1709,9,1710,9],[1551,0,1552,0],[1551,1,1552,1],[1551,4,1552,4],[1551,9,1552,9],[1551,6,1552,6],[1551,5,1552,5],[1551,3,1552,3],[1551,2,1552,2],[1542,24,1543,24],[1542,25,1543,25],[1551,16,1552,16],[1551,17,1552,17],[1551,18,1552,18],[1547,22,1547,26],[1551,19,1552,19],[1551,20,1552,20],[1551,21,1552,21],[1661,28,1662,28],[1542,0,1543,0],[1542,1,1543,1],[1542,4,1543,4],[1542,6,1543,6],[1542,7,1543,7],[1542,8,1543,8],[1542,9,1543,9],[1542,10,1543,10],[1551,11,1552,11],[1661,22,1662,25],[1634,22,1634,25],[1661,26,1662,26],[1661,27,1662,27],[1656,26,1657,26],[1656,27,1657,27],[1652,22,1652,25],[1653,22,1653,25],[1654,22,1654,25],[1655,22,1655,25],[1661,18,1662,18],[1661,19,1662,19],[1661,20,1662,20],[1661,21,1662,21],[1661,14,1662,14],[1661,15,1662,15],[1661,16,1662,16],[1661,17,1662,17],[1661,10,1662,10],[1661,11,1662,11],[1661,12,1662,12],[1661,13,1662,13],[1656,30,1657,30],[1659,22,1659,25],[1660,22,1660,25],[1661,3,1662,3],[1661,4,1662,4],[1661,5,1662,5],[1661,6,1662,6],[1661,7,1662,7],[1661,8,1662,8],[1661,9,1662,9],[1656,28,1657,28],[1656,29,1657,29],[1656,19,1657,19],[1656,20,1657,20],[1656,21,1657,21],[1656,22,1657,25],[1656,15,1657,15],[1656,16,1657,16],[1656,17,1657,17],[1656,18,1657,18],[1656,11,1657,11],[1656,12,1657,12],[1656,13,1657,13],[1656,14,1657,14],[1656,7,1657,7],[1656,8,1657,8],[1656,9,1657,9],[1656,10,1657,10],[1656,3,1657,3],[1656,4,1657,4],[1656,5,1657,5],[1656,6,1657,6],[1649,27,1650,27],[1649,28,1650,28],[1649,29,1650,29],[1649,30,1650,30],[1649,20,1650,20],[1649,21,1650,21],[1649,22,1650,25],[1649,26,1650,26],[1649,16,1650,16],[1649,17,1650,17],[1649,18,1650,18],[1649,19,1650,19],[1649,12,1650,12],[1649,13,1650,13],[1649,14,1650,14],[1649,15,1650,15],[1648,22,1648,25],[1649,3,1650,3],[1649,4,1650,4],[1649,5,1650,5],[1649,6,1650,6],[1649,7,1650,7],[1649,8,1650,8],[1649,9,1650,9],[1649,10,1650,10],[1649,11,1650,11],[1646,8,1647,8],[1646,9,1647,9],[1646,10,1647,10],[1646,22,1646,25],[1647,22,1647,25],[1646,4,1647,4],[1646,5,1647,5],[1646,6,1647,6],[1646,7,1647,7],[1646,0,1647,0],[1646,1,1647,1],[1646,2,1647,2],[1646,3,1647,3],[1640,26,1641,26],[1642,22,1642,25],[1643,22,1643,25],[1644,22,1644,25],[1640,8,1641,8],[1640,9,1641,9],[1640,10,1641,10],[1640,22,1641,25],[1640,4,1641,4],[1640,5,1641,5],[1640,6,1641,6],[1640,7,1641,7],[1640,0,1641,0],[1640,1,1641,1],[1640,2,1641,2],[1640,3,1641,3],[1637,9,1638,9],[1637,10,1638,10],[1617,29,1618,29],[1637,22,1638,22],[1637,23,1638,23],[1637,24,1638,24],[1637,25,1638,25],[1637,26,1638,26],[1632,22,1632,26],[1633,22,1633,26],[1635,29,1636,29],[1637,0,1638,0],[1637,1,1638,1],[1637,2,1638,2],[1637,3,1638,3],[1637,4,1638,4],[1637,5,1638,5],[1637,6,1638,6],[1637,7,1638,7],[1637,8,1638,8],[1614,19,1615,19],[1614,20,1615,20],[1614,21,1615,21],[1614,22,1614,26],[1615,22,1615,26],[1612,30,1613,30],[1629,22,1629,26],[1614,29,1615,29],[1614,27,1615,27],[1614,30,1615,30],[1617,30,1618,30],[1612,29,1613,29],[1612,22,1612,26],[1612,27,1613,27],[1612,28,1613,28],[1612,16,1613,16],[1612,17,1613,17],[1612,18,1613,18],[1626,9,1627,9],[1626,10,1627,10],[1626,7,1627,7],[1614,17,1615,17],[1614,18,1615,18],[1626,8,1627,8],[1614,8,1615,8],[1614,9,1615,9],[1622,7,1623,7],[1622,8,1623,8],[1622,9,1623,9],[1622,4,1623,4],[1626,4,1627,4],[1626,5,1627,5],[1626,6,1627,6],[1626,0,1627,0],[1626,1,1627,1],[1626,2,1627,2],[1626,3,1627,3],[1608,29,1609,29],[1608,30,1609,30],[1620,22,1620,26],[1608,16,1609,16],[1608,17,1609,17],[1608,18,1609,18],[1608,19,1609,19],[1608,20,1609,20],[1608,21,1609,21],[1613,22,1613,26],[1622,0,1623,0],[1622,1,1623,1],[1622,2,1623,2],[1622,3,1623,3],[1635,18,1636,18],[1635,19,1636,19],[1635,20,1636,20],[1635,21,1636,21],[1635,22,1636,25],[1622,22,1622,26],[1623,22,1623,26],[1625,22,1625,26],[1627,22,1627,26],[1630,22,1630,26],[1631,22,1631,26],[1626,22,1626,26],[1602,30,1603,30],[1604,16,1605,16],[1604,17,1605,17],[1604,18,1605,18],[1604,19,1605,19],[1604,20,1605,20],[1604,21,1605,21],[1604,29,1605,29],[1604,30,1605,30],[1602,19,1603,19],[1617,4,1618,4],[1617,5,1618,5],[1617,6,1618,6],[1622,10,1623,10],[1617,7,1618,7],[1617,8,1618,8],[1617,9,1618,9],[1617,10,1618,10],[1622,5,1623,5],[1622,6,1623,6],[1617,0,1618,0],[1617,1,1618,1],[1617,2,1618,2],[1617,3,1618,3],[1602,20,1603,20],[1602,21,1603,21],[1602,29,1603,29],[1614,7,1615,7],[1602,16,1603,16],[1602,17,1603,17],[1602,18,1603,18],[1614,10,1615,10],[1614,11,1615,11],[1614,16,1615,16],[1612,4,1613,4],[1612,5,1613,5],[1612,6,1613,6],[1614,0,1615,0],[1614,1,1615,1],[1614,2,1615,2],[1614,3,1615,3],[1614,4,1615,4],[1614,5,1615,5],[1614,6,1615,6],[1598,29,1599,29],[1598,30,1599,30],[1612,8,1613,8],[1612,9,1613,9],[1612,10,1613,10],[1612,11,1613,11],[1612,12,1613,12],[1612,13,1613,13],[1612,14,1613,14],[1612,15,1613,15],[1598,27,1599,27],[1599,22,1599,26],[1598,28,1599,28],[1598,16,1599,16],[1598,17,1599,17],[1598,18,1599,18],[1598,19,1599,19],[1598,20,1599,20],[1598,21,1599,21],[1598,22,1598,26],[1608,28,1609,28],[1612,7,1613,7],[1612,0,1613,0],[1612,1,1613,1],[1612,2,1613,2],[1612,3,1613,3],[1612,19,1613,19],[1612,20,1613,20],[1612,21,1613,21],[1608,7,1609,7],[1593,21,1595,21],[1593,29,1595,29],[1593,28,1595,28],[1593,30,1595,30],[1593,22,1593,26],[1593,27,1595,27],[1594,22,1594,26],[1595,22,1595,26],[1591,20,1592,20],[1591,21,1592,21],[1591,29,1592,29],[1591,30,1592,30],[1591,22,1591,26],[1592,22,1592,26],[1591,27,1592,27],[1591,28,1592,28],[1591,16,1592,16],[1591,17,1592,17],[1591,18,1592,18],[1591,19,1592,19],[1608,8,1609,8],[1608,9,1609,9],[1608,10,1609,10],[1608,11,1609,11],[1608,12,1609,12],[1608,13,1609,13],[1608,14,1609,14],[1608,15,1609,15],[1602,28,1603,28],[1604,28,1605,28],[1607,22,1607,26],[1604,22,1604,26],[1605,22,1605,26],[1604,27,1605,27],[1608,22,1608,26],[1609,22,1609,26],[1608,27,1609,27],[1608,0,1609,0],[1608,1,1609,1],[1608,2,1609,2],[1608,3,1609,3],[1608,4,1609,4],[1608,5,1609,5],[1608,6,1609,6],[1586,30,1587,30],[1588,16,1589,16],[1588,17,1589,17],[1588,18,1589,18],[1588,19,1589,19],[1588,20,1589,20],[1588,21,1589,21],[1588,29,1589,29],[1588,30,1589,30],[1586,20,1587,20],[1586,21,1587,21],[1586,29,1587,29],[1588,22,1588,26],[1589,22,1589,26],[1586,27,1587,27],[1588,27,1589,27],[1604,12,1605,12],[1604,13,1605,13],[1604,14,1605,14],[1604,15,1605,15],[1586,16,1587,16],[1586,17,1587,17],[1586,18,1587,18],[1586,19,1587,19],[1582,30,1583,30],[1584,16,1585,16],[1584,17,1585,17],[1584,18,1585,18],[1584,19,1585,19],[1584,20,1585,20],[1584,21,1585,21],[1584,29,1585,29],[1584,30,1585,30],[1582,20,1583,20],[1582,21,1583,21],[1582,29,1583,29],[1582,22,1582,26],[1583,22,1583,26],[1582,28,1583,28],[1582,27,1583,27],[1582,16,1583,16],[1582,17,1583,17],[1582,18,1583,18],[1582,19,1583,19],[1579,30,1580,30],[1584,10,1585,10],[1584,11,1585,11],[1586,5,1587,5],[1586,6,1587,6],[1586,7,1587,7],[1586,8,1587,8],[1586,9,1587,9],[1586,10,1587,10],[1586,11,1587,11],[1579,21,1580,21],[1579,29,1580,29],[1579,22,1579,26],[1580,22,1580,26],[1579,27,1580,27],[1579,28,1580,28],[1579,17,1580,17],[1579,18,1580,18],[1579,19,1580,19],[1579,20,1580,20],[1577,30,1578,30],[1588,0,1589,0],[1588,1,1589,1],[1588,2,1589,2],[1588,3,1589,3],[1588,4,1589,4],[1584,6,1585,6],[1584,7,1585,7],[1584,8,1585,8],[1584,9,1585,9],[1577,21,1578,21],[1577,29,1578,29],[1577,22,1577,26],[1578,22,1578,26],[1577,27,1578,27],[1577,28,1578,28],[1577,17,1578,17],[1577,18,1578,18],[1577,19,1578,19],[1577,20,1578,20],[1586,4,1587,4],[1582,9,1583,9],[1582,10,1583,10],[1582,11,1583,11],[1584,5,1585,5],[1582,4,1583,4],[1582,5,1583,5],[1582,6,1583,6],[1586,0,1587,0],[1586,1,1587,1],[1586,2,1587,2],[1586,3,1587,3],[1573,21,1574,21],[1573,29,1574,29],[1584,0,1585,0],[1584,1,1585,1],[1584,2,1585,2],[1584,3,1585,3],[1584,4,1585,4],[1582,7,1583,7],[1582,8,1583,8],[1577,16,1578,16],[1573,17,1574,17],[1573,18,1574,18],[1573,19,1574,19],[1573,20,1574,20],[1579,9,1580,9],[1579,10,1580,10],[1579,11,1580,11],[1573,16,1574,16],[1579,16,1580,16],[1577,12,1578,12],[1577,13,1578,13],[1577,14,1578,14],[1577,15,1578,15],[1579,12,1580,12],[1572,22,1572,26],[1579,4,1580,4],[1577,8,1578,8],[1577,9,1578,9],[1577,10,1578,10],[1577,11,1578,11],[1579,5,1580,5],[1579,6,1580,6],[1579,7,1580,7],[1579,8,1580,8],[1579,0,1580,0],[1579,1,1580,1],[1579,2,1580,2],[1579,3,1580,3],[1577,4,1578,4],[1577,5,1578,5],[1577,6,1578,6],[1577,7,1578,7],[1577,0,1578,0],[1577,1,1578,1],[1577,2,1578,2],[1577,3,1578,3],[1567,20,1569,20],[1567,21,1569,21],[1567,22,1567,26],[1568,22,1568,26],[1569,22,1569,26],[1567,16,1569,16],[1567,17,1569,17],[1567,18,1569,18],[1567,19,1569,19],[1565,27,1566,27],[1565,29,1566,29],[1565,30,1566,30],[1573,27,1574,27],[1573,28,1574,28],[1567,27,1569,27],[1573,30,1574,30],[1567,28,1569,28],[1567,29,1569,29],[1567,30,1569,30],[1565,20,1566,20],[1565,21,1566,21],[1565,22,1565,26],[1566,22,1566,26],[1565,16,1566,16],[1565,17,1566,17],[1565,18,1566,18],[1565,19,1566,19],[1560,30,1561,30],[1562,16,1563,16],[1562,17,1563,17],[1562,18,1563,18],[1562,19,1563,19],[1562,20,1563,20],[1562,21,1563,21],[1562,29,1563,29],[1562,30,1563,30],[1560,20,1561,20],[1560,21,1561,21],[1560,29,1561,29],[1560,28,1561,28],[1561,22,1561,26],[1560,27,1561,27],[1560,16,1561,16],[1560,17,1561,17],[1560,18,1561,18],[1560,19,1561,19],[1556,30,1557,30],[1558,16,1559,16],[1558,17,1559,17],[1558,18,1559,18],[1558,19,1559,19],[1558,20,1559,20],[1558,21,1559,21],[1558,29,1559,29],[1558,30,1559,30],[1556,20,1557,20],[1556,21,1557,21],[1556,29,1557,29],[1556,22,1556,26],[1556,27,1557,27],[1556,28,1557,28],[1557,22,1557,26],[1556,16,1557,16],[1556,17,1557,17],[1556,18,1557,18],[1556,19,1557,19],[1553,30,1554,30],[1573,9,1574,9],[1573,10,1574,10],[1573,11,1574,11],[1573,12,1574,12],[1573,13,1574,13],[1573,14,1574,14],[1573,15,1574,15],[1573,22,1573,26],[1574,22,1574,26],[1553,20,1554,20],[1553,21,1554,21],[1553,29,1554,29],[1553,22,1553,26],[1554,22,1554,26],[1553,27,1554,27],[1553,28,1554,28],[1553,16,1554,16],[1553,17,1554,17],[1553,18,1554,18],[1553,19,1554,19],[1551,29,1552,29],[1551,30,1552,30],[1551,22,1551,26],[1551,27,1552,27],[1551,28,1552,28],[1552,22,1552,26],[1551,12,1552,12],[1551,13,1552,13],[1551,14,1552,14],[1551,15,1552,15],[1540,30,1541,30],[1542,30,1543,30],[1540,20,1541,20],[1540,21,1541,21],[1540,22,1541,25],[1540,29,1541,29],[1542,26,1543,26],[1542,27,1543,27],[1542,22,1543,22],[1542,23,1543,23],[1540,16,1541,16],[1540,17,1541,17],[1540,18,1541,18],[1540,19,1541,19],[1537,26,1538,26],[1537,27,1538,27],[1537,28,1538,28],[1537,30,1538,30],[1537,8,1538,8],[1537,9,1538,9],[1537,10,1538,10],[1537,12,1538,12],[1537,4,1538,4],[1537,5,1538,5],[1537,6,1538,6],[1537,7,1538,7],[1537,0,1538,0],[1537,1,1538,1],[1537,2,1538,2],[1537,3,1538,3],[1535,26,1536,26],[1535,27,1536,27],[1535,28,1536,28],[1535,30,1536,30],[1529,26,1530,26],[1529,27,1530,27],[1535,0,1536,0],[1535,1,1536,1],[1535,2,1536,2],[1535,3,1536,3],[1535,4,1536,4],[1535,5,1536,5],[1535,6,1536,6],[1535,7,1536,7],[1529,8,1530,8],[1529,9,1530,9],[1529,10,1530,10],[1529,12,1530,12],[1529,4,1530,4],[1529,5,1530,5],[1529,6,1530,6],[1529,7,1530,7],[1529,0,1530,0],[1529,1,1530,1],[1529,2,1530,2],[1529,3,1530,3],[1516,22,1516,25],[1520,22,1520,25],[1526,22,1526,25],[1527,22,1527,25],[1519,22,1519,25],[1523,22,1523,25],[1535,22,1536,25],[1537,22,1538,25],[1539,22,1539,25],[1529,22,1530,22],[1529,23,1530,23],[1529,24,1530,24],[1529,25,1530,25],[1535,8,1536,8],[1535,9,1536,9],[1535,10,1536,10],[1535,12,1536,12],[1512,20,1513,20],[1512,21,1513,21],[1512,27,1513,27],[1512,29,1513,29],[1512,16,1513,16],[1512,17,1513,17],[1512,18,1513,18],[1512,19,1513,19]],"merged_total":6322,"flags":["formulas_cached_only","merged_cut"]}
["Courier",null,"Menu Text","Data Type","LCD","MODBUS Address",null,"Data Group",null,null,null,"Default Setting","Cell Type","Min","Max","Step","Password Level","Model",{"$nulls":4},"Visible If",{"$nulls":5},"Comment","CS103","GI"]
["Col","Row",null,null,null,"Start","End","Courier","MODBUS",{"$nulls":8},"P141","P142","P143","P144","P145","Cell","Test","Value","Ripple","BF03","Mult Pri/Sec"]
[]
[0,0,"SYSTEM DATA",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[0,1,"Language","Indexed String",null,null,null,"G19","G19",null,1,"English","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[0,1,"Language","Indexed String",null,null,null,"G19","G19",null,1,"English","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Chinese Language variant","*"]
[{"$nulls":28},"Chinese via HMI only"]
[0,2,"Password","ASCII Password (4 chars)",null,"4x00001","4x00002","G20","G20",null,2,"AAAA","Setting",65,90,1,0,"*","*","*","*","*",{"$nulls":7},"*"]
[0,3,"Sys Fn Links","Binary Flag (8 bits)",null,"4x00003",null,"G95","G95",null,1,0,"Setting",1,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[0,4,"Description","ASCII Text (16 chars)",null,"4x00004","4x00011",null,"G3",null,8,"MiCOM P141","Setting",32,163,1,2,"*",{"$nulls":11},"*"]
[{"$nulls":11},"MiCOM P142",{"$nulls":6},"*"]
[{"$nulls":11},"MiCOM P143",{"$nulls":7},"*"]
[{"$nulls":11},"MiCOM P144",{"$nulls":8},"*"]
[{"$nulls":11},"MiCOM P145",{"$nulls":9},"*"]
[0,5,"Plant Reference","ASCII Text (16 chars)",null,"4x00012","4x00019",null,"G3",null,8,"MiCOM","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[0,6,"Model Number","ASCII Text (16 chars)",null,"3x00020","3x00035",null,"G3",null,16,"Model Number","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[0,7,"Firmware Number","ASCII Text (16 chars)",{"$nulls":4},"G3",null,8,"Firmware Number","Data",{"$nulls":16},"*"]
[0,8,"Serial Number","ASCII Text (7 chars)",null,"3x00044","3x00051",null,"G3",null,8,"Serial Number","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[0,9,"Frequency","Unsigned Integer (16 bits)",null,"4x00020",null,null,"G1",null,1,50,"Setting",50,60,10,2,"*","*","*","*","*",{"$nulls":7},"*"]
[0,"0A","Comms Level","Unsigned Integer (16 bits)",{"$nulls":7},2,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[0,"0B","Relay Address","Unsigned Integer (16 bits)",{"$nulls":7},255,"Setting",0,255,1,1,"*","*","*","*","*",{"$nulls":6},"Build = Courier"]
[{"$nulls":28},"Address available via LCD"]
[0,"0B","Relay Address","Unsigned Integer (16 bits)",{"$nulls":7},1,"Setting",1,247,1,1,"*","*","*","*","*",{"$nulls":6},"Build = MODBUS"]
[{"$nulls":28},"Address available via LCD"]
[0,"0B","Relay Address","Unsigned Integer (16 bits)",{"$nulls":7},1,"Setting",0,254,1,1,"*","*","*","*","*",{"$nulls":6},"Build = IEC60870-5-103"]
[{"$nulls":28},"Address available via LCD"]
[0,"0B","Relay Address","Unsigned Integer (16 bits)",{"$nulls":7},1,"Setting",0,65534,1,1,"*","*","*","*","*",{"$nulls":6},"Build = DNP3.0"]
[{"$nulls":28},"Address available via LCD"]
[null,null,null,"Binary Flag (16 bits)",null,"3x00001",null,null,"G26",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Relay status (repeat of Courier Status byte without"]
[{"$nulls":28},"the busy flag)"]
[0,"0C","Plant Status","Binary Flag (16 bits)",null,"3x00002",null,"G4","G4",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*","*"]
[0,"0D","Control Status","Binary Flag (16 bits)",null,"3x00004",null,"G5","G5",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*","*"]
[0,"0E","Active Group","Unsigned Integer (16 bits)",null,"3x00006",null,null,"G1",null,1,1,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*","*"]
[0,10,"CB Trip/Close","Indexed String",null,null,null,"G55",null,null,null,"No Operation","Command",0,2,1,1,"*","*","*","*","*","G99 = 1, 3, 5, 7",null,null,null,"*",null,"Visible to LCD + Front Port","*"]
[0,10,"CB Trip/Close","Indexed String","N/A","4x00021",null,"G55","G55",null,null,"No Operation","Command",0,2,1,1,"*","*","*","*","*","G99 = 2, 3, 6, 7",null,null,null,"*",null,"Visible to Rear Port","*"]
[0,11,"Software Ref. 1","ASCII Text (16 chars)",null,"3x00052","3x00059",null,"G3",null,8,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Relay software reference","*"]
[0,12,"Software Ref. 2","ASCII Text (16 chars)",{"$nulls":4},"G3",null,8,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"IEC61850/UCA2/DNP3 builds only","*"]
[0,13,"Software Ref. 3","ASCII Text (16 chars)",{"$nulls":4},"G3",null,8,null,"Data",{"$nulls":16},"*"]
[0,14,"Software Ref. 4","ASCII Text (16 chars)",{"$nulls":4},"G3",null,8,null,"Data",{"$nulls":16},"*"]
[0,20,"Opto I/P Status","Binary Flag (32 bits)",null,"3x00007",null,"G8","G8",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*","*"]
[null,null,null,"Indexed String"]
[0,21,"Relay O/P Status","Binary Flag (32 bits)",null,"3x00008","3x00009","G9","G9",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*","*"]
[null,null,null,"Indexed String"]
[0,22,"Alarm Status 1","Binary Flag (32 bits)",null,"3x00011","3x00012","G96-1","G96-1",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*","*"]
[null,null,null,"Indexed String"]
[0,23,"UNUSED"]
[0,30,"Opto I/P Status","Binary Flag (32 bits)",null,"3x00725","3x00726","G27","G27",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Duplicate of [0020]","*","*"]
[null,null,null,"Indexed String",{"$nulls":24},"DDB signals 32-63"]
[0,40,"Relay O/P Status","Binary Flag (32 bits)",null,"3x00723","3x00724","G27","G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Duplicate of [0021]","*","*"]
[null,null,null,"Indexed String",{"$nulls":24},"DDB signals 0-31"]
[0,50,"Alarm Status 1","Binary Flag (32 bits)",null,"3x00011","3x00012","G96-1","G96-1",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Alarms","*","*"]
[null,null,null,"Indexed String"]
[0,51,"Alarm Status 2","Binary Flag (32 bits)",null,"3x00013","3x00014","G96-2","G96-2",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Alarms","*","*"]
[null,null,null,"Indexed String"]
[0,52,"Alarm Status 3","Binary Flag (32 bits)",null,"3x00015","3x00016","G228","G228",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Platform Alarms","*","*"]
[null,null,null,"Indexed String"]
[0,"D0","Access Level","Unsigned Integer (16 bits)",null,"3x00010",null,"G1","G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[0,"D1","Password Control","Unsigned Integer (16 bits)",null,"4x00022",null,"G22","G22",null,1,2,"Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[0,"D2","Password Level 1","ASCII Password (4 chars)",null,"4x00023","4x00024","G20","G20",null,2,"AAAA","Setting",65,90,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[0,"D3","Password Level 2","ASCII Password (4 chars)",null,"4x00025","4x00026","G20","G20",null,2,"AAAA","Setting",65,90,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[1,0,"VIEW RECORDS",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[{"$nulls":5},"3x00100",null,null,"G1",null,1,{"$nulls":17},"No of event records stored"]
[{"$nulls":5},"3x00101",null,null,"G1",null,1,{"$nulls":17},"No of fault records stored"]
[{"$nulls":5},"3x00102",null,null,"G1",null,1,{"$nulls":17},"No of maintenance records stored"]
[1,1,"Select Event","Unsigned Integer (16 bits)",null,"4x00100",null,null,"G1",null,null,0,"Setting",0,249,1,0,"*","*","*","*","*",{"$nulls":4},"*",null,"Max value is oldest record","*"]
[null,null,"[0...n]",{"$nulls":25},"n is last event record."]
[1,2,"Menu Cell Ref","Cell Reference","N/A","3x00107",null,null,"G13",null,1,"(From Record)","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Indicates type of event","*"]
[{"$nulls":28},"See event sheet"]
[1,3,"Time & Date","IEC870 Date & Time",null,"3x00103","3x00106",null,"G12",null,4,"(From Record)","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,4,"Record Text","ASCII Text (32 chars)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"See event sheet","*"]
[1,5,"Record Value","Unsigned Integer (32 bits)",null,"3x00108","3x00109",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Note DTL depends on event type","*"]
[{"$nulls":28},"See event sheet of spreadsheet"]
[1,6,"Select Fault","Unsigned Integer (16 bits)",null,"4x00101",null,null,"G1",null,null,0,"Setting",0,4,1,0,"*","*","*","*","*",{"$nulls":4},"*",null,"Allows Fault Record to be selected","*"]
[null,null,"[0...n]",{"$nulls":25},"n is last fault record"]
[{"$nulls":5},"3x00110",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"MODBUS address where change occurred"]
[{"$nulls":28},"Alarm 30011; Relay 30723; Opto 30725"]
[{"$nulls":5},"3x00111",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"State of current 16 ddb elements"]
[{"$nulls":5},"3x00112",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Additional data present"]
["N/A",null,"Started Phase",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","Any Current Protection Start",{"$nulls":6},"*"]
[null,null,"A B C N",{"$nulls":25},"A/B/C/N Visible if Start A/B/C/N"]
["N/A",null,"Tripped Phase",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","Any Current Protection Trip",{"$nulls":6},"*"]
[null,null,"A B C N",{"$nulls":25},"A/B/C/N Visible if Trip A/B/C/N"]
["N/A",null,"Overcurrent",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","I> Start"]
[null,null,"Start I> 1234",{"$nulls":25},"1/2/3/4 Visible if Start I>1/2/3/4"]
["N/A",null,"Overcurrent",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","I> Trip"]
[null,null,"Trip I> 1234",{"$nulls":25},"1/2/3/4 Visible if Trip I>1/2/3/4"]
["N/A",null,"Neg Seq O/C",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","I2> Start"]
[null,null,"Start I2> 1234",{"$nulls":25},"1/2/3/4 Visible if Start I>1/2/3/4"]
["N/A",null,"Neg Seq O/C",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","I2> Trip"]
[null,null,"Trip I2> 1234",{"$nulls":25},"1/2/3/4 Visible if Trip I>1/2/3/4"]
["N/A",null,"Broken Conductor",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","Broken Conductor Trip"]
[null,null,"Start Trip"]
["N/A",null,"Earth Fault 1",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","IN1> Start"]
[null,null,"Start IN1> 1234",{"$nulls":25},"1/2/3/4 visible if Start IN1>1/2/3/4"]
["N/A",null,"Earth Fault 1",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","IN1> Trip"]
[null,null,"Trip IN1> 1234",{"$nulls":25},"1/2/3/4 visible if Trip IN1>1/2/3/4"]
["N/A",null,"Earth Fault 2",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","IN2> Start"]
[null,null,"Start IN2> 1234",{"$nulls":25},"1/2/3/4 visible if Start IN2>1/2/3/4"]
["N/A",null,"Earth Fault 2",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","IN2> Trip"]
[null,null,"Trip IN2> 1234",{"$nulls":25},"1/2/3/4 visible if Trip IN2>1/2/3/4"]
["N/A",null,"Sensitive E/F",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","ISEF> Start"]
[null,null,"Start ISEF> 1234",{"$nulls":25},"1/2/3/4 visible if Start ISEF>1/2/3/4"]
["N/A",null,"Sensitive E/F",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","ISEF> Trip"]
[null,null,"Trip ISEF> 1234",{"$nulls":25},"1/2/3/4 visible if Trip ISEF>1/2/3/4"]
["N/A",null,"Restricted E/F",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","IREF> Trip"]
[null,null,"Trip IREF>"]
["N/A",null,"Residual O/V NVD",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","VN> Start"]
[null,null,"Start VN> 1 2",{"$nulls":25},"1/2 visible if Start VN>1/2"]
["N/A",null,"Residual O/V NVD",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","VN> Trip"]
[null,null,"Trip VN> 1 2",{"$nulls":25},"1/2 visible if Trip VN>1/2"]
["N/A",null,"Thermal  Overload",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","Thermal Overload Alarm/Trip"]
[null,null,"Alarm Trip"]
["N/A",null,"Neg Seq O/V",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","V2> Start / V2> Trip"]
[null,null,"V2> Start Trip"]
["N/A",null,"U/Voltage Start",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","V< Start"]
[null,null,"V< 1 2  AB BC CA",{"$nulls":25},"1/2/AB/BC/CA visible if Start V<1/2"]
["N/A",null,"U/Voltage Trip",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","V< Trip"]
[null,null,"V< 1 2  AB BC CA",{"$nulls":25},"1/2/AB/BC/CA visible if Trip V<1/2"]
["N/A",null,"O/Voltage Start",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","V> Start"]
[null,null,"V> 1 2  AB BC CA",{"$nulls":25},"1/2/AB/BC/CA visible if Start V>1/2"]
["N/A",null,"O/Voltage Trip",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","V> Trip"]
[null,null,"V> 1 2  AB BC CA",{"$nulls":25},"1/2/AB/BC/CA visible if Trip V>1/2"]
["N/A",null,"Underfrequency",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","F< Start"]
[null,null,"Start F< 1234",{"$nulls":25},"1/2/3/4 visible if Start F<1/2/3/4"]
["N/A",null,"Underfrequency",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","F< Trip"]
[null,null,"Trip F< 1234",{"$nulls":25},"1/2/3/4 visible if Trip F<1/2/3/4"]
["N/A",null,"Overfrequency",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","F> Start"]
[null,null,"Start F> 1 2",{"$nulls":25},"1/2 visible if Start F>1/2"]
["N/A",null,"Overfrequency",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","F> Trip"]
[null,null,"Trip F> 1 2",{"$nulls":25},"1/2 visible if Trip F>1/2"]
["N/A",null,"df/dt Protection",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","df/dt Start"]
[null,null,"Start df/dt>1234",{"$nulls":25},"1/2/2/3/4 visible if Start df/dt 1/2/3/4"]
["N/A",null,"df/dt Protection",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","df/dt Trip"]
[null,null,"Trip df/dt>1234",{"$nulls":25},"1/2/2/3/4 visible if Trip df/dt 1/2/3/4"]
["N/A",null,"Overadmittance ",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","YN> Start / YN> Trip"]
[null,null,"YN> Start Trip",{"$nulls":25},"visible if Start YN>/Trip YN>"]
["N/A",null,"Overconductance",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","GN> Start / GN> Trip"]
[null,null,"GN> Start Trip",{"$nulls":25},"visible if Start GN>/Trip GN>"]
["N/A",null,"Oversusceptance",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","BN> Start / BN> Trip"]
[null,null,"BN> Start Trip",{"$nulls":25},"visible if Start BN>/Trip BN>"]
["N/A",null,"Breaker Fail",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","CB Fail"]
[null,null,"CB Fail 1 2",{"$nulls":25},"1/2 visible if CB Fail 1/2"]
["N/A",null,"Supervision",{"$nulls":9},"Data",{"$nulls":4},"*","*","*","*","*","Alarm VTS/CTS/VCO/CLP",{"$nulls":5},"VTS/CTS/VCO/CLP visible if "]
[null,null,"VTS CTS VCO CLP",{"$nulls":25},"Alarm VTS/CTS/VCO/CLP"]
["N/A",null,"A/R State",{"$nulls":9},"Data",{"$nulls":5},"*","*","*","*","SC Count>0"]
[null,null,"Trip 1 2 3 4 5",{"$nulls":25},"1/2/3/4 visible if SC: Count 1/2/3/4"]
[1,7,"Faulted Phase","Binary Flag (8 bits)","N/A","3x00113",null,"G16","G16",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Started phases + tripped phases","*"]
[1,8,"Start Elements 1","Binary Flag (32 bits)","N/A","3x00114","3x00115","G84","G84",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Started main elements","*"]
[null,null,null,"Indexed String"]
[1,9,"Start Elements 2","Binary Flag (32 bits)","N/A","3x00116","3x00117","G107","G107",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Started secondary elements","*"]
[null,null,null,"Indexed String"]
[1,"0A","Start Elements 3","Binary Flag (32 bits)","N/A","3x00118","3x00119","G161","G161",{"$nulls":8},"*","*","*","*","*",{"$nulls":6},"Advanced frequency elements"]
[null,null,null,"Indexed String"]
[1,"0B","Unused"]
[1,"0C","Trip Elements 1","Binary Flag (32 bits)","N/A","3x00121","3x00122","G85","G85",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Tripped main elements","*"]
[null,null,null,"Indexed String"]
[1,"0D","Trip Elements 2","Binary Flag (32 bits)","N/A","3x00123","3x00124","G86","G86",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Tripped secondary elements","*"]
[null,null,null,"Indexed String"]
[1,"0E","Trip Elements 3","Binary Flag (32 bits)","N/A","3x00125","3x00126","G162","G162",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Advanced frequency elements"]
[null,null,null,"Indexed String"]
[1,"0F","Trip Elements 4","Binary Flag (32 bits)","N/A","3x00127","3x00128","G164","G164",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Advanced frequency elements"]
[null,null,null,"Indexed String"]
[1,10,"Fault Alarms","Binary Flag (32 bits)","N/A","3x00129","3x00130","G87","G87",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Faullt Alarms/Warnings","*"]
[null,null,null,"Indexed String"]
[1,11,"Fault Time","IEC870 Date & Time",null,"3x00131","3x00132",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Fault Record Time Stamp"]
[1,12,"Active Group","Unsigned Integer (16 bits)",null,"3x00135",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,13,"System Frequency","Courier Number (frequency)",null,"3x00136",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,14,"Fault Duration","Courier Number (time)",null,"3x00137","3x00138",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,15,"CB Operate Time","Courier Number (time)",null,"3x00141",null,null,"G25",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,16,"Relay Trip Time","Courier Number (time)",null,"3x00142","3x00143",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,17,"Fault Location","Courier Number (metres)",null,"3x00144","3x00145",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","SMF",null,null,"*",null,null,"OD09=0 AND 0D0A=0, can be invalid","*"]
[1,18,"Fault Location","Courier Number (miles)",null,"3x00146","3x00147",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","SMF",null,null,"*",null,null,"OD09=1 AND 0D0A=0, can be invalid","*"]
[1,19,"Fault Location","Courier Number (impedance)",null,"3x00148","3x00149",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","SMF",null,null,"*",null,null,"0D0A=1 Can be Invalid","*"]
[1,"1A","Fault Location","Courier Number (percentage)",null,"3x00150","3x00151",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","SMF",null,null,"*",null,null,"0D0A=2 Can be Invalid","*"]
[1,"1B","IA","Courier Number (current)",null,"3x00152","3x00153",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[1,"1C","IB","Courier Number (current)",null,"3x00154","3x00155",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[1,"1D","IC","Courier Number (current)",null,"3x00156","3x00157",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[1,"1E","VAB","Courier Number (voltage)",null,"3x00158","3x00159",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[1,"1F","VBC","Courier Number (voltage)",null,"3x00160","3x00161",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[1,20,"VCA","Courier Number (voltage)",null,"3x00162","3x00163",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[1,21,"IN Measured","Courier Number (current)",null,"3x00164","3x00165",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M5"]
[1,22,"IN Derived","Courier Number (current)",null,"3x00166","3x00167",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
[1,23,"IN Sensitive","Courier Number (current)",null,"3x00168","3x00169",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M6"]
[1,24,"IREF Diff","Courier Number (current)",null,"3x00170","3x00171",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4","(0915=1) && (3A01=3,4 OR 5)"]
[1,25,"IREF Bias","Courier Number (current)",null,"3x00172","3x00173",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4","(0915=1) && (3A01=3,4 OR 5)"]
[1,26,"VAN","Courier Number (voltage)",null,"3x00174","3x00175",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
[1,27,"VBN","Courier Number (voltage)",null,"3x00176","3x00177",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
[1,28,"VCN","Courier Number (voltage)",null,"3x00178","3x00179",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
[1,29,"VN Derived","Courier Number (voltage)",null,"3x00180","3x00181",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M1"]
[null,null,"VN Measured",{"$nulls":17},"*",{"$nulls":6},"M3"]
[1,"2A","Admittance","Courier Number (inverse ohms)",null,"3x00182","3x00183",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M6/M1","(091B=1) && (4002=0)"]
[{"$nulls":20},"*",{"$nulls":6},"M6/M3","In MODBUS represented in [mS]"]
[1,"2B","Conductance","Courier Number (inverse ohms)",null,"3x00184","3x00185",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M6/M1","(091B=1) && (4002=0)"]
[{"$nulls":20},"*",{"$nulls":6},"M6/M3","In MODBUS represented in [mS]"]
[1,"2C","Susceptance","Courier Number (inverse ohms)",null,"3x00186","3x00187",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M6/M1","(091B=1) && (4002=0)"]
[{"$nulls":20},"*",{"$nulls":6},"M6/M3","In MODBUS represented in [mS]"]
[1,"2D","Admittance","Courier Number (inverse ohms)",null,"3x00188","3x00189",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M5/M1","(091B=1) && (4002=1)"]
[{"$nulls":20},"*",{"$nulls":6},"M5/M3","In MODBUS represented in [mS]"]
[1,"2E","Conductance","Courier Number (inverse ohms)",null,"3x00190","3x00191",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M5/M1","(091B=1) && (4002=1)"]
[{"$nulls":20},"*",{"$nulls":6},"M5/M3","In MODBUS represented in [mS]"]
[1,"2F","Susceptance","Courier Number (inverse ohms)",null,"3x00192","3x00193",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M5/M1","(091B=1) && (4002=1)"]
[{"$nulls":20},"*",{"$nulls":6},"M5/M3","In MODBUS represented in [mS]"]
[1,"F0","Select Maint","Unsigned Integer (16 bits)",null,"4x00102",null,null,"G1",null,null,"Manual override to select a fault record","Setting",0,4,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,"Allows Self Test Report to be selected","*"]
[null,null,"[0...n]",{"$nulls":25},"n is last maintenance record"]
[1,"F1","Maint Text","ASCII Text (32 chars)",{"$nulls":6},1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,"F2","Maint Type","Unsigned Integer (32 bits)",null,"3x00036","3x00037",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,"F3","Maint Data","Unsigned Integer (32 bits)",null,"3x00038","3x00039",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[1,"FF","Reset Indication","Indexed String",null,null,null,"G11",null,null,null,"No","Command",0,1,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[2,0,"MEASUREMENTS 1",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[2,1,"IA Magnitude","Courier Number (current)",null,"3x00200","3x00201",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,2,"IA Phase Angle","Courier Number (angle)",null,"3x00202",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,3,"IB Magnitude","Courier Number (current)",null,"3x00203","3x00204",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,4,"IB Phase Angle","Courier Number (angle)",null,"3x00205",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,5,"IC Magnitude","Courier Number (current)",null,"3x00206","3x00207",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,6,"IC Phase Angle","Courier Number (angle)",null,"3x00208",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,7,"IN Measured Mag","Courier Number (current)",null,"3x00209","3x00210",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M5",null,"*"]
[2,8,"IN Measured Ang","Courier Number (angle)",null,"3x00211",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,9,"IN Derived Mag","Courier Number (current)",null,"3x00212","3x00213",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,"0A","IN Derived Angle","Courier Number (angle)",null,"3x00214",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,"0B","ISEF Magnitude","Courier Number (current)",null,"3x00215","3x00216",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M6",null,"*"]
[2,"0C","ISEF Angle","Courier Number (angle)",null,"3x00217",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,"0D","I1 Magnitude","Courier Number (current)",null,"3x00218","3x00219",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,"0E","I2 Magnitude","Courier Number (current)",null,"3x00220","3x00221",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,"0F","I0 Magnitude","Courier Number (current)",null,"3x00222","3x00223",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,10,"IA RMS","Courier Number (current)",null,"3x00224","3x00225",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,11,"IB RMS","Courier Number (current)",null,"3x00226","3x00227",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,12,"IC RMS","Courier Number (current)",null,"3x00228","3x00229",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[2,14,"VAB Magnitude","Courier Number (voltage)",null,"3x00230","3x00231",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,15,"VAB Phase Angle","Courier Number (angle)",null,"3x00232",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,16,"VBC Magnitude","Courier Number (voltage)",null,"3x00233","3x00234",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,17,"VBC Phase Angle","Courier Number (angle)",null,"3x00235",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,18,"VCA Magnitude","Courier Number (voltage)",null,"3x00236","3x00237",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,19,"VCA Phase Angle","Courier Number (angle)",null,"3x00238",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,"1A","VAN Magnitude","Courier Number (voltage)",null,"3x00239","3x00240",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,"1B","VAN Phase Angle","Courier Number (angle)",null,"3x00241",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,"1C","VBN Magnitude","Courier Number (voltage)",null,"3x00242","3x00243",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,"1D","VBN Phase Angle","Courier Number (angle)",null,"3x00244",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,"1E","VCN Magnitude","Courier Number (voltage)",null,"3x00245","3x00246",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,"1F","VCN Phase Angle","Courier Number (angle)",null,"3x00247",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,22,"VN Derived Mag","Courier Number (voltage)",null,"3x00248","3x00249",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M1",null,"*"]
[null,null,"VN Measured Mag",{"$nulls":17},"*",{"$nulls":6},"M3"]
[2,23,"VN Derived Ang","Courier Number (angle)",null,"3x00250",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":7},"*"]
[null,null,"VN Measured Ang",{"$nulls":17},"*"]
[2,24,"V1 Magnitude","Courier Number (voltage)",null,"3x00251","3x00252",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,25,"V2 Magnitude","Courier Number (voltage)",null,"3x00253","3x00254",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,26,"V0 Magnitude","Courier Number (voltage)",null,"3x00255","3x00256",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M1",null,"*"]
[{"$nulls":20},"*",{"$nulls":6},"M3"]
[2,27,"VAN RMS","Courier Number (voltage)",null,"3x00257","3x00258",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,28,"VBN RMS","Courier Number (voltage)",null,"3x00259","3x00260",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,29,"VCN RMS","Courier Number (voltage)",null,"3x00261","3x00262",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[2,"2D","Frequency","Courier Number (frequency)",null,"3x00263",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[2,"2E","C/S Voltage Mag","Courier Number (voltage)",null,"3x00264","3x00265",null,"G24",null,2,null,"Data",{"$nulls":6},"*",null,"*",{"$nulls":5},"M2",null,"*"]
[2,"2F","C/S Voltage Ang","Courier Number (angle)",null,"3x00266",null,null,"G30",null,1,null,"Data",{"$nulls":6},"*",null,"*",{"$nulls":7},"*"]
[2,30,"C/S Bus-Line Ang","Courier Number (angle)",null,"3x00267",null,null,"G30",null,1,null,"Data",{"$nulls":6},"*",null,"*","0923 = 1",{"$nulls":5},"Visible if System Checks enabled","*"]
[2,31,"Slip Frequency","Courier Number (frequency)",null,"3x00268",null,null,"G30",null,1,null,"Data",{"$nulls":6},"*",null,"*","0923 = 1",{"$nulls":5},"Visible if System Checks enabled","*"]
[2,40,"I1 Magnitude","Courier Number (current)",null,"3x00218","3x00219",null,"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4","Additional Measurements Phase 2.1"]
[2,41,"I1 Phase Angle","Courier Number (angle)",null,"3x00269",null,null,"G30",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Additional Measurements Phase 2.1"]
[2,42,"I2 Magnitude","Courier Number (current)",null,"3x00220","3x00221",null,"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4","Additional Measurements Phase 2.1"]
[2,43,"I2 Phase Angle","Courier Number (angle)",null,"3x00270",null,null,"G30",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Additional Measurements Phase 2.1"]
[2,44,"I0 Magnitude","Courier Number (current)",null,"3x00222","3x00223",null,"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4","Additional Measurements Phase 2.1"]
[2,45,"I0 Phase Angle","Courier Number (angle)",null,"3x00271",null,null,"G30",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Additional Measurements Phase 2.1"]
[2,46,"V1 Magnitude","Courier Number (voltage)",null,"3x00251","3x00252",null,"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1","Additional Measurements Phase 2.1"]
[2,47,"V1 Phase Angle","Courier Number (angle)",null,"3x00272",null,null,"G30",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Additional Measurements Phase 2.1"]
[2,48,"V2 Magnitude","Courier Number (voltage)",null,"3x00253","3x00254",null,"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1","Additional Measurements Phase 2.1"]
[2,49,"V2 Phase Angle","Courier Number (angle)",null,"3x00273",null,null,"G30",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Additional Measurements Phase 2.1"]
[2,"4A","V0 Magnitude","Courier Number (voltage)",null,"3x00255","3x00256",null,"G24",null,null,null,"Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":5},"M1","Additional Measurements Phase 2.1"]
[{"$nulls":20},"*",{"$nulls":6},"M3"]
[2,"4B","V0 Phase Angle","Courier Number (angle)",null,"3x00274",null,null,"G30",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Additional Measurements Phase 2.1"]
[3,0,"MEASUREMENTS 2",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[3,1,"A Phase Watts","Courier Number (power)",null,"3x00300","3x00302",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,2,"B Phase Watts","Courier Number (power)",null,"3x00303","3x00305",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,3,"C Phase Watts","Courier Number (power)",null,"3x00306","3x00308",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,4,"A Phase VArs","Courier Number (VAr)",null,"3x00309","3x00311",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,5,"B Phase VArs","Courier Number (VAr)",null,"3x00312","3x00314",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,6,"C Phase VArs","Courier Number (VAr)",null,"3x00315","3x00317",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,7,"A Phase VA","Courier Number (VA)",null,"3x00318","3x00320",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,8,"B Phase VA","Courier Number (VA)",null,"3x00321","3x00323",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,9,"C Phase VA","Courier Number (VA)",null,"3x00324","3x00326",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,"0A","3 Phase Watts","Courier Number (power)",null,"3x00327","3x00329",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,"0B","3 Phase VArs","Courier Number (VAr)",null,"3x00330","3x00332",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,"0C","3 Phase VA","Courier Number (VA)",null,"3x00333","3x00335",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4",null,"*"]
[3,"0E","3Ph Power Factor","Courier Number (decimal)",null,"3x00336",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[3,"0F","APh Power Factor","Courier Number (decimal)",null,"3x00337",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[3,10,"BPh Power Factor","Courier Number (decimal)",null,"3x00338",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[3,11,"CPh Power Factor","Courier Number (decimal)",null,"3x00339",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[3,12,"3Ph WHours Fwd","Courier Number (Wh)",null,"3x00340","3x00342",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase Watt - Hours (Forward)","*"]
[3,13,"3Ph WHours Rev","Courier Number (Wh)",null,"3x00343","3x00345",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase Watts - Hours (Reverse)","*"]
[3,14,"3Ph VArHours Fwd","Courier Number (VArh)",null,"3x00346","3x00348",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VAr - Hours (Forward)","*"]
[3,15,"3Ph VArHours Rev","Courier Number (VArh)",null,"3x00349","3x00351",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VAr - Hours (Reverse)","*"]
[3,16,"3Ph W Fix Demand","Courier Number (power)",null,"3x00352","3x00354",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase Watts - Fixed Demand","*"]
[3,17,"3Ph VArs Fix Dem","Courier Number (VAr)",null,"3x00355","3x00357",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArs - Fixed Demand","*"]
[3,18,"IA  Fixed Demand","Courier Number (current)",null,"3x00358","3x00359",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,19,"IB  Fixed Demand","Courier Number (current)",null,"3x00360","3x00361",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,"1A","IC  Fixed Demand","Courier Number (current)",null,"3x00362","3x00363",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,"1B","3 Ph W Roll Dem","Courier Number (power)",null,"3x00364","3x00366",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase Watts - Rolling Demand","*"]
[3,"1C","3Ph VArs RollDem","Courier Number (VAr)",null,"3x00367","3x00369",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArs - Rolling Demand","*"]
[3,"1D","IA Roll Demand","Courier Number (current)",null,"3x00370","3x00371",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,"1E","IB Roll Demand","Courier Number (current)",null,"3x00372","3x00373",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,"1F","IC Roll Demand","Courier Number (current)",null,"3x00374","3x00375",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,20,"3Ph W Peak Dem","Courier Number (power)",null,"3x00376","3x00378",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase Watts - Peak Demand","*"]
[3,21,"3Ph VAr Peak Dem","Courier Number (VAr)",null,"3x00379","3x00381",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArs - Peak Demand","*"]
[3,22,"IA Peak Demand","Courier Number (current)",null,"3x00382","3x00383",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,23,"IB Peak Demand","Courier Number (current)",null,"3x00384","3x00385",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,24,"IC Peak Demand","Courier Number (current)",null,"3x00386","3x00387",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[3,25,"Reset Demand","Indexed String",null,"4x00103",null,"G11","G11",null,null,"No","Command",0,1,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[{"$nulls":28},"South Park Modifications - Part 2"]
[{"$nulls":4},"N/A","3x00388","3x00389",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","A Phase Watts (see [0301]) "]
[{"$nulls":4},"N/A","3x00390","3x00391",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","B Phase Watts (see [0302]) "]
[{"$nulls":4},"N/A","3x00392","3x00393",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","C Phase Watts (see [0303]) "]
[{"$nulls":4},"N/A","3x00394","3x00395",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","A Phase VArs (see [0304]) "]
[{"$nulls":4},"N/A","3x00396","3x00397",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","B Phase VArs (see [0305]) "]
[{"$nulls":4},"N/A","3x00398","3x00399",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","C Phase VArs (see [0306]) "]
[{"$nulls":4},"N/A","3x00400","3x00401",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","A Phase VA (see [0307]) "]
[{"$nulls":4},"N/A","3x00402","3x00403",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","B Phase VA (see [0308]) "]
[{"$nulls":4},"N/A","3x00404","3x00405",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","C Phase VA (see [0309]) "]
[{"$nulls":4},"N/A","3x00406","3x00407",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase Watts (see [030A]) "]
[{"$nulls":4},"N/A","3x00408","3x00409",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArs (see [030B]) "]
[{"$nulls":4},"N/A","3x00410","3x00411",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VA (see [030C]) "]
[{"$nulls":4},"N/A","3x00412","3x00413",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase WHours Fwd (see [0312]) "]
[{"$nulls":4},"N/A","3x00414","3x00415",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase WHours Rev (see [0313]) "]
[{"$nulls":4},"N/A","3x00416","3x00417",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArHours Fwd (see [0314]) "]
[{"$nulls":4},"N/A","3x00418","3x00419",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArHours Rev (see [0315]) "]
[{"$nulls":4},"N/A","3x00420","3x00421",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase W Fix Demand (see [0316]) "]
[{"$nulls":4},"N/A","3x00422","3x00423",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArs Fix Demand (see [0317]) "]
[{"$nulls":4},"N/A","3x00424","3x00425",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase W Roll Demand (see [031B]) "]
[{"$nulls":4},"N/A","3x00426","3x00427",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArs Roll Demand (see [031C]) "]
[{"$nulls":4},"N/A","3x00428","3x00429",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase W Peak Demand (see [0320]) "]
[{"$nulls":4},"N/A","3x00430","3x00431",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1*M4","3 Phase VArs Peak Demand (see [0321]) "]
[4,0,"MEASUREMENTS 3",{"$nulls":14},"*","*","*","*","*"]
[4,1,"Highest Phase I","Courier Number (current)",null,"3x00432","3x00433",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
[4,2,"Thermal State","Courier Number (percentage)",null,"3x00434",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","(0917=1) && (3C01>=1)"]
[4,3,"Reset Thermal","Indexed String",null,"4x00104",null,"G11","G11",null,1,"No","Command",0,1,1,1,"*","*","*","*","*","(0917=1) && (3C01>=1)"]
[4,4,"IREF Diff","Courier Number (current)",null,"3x00435","3x00436",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(0915=1) && (3A01=5, 6 OR 7)",{"$nulls":4},"M4"]
[4,5,"IREF Bias","Courier Number (current)",null,"3x00437","3x00438",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(0915=1) && (3A01=5, 6 OR 7)",{"$nulls":4},"M4"]
[4,6,"Admittance SEF","Courier Number (inverse ohms)",null,"3x00439","3x00440",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(091B=1) && (4002=0)",{"$nulls":4},"M6/M1","In MODBUS represented in [mS]"]
[{"$nulls":20},"*",{"$nulls":6},"M6/M3"]
[4,7,"Conductance SEF","Courier Number (inverse ohms)",null,"3x00441","3x00442",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(091B=1) && (4002=0)",{"$nulls":4},"M6/M1","In MODBUS represented in [mS]"]
[{"$nulls":20},"*",{"$nulls":6},"M6/M3"]
[4,8,"Susceptance SEF","Courier Number (inverse ohms)",null,"3x00443","3x00444",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(091B=1) && (4002=0)",{"$nulls":4},"M6/M1","In MODBUS represented in [mS]"]
[{"$nulls":20},"*",{"$nulls":6},"M6/M3"]
[4,9,"Admittance E/F","Courier Number (inverse ohms)",null,"3x00445","3x00446",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(091B=1) && (4002=1)",{"$nulls":4},"M5/M1","In MODBUS represented in [mS]"]
[{"$nulls":20},"*",{"$nulls":6},"M5/M3"]
[4,"0A","Conductance E/F","Courier Number (inverse ohms)",null,"3x00447","3x00448",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(091B=1) && (4002=1)",{"$nulls":4},"M5/M1","In MODBUS represented in [mS]"]
[{"$nulls":20},"*",{"$nulls":6},"M5/M3"]
[4,"0B","Susceptance E/F","Courier Number (inverse ohms)",null,"3x00449","3x00450",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*",null,"*","(091B=1) && (4002=1)",{"$nulls":4},"M5/M1","In MODBUS represented in [mS]"]
[{"$nulls":20},"*",{"$nulls":6},"M5/M3"]
[4,"0C","I2/I1 Ratio","Courier Number (decimal)",null,"3x00451",null,null,"G30",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*"]
[4,"0D","SEF Power","Courier Number (power)",null,"3x00452","3x00453",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","(0915=1)&&",{"$nulls":4},"M3*M6"]
[{"$nulls":22},"((3A01=3) OR (3A01=7))",{"$nulls":5},"Note P144 has no 3A01=7 option"]
[4,"0E","df/dt","Courier Number (Hz/sec)",null,"3x00454","3x00455",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","(091F=1)",{"$nulls":5},"Did depend on 091C - now 091F"]
[4,"0F","IA 2ndHarm","Courier Number (percentage)",null,"3x00456",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*"]
[4,10,"IB 2ndHarm","Courier Number (percentage)",null,"3x00457",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*"]
[4,11,"IC 2ndHarm","Courier Number (percentage)",null,"3x00458",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*"]
[4,12,"APh Sen Watts","Courier Number (Power)",null,"3x00459","3x00460",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","(091C=1) && (4129=1)",{"$nulls":5},"Visible only when Sen power is enabled"]
[4,13,"APh Sen Vars","Courier Number (Var)",null,"3x00461","3x00462",null,"G125",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*","(091C=1) && (4129=1)",{"$nulls":5},"Visible only when Sen power is enabled"]
[4,14,"APh Power Angle","Courier Number (angle)",null,"3x00463",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","(091C=1) && (4129=1)",{"$nulls":5},"Visible only when Sen power is enabled"]
[5,0,"STAGE STATISTICS",{"$nulls":14},"*","*","*","*","*","927 = 1"]
[5,"01","Stg1 f+t Sta","Unsigned Integer (16 bits)",null,"3x00480",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 1"]
[5,"02","Stg1 f+t Trp","Unsigned Integer (16 bits)",null,"3x00481",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 1"]
[5,"03","Stg1 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00482",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 1"]
[5,"04","Stg1 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00483",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 1"]
[5,"05","Stg1 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00484",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 1"]
[5,"06","Stg1 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00485",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 1"]
[5,"07","Stg1 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00486",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 1"]
[5,"08","Stg1 Revn Date","IEC870 Date & Time",null,"3x00487","3x00490",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Date only of front panel, date and time over comms "]
["N/A",null,"Stg1 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1",{"$nulls":5},"Time only on front panel, not available over comms"]
[5,"0A","Stg2 f+t Sta","Unsigned Integer (16 bits)",null,"3x00491",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 2"]
[5,"0B","Stg2 f+t Trp","Unsigned Integer (16 bits)",null,"3x00492",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 2"]
[5,"0C","Stg2 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00493",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 2"]
[5,"0D","Stg2 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00494",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 2"]
[5,"0E","Stg2 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00495",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 2"]
[5,"0F","Stg2 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00496",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 2"]
[5,10,"Stg2 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00497",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 2"]
[5,11,"Stg2 Revn Date","IEC870 Date & Time",null,"3x00498","3x00501",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg2 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,13,"Stg3 f+t Sta","Unsigned Integer (16 bits)",null,"3x00502",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 3"]
[5,14,"Stg3 f+t Trp","Unsigned Integer (16 bits)",null,"3x00503",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 3"]
[5,15,"Stg3 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00504",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 3"]
[5,16,"Stg3 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00505",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 3"]
[5,17,"Stg3 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00506",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 3"]
[5,18,"Stg3 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00507",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 3"]
[5,19,"Stg3 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00508",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 3"]
[5,"1A","Stg3 Revn Date","IEC870 Date & Time",null,"3x00509","3x00512",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg3 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,"1C","Stg4 f+t Sta","Unsigned Integer (16 bits)",null,"3x00513",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 4"]
[5,"1D","Stg4 f+t Trp","Unsigned Integer (16 bits)",null,"3x00514",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 4"]
[5,"1E","Stg4 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00515",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 4"]
[5,"1F","Stg4 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00516",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 4"]
[5,20,"Stg4 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00517",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 4"]
[5,21,"Stg4 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00518",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 4"]
[5,22,"Stg4 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00519",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 4"]
[5,23,"Stg4 Revn Date","IEC870 Date & Time",null,"3x00520","3x00523",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg4 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,25,"Stg5 f+t Sta","Unsigned Integer (16 bits)",null,"3x00524",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 5"]
[5,26,"Stg5 f+t Trp","Unsigned Integer (16 bits)",null,"3x00525",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 5"]
[5,27,"Stg5 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00526",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 5"]
[5,28,"Stg5 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00527",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 5"]
[5,29,"Stg5 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00528",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 5"]
[5,"2A","Stg5 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00529",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 5"]
[5,"2B","Stg5 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00530",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 5"]
[5,"2C","Stg5 Revn Date","IEC870 Date & Time",null,"3x00531","3x00534",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg5 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,"2E","Stg6 f+t Sta","Unsigned Integer (16 bits)",null,"3x00535",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 6"]
[5,"2F","Stg6 f+t Trp","Unsigned Integer (16 bits)",null,"3x00536",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 6"]
[5,30,"Stg6 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00537",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 6"]
[5,31,"Stg6 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00538",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 6"]
[5,32,"Stg6 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00539",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 6"]
[5,33,"Stg6 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00540",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 6"]
[5,34,"Stg6 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00541",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 6"]
[5,35,"Stg6 Revn Date","IEC870 Date & Time",null,"3x00542","3x00545",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg6 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,37,"Stg7 f+t Sta","Unsigned Integer (16 bits)",null,"3x00546",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 7"]
[5,38,"Stg7 f+t Trp","Unsigned Integer (16 bits)",null,"3x00547",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 7"]
[5,39,"Stg7 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00548",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 7"]
[5,"3A","Stg7 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00549",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 7"]
[5,"3B","Stg7 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00550",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 7"]
[5,"3C","Stg7 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00551",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 7"]
[5,"3D","Stg7 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00552",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 7"]
[5,"3E","Stg7 Revn Date","IEC870 Date & Time",null,"3x00553","3x00556",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg7 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,40,"Stg8 f+t Sta","Unsigned Integer (16 bits)",null,"3x00557",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 8"]
[5,41,"Stg8 f+t Trp","Unsigned Integer (16 bits)",null,"3x00558",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 8"]
[5,42,"Stg8 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00559",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 8"]
[5,43,"Stg8 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00560",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 8"]
[5,44,"Stg8 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00561",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 8"]
[5,45,"Stg8 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00562",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 8"]
[5,46,"Stg8 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00563",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 8"]
[5,47,"Stg8 Revn Date","IEC870 Date & Time",null,"3x00564","3x00567",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg8 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,49,"Stg9 f+t Sta","Unsigned Integer (16 bits)",null,"3x00568",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t starts for Stage 9"]
[5,"4A","Stg9 f+t Trp","Unsigned Integer (16 bits)",null,"3x00569",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+t trips for Stage 9"]
[5,"4B","Stg9 f+df/dt Trp","Unsigned Integer (16 bits)",null,"3x00570",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+df/dt trips for Stage 9"]
[5,"4C","Stg9 df/dt+t Sta","Unsigned Integer (16 bits)",null,"3x00571",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt+t starts for Stage 9"]
[5,"4D","Stg9 df/dt+t Trp","Unsigned Integer (16 bits)",null,"3x00572",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of df/dt trips for Stage 9"]
[5,"4E","Stg9 f+Df/Dt Sta","Unsigned Integer (16 bits)",null,"3x00573",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT starts for Stage 9"]
[5,"4F","Stg9 f+Df/Dt Trp","Unsigned Integer (16 bits)",null,"3x00574",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1",{"$nulls":5},"Number of f+DF/DT trips for Stage 9"]
[5,50,"Stg9 Revn Date","IEC870 Date & Time",null,"3x00575","3x00578",null,"G12",null,4,null,"Data",{"$nulls":4},"*","*","*","*","*","927 = 1"]
["N/A",null,"Stg9 Revn Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*","927 = 1"]
[5,52,"Reset Statistics","Indexed String",null,"4x00105",null,"G155","G1",null,1,"No Operation","Command",0,10,1,2,"*","*","*","*","*","927 = 1",{"$nulls":5},"Reset stage statistics"]
[6,0,"CB CONDITION",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"CB CONDITION MONITORING","*"]
[6,1,"CB Operations","Unsigned Integer (16 bits)",null,"3x00600",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Number of Circuit Breaker Operations","*"]
[6,2,"Total IA Broken","Courier Number (current)",null,"3x00601","3x00602",null,"G24",null,2,null,"Data","NM1",null,null,null,"*","*","*","*","*",{"$nulls":5},"M4^1001","Broken Current A Phase","*"]
[6,3,"Total IB Broken","Courier Number (current)",null,"3x00603","3x00604",null,"G24",null,2,null,"Data","NM1",null,null,null,"*","*","*","*","*",{"$nulls":5},"M4^1001","Broken Current B Phase","*"]
[6,4,"Total IC Broken","Courier Number (current)",null,"3x00605","3x00606",null,"G24",null,2,null,"Data","NM1",null,null,null,"*","*","*","*","*",{"$nulls":5},"M4^1001","Broken Current C Phase","*"]
[6,5,"CB Operate Time","Courier Number (time)",null,"3x00607",null,null,"G25",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Circuit Breaker operating time","*"]
[6,6,"Reset CB Data","Indexed String",null,"4x00150",null,"G11","G11",null,1,"No","Command",0,1,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,"Reset All Values","*"]
[7,0,"CB CONTROL",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[7,1,"CB Control by","Indexed String",null,"4x00200",null,"G99","G99",null,1,"Disabled","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[7,2,"Close Pulse Time","Courier Number (time)",null,"4x00201",null,null,"G2",49,1,0.5,"Setting",0.1,10,0.01,2,"*","*","*","*","*","0701 <> 0",{"$nulls":6},"*"]
[7,3,"Trip Pulse Time","Courier Number (time)",null,"4x00202",null,null,"G2",49,1,0.5,"Setting",0.1,5,0.01,2,"*","*","*","*","*","0701 <> 0",{"$nulls":6},"*"]
[7,5,"Man Close Delay","Courier Number (time)",null,"4x00203",null,null,"G2",59999,1,10,"Setting",0.01,600,0.01,2,"*","*","*","*","*","0701 <> 0",{"$nulls":5},"Manual Close Delay","*"]
[7,6,"CB Healthy Time","Courier Number (time)",null,"4x00204","4x00205",null,"G35","1E06",2,5,"Setting",0.01,9999,0.01,2,"*","*","*","*","*","0701 <> 0",{"$nulls":5},"CB Healthy Window","*"]
[7,7,"Sys Check Time","Courier Number (time)",null,"4x00206","4x00207",null,"G35","1E06",2,5,"Setting",0.01,9999,0.01,2,null,null,"*","*","*","0701 <> 0",{"$nulls":5},"System Checks OK Window","*"]
[7,8,"Lockout Reset","Indexed String",null,"4x00208",null,"G11","G11",59999,1,"No","Command",0,1,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[7,9,"Reset Lockout by","Indexed String",null,"4x00209",null,"G81","G81",59999,1,"CB Close","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[7,"0A","Man Close RstDly","Courier Number (time)",null,"4x00210",null,null,"G2",59999,1,5,"Setting",0.1,600,0.01,2,"*","*","*","*","*","0709 = 1",{"$nulls":5},"Manual Close Reset Delay","*"]
[7,"0B","Autoreclose Mode","Indexed String",null,"4x00211",null,"G78","G78",59999,1,"No Operation","Command",0,2,1,2,null,"*","*","*","*","0924 = 1",null,null,null,"*",null,"Command AR In/Out of Service","*"]
[7,"0E","AR Status","Indexed String",null,"3x00608",null,"G83","G83",59999,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":6},"*"]
[7,"0F","Total Reclosures","Unsigned Integer (16 bits)",null,"3x00609",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of Autoreclosures","*"]
[7,10,"Reset Total AR","Indexed String",null,"4x00212",null,"G11","G11",null,1,"No","Command",0,1,1,2,null,"*","*","*","*","0924 = 1",null,null,null,"*",null,"Reset AR Counters"]
[7,11,"CB Status Input","Indexed String",null,"4x00213",null,"G118","G118",null,1,"None","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"52A and 52B Logic Input Assignment "]
[7,12,"1 Shot Clearance","Unsigned Integer (16 bits)",null,"3x00610",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of successful clearances after 1 shot"]
[7,13,"2 Shot Clearance","Unsigned Integer (16 bits)",null,"3x00611",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of successful clearances after 2 shots"]
[7,14,"3 Shot Clearance","Unsigned Integer (16 bits)",null,"3x00612",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of successful clearances after 3 shots"]
[7,15,"4 Shot Clearance","Unsigned Integer (16 bits)",null,"3x00613",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of successful clearances after 4 shots"]
[7,16,"Persistent Fault","Unsigned Integer (16 bits)",null,"3x00614",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of unsuccessful clearances with AR going to lockout"]
[7,20,"Shot1 Recloses","Unsigned Integer (16 bits)",null,"3x00615",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of 1 shot reclose attempts "]
[7,21,"Shot234 Recloses","Unsigned Integer (16 bits)",null,"3x00616",null,null,"G1",null,1,null,"Data",{"$nulls":5},"*","*","*","*","0924 = 1",{"$nulls":5},"Total number of 2, 3, 4 shot reclose attempts"]
[8,0,"DATE AND TIME",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[8,1,"Date/Time","IEC870 Date & Time","N/A","4x00300","4x00303",null,"G12",null,4,null,"Setting",null,null,null,0,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[null,"N/A","Date",{"$nulls":25},"Front Panel Menu only"]
[null,null,"1998-01-12"]
[null,"N/A","Time",{"$nulls":25},"Front Panel Menu only"]
[null,null,"12:00:00"]
[8,4,"IRIG-B Sync","Indexed String",null,"4x00304",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","IRIG-B Fitted",{"$nulls":6},"*"]
[8,5,"IRIG-B Status","Indexed String",null,"3x00090",null,"G17","G17",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*","0804 = 1 ",null,null,null,"*",null,null,"*"]
[8,6,"Battery Status","Indexed String",null,"3x00091",null,"G59","G59",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[8,7,"Battery Alarm","Indexed String",null,"4x00305",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[8,13,"SNTP Status","Indexed String",null,null,null,"G247",{"$nulls":4},"Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850/DNP3oe",{"$nulls":6},"*"]
[8,20,"LocalTime Enable","Indexed String",null,null,null,"G254",null,null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Local Time","*"]
[8,21,"LocalTime Offset","Courier Number (minutes)",{"$nulls":7},0,"Setting",-720,720,15,2,"*","*","*","*","*","[0820]>0",{"$nulls":5},"Local Time","*"]
[8,22,"DST Enable","Indexed String",null,null,null,"G37",null,null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*","[0820]>0",{"$nulls":5},"Local Time","*"]
[8,23,"DST Offset","Courier Number (minutes)",{"$nulls":7},"60 mins","Setting",30,60,30,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,24,"DST Start","Indexed String",null,null,null,"G252",null,null,null,"Last","Setting",0,4,1,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,25,"DST Start Day","Indexed String",null,null,null,"G250",null,null,null,"Sunday","Setting",0,6,1,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,26,"DST Start Month","Indexed String",null,null,null,"G251",null,null,null,"March","Setting",0,11,1,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,27,"DST Start Mins","Courier Number (minutes)",{"$nulls":7},60,"Setting",0,1425,15,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,28,"DST End","Indexed String",null,null,null,"G252",null,null,null,"Last","Setting",0,1,4,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,29,"DST End Day","Indexed String",null,null,null,"G250",null,null,null,"Sunday","Setting",0,1,1,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,"2A","DST End Month","Indexed String",null,null,null,"G251",null,null,null,"October","Setting",0,11,1,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,"2B","DST End Mins","Courier Number (minutes)",{"$nulls":7},60,"Setting",0,1425,15,2,"*","*","*","*","*","[0820]>0 AND [0822]>0",{"$nulls":5},"Local Time","*"]
[8,30,"RP1 Time Zone","Indexed String",null,null,null,"G253",null,null,null,"Local","Setting",0,1,1,2,"*","*","*","*","*","[0820]>1",{"$nulls":5},"Local Time and RP1 protocol","*"]
[8,31,"RP2 Time Zone","Indexed String",null,null,null,"G253",null,null,null,"Local","Setting",0,1,1,2,"*","*","*","*","*","[0820]>1",{"$nulls":5},"Local Time and RP2 protocol","*"]
[8,32,"DNPOE Time Zone","Indexed String",null,null,null,"G253",null,null,null,"Local","Setting",0,1,1,2,"*","*","*","*","*","[0820]>1",{"$nulls":5},"Local Time and DNP3 over ethernet","*"]
[8,33,"Tunnel Time Zone","Indexed String",null,null,null,"G253",null,null,null,"Local","Setting",0,1,1,2,"*","*","*","*","*","[0820]>1",{"$nulls":5},"Local Time and tunnelled Courier","*"]
[null,"N/A","Date & Time","IEC870 Date & Time",null,"4x02049","4x02052",null,"G12",null,4,null,"Setting",null,null,null,0,"*","*","*","*","*",{"$nulls":6},"Duplicate time synch for Sincor","*"]
[9,0,"CONFIGURATION",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[9,1,"Restore Defaults","Indexed String",null,"4x00402",null,"G53","G53",null,null,"No Operation","Command",0,5,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[9,2,"Setting Group","Indexed String",null,"4x00403",null,"G61","G61",null,null,"Select via Menu","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,3,"Active Settings","Indexed String",null,"4x00404",null,"G90","G90",null,null,"Group 1","Setting",0,3,1,1,"*","*","*","*","*","0902 = 0",{"$nulls":6},"*"]
[9,4,"Save Changes","Indexed String",null,"4x00405",null,"G62","G62",null,null,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[9,5,"Copy From","Indexed String",null,"4x00406",null,"G90","G90",null,null,"Group 1","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[9,6,"Copy To","Indexed String",null,"4x00407",null,"G98","G98",null,null,"No Operation","Command",0,3,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[9,7,"Setting Group 1","Indexed String",null,"4x00408",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,8,"Setting Group 2","Indexed String",null,"4x00409",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,9,"Setting Group 3","Indexed String",null,"4x00410",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"0A","Setting Group 4","Indexed String",null,"4x00411",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"0B","System Config","Indexed String",null,"4x00433",null,"G80","G80",null,null,"Invisible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,10,"Overcurrent","Indexed String",null,"4x00412",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,11,"Neg Sequence O/C","Indexed String",null,"4x00413",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,12,"Broken Conductor","Indexed String",null,"4x00414",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,13,"Earth Fault 1","Indexed String",null,"4x00415",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,14,"Earth Fault 2","Indexed String",null,"4x00416",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,15,"SEF/REF Prot'n","Indexed String",null,"4x00417",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*",null,"*",{"$nulls":7},"*"]
[null,null,"SEF Protection","Indexed String",null,"4x00417",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,null,null,null,"*"]
[9,16,"Residual O/V NVD","Indexed String",null,"4x00418",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Residual Overvoltage","*"]
[9,17,"Thermal Overload","Indexed String",null,"4x00419",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,18,"Neg Sequence O/V","Indexed String",null,"4x00420",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,19,"Cold Load Pickup","Indexed String",null,"4x00421",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"1A","Selective Logic","Indexed String",null,"4x00422",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"1B","Admit Protection","Indexed String",null,"4x00423",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"1C","Power Protection","Indexed String",null,"4x00434",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Power Protection - 4 stages 2 stages over power and 2 underpower ","*"]
[9,"1D","Volt Protection","Indexed String",null,"4x00424",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"1E","Freq Protection","Indexed String",null,"4x00425",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,20,"CB Fail","Indexed String",null,"4x00426",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,21,"Supervision","Indexed String",null,"4x00427",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,22,"Fault Locator","Indexed String",null,"4x00428",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[9,23,"System Checks","Indexed String",null,"4x00429",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,null,null,"*","*","*",{"$nulls":7},"*"]
[9,24,"Auto-Reclose","Indexed String",null,"4x00430",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":7},"*"]
[9,25,"Input Labels","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,26,"Output Labels","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,27,"Adv. Freq Prot'n","Indexed String",null,"4x00434",null,"G37",null,null,null,"Disabled","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":7},"*"]
[9,28,"CT & VT Ratios","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,29,"Record Control","Indexed String",null,null,null,"G80",null,null,null,"Invisible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"2A","Disturb Recorder","Indexed String",null,null,null,"G80",null,null,null,"Invisible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":6},"Disturbance recorder","*"]
[9,"2B","Measure't Setup","Indexed String",null,null,null,"G80",null,null,null,"Invisible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"2C","Comms Settings","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"2D","Commission Tests","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,"2E","Setting Values","Indexed String",null,null,null,"G54",null,null,null,"Primary","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":6},"Delete MODBUS Address","*"]
[9,"2F","Control Inputs","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Phase 2.1 Modification","*"]
[9,35,"Ctrl I/P Config","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,36,"Ctrl I/P Labels","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,39,"Direct Access","Indexed String",null,null,null,"G231",null,null,null,"Enabled","Setting",0,3,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[9,39,"Direct Access","Indexed String",null,null,null,"G231",null,null,null,"Enabled","Setting",0,3,1,1,{"$nulls":11},"Chinese Build - cell not available","*"]
[9,40,"InterMiCOM","Indexed String",null,"4x00440",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM - ZN0025 required in slot A","*"]
[9,49,"IEC GOOSE","Indexed String",null,null,null,"G80",null,null,null,"Visible","Setting",0,1,1,1,{"$nulls":4},"*","Build = IEC61850",{"$nulls":6},"*"]
[9,50,"Function Key","Indexed String",null,"4x00432",null,"G80",null,null,null,"Visible","Setting",0,1,1,1,{"$nulls":4},"*",{"$nulls":7},"*"]
[{"$nulls":7},"G37","G37"]
[9,"FB","RP1 Read Only","Indexed String",null,"NA",null,"G37","NA",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Enable Remote Read Only Mode on RP1 courier or CS103","*","*"]
[9,"FC","RP2 Read Only","Indexed String",null,"NA",null,"G37","NA",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Enable Remote Read Only Mode on RP2 courier ","*","*"]
[9,"FD","NIC Read Only","Indexed String",null,"NA",null,"G37","NA",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Enable Remote Read Only Mode on Tunnelled courier","*","*"]
[9,"FF","LCD Contrast","Unsigned Integer (16 bits)",{"$nulls":7},11,"Setting",0,31,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
[{"$nulls":5},"4x00400",null,null,"G18",null,1,{"$nulls":17},"Record Selection Command register"]
[{"$nulls":5},"4x00401",null,null,"G6",null,1,{"$nulls":17},"Record Control Command register"]
["0A",0,"CT AND VT RATIOS",{"$nulls":14},"*","*","*","*","*","0928 = 1 ",{"$nulls":5},"values for multiplier see mult column","*"]
["0A",1,"Main VT Primary","Courier Number (voltage)",null,"4x00500","4x00501",null,"G35",999900,2,110,"Setting",100,1000000,1,2,"*","*","*","*","*",{"$nulls":6},"Label V1 = Main VT Rating/110","*"]
["0A",2,"Main VT Sec'y","Courier Number (voltage)",null,"4x00502",null,null,"G2",340,1,110,"Setting","80*V1","140*V1","1*V1",2,"*","*","*","*","*",{"$nulls":6},"Label M1 = 0A01/0A02","*"]
["0A",3,"C/S VT Primary","Courier Number (voltage)",null,"4x00503","4x00504",null,"G35",999900,2,110,"Setting",100,1000000,1,2,null,null,"*",null,"*",{"$nulls":6},"Label V2 = C/S VT Rating/110","*"]
["0A",4,"C/S VT Secondary","Courier Number (voltage)",null,"4x00505",null,null,"G2",340,1,110,"Setting","80*V2","140*V2","1*V2",2,null,null,"*",null,"*",{"$nulls":6},"Check Sync VT Secondary","*"]
[{"$nulls":28},"Label M2 = 0A03/0A04"]
["0A",5,"NVD VT Primary","Courier Number (voltage)",null,"4x00514","4x00515",null,"G35",999900,2,440,"Setting",100,1000000,1,2,null,null,null,"*",{"$nulls":7},"Label V3 = NVD VT Rating/110"]
["0A",6,"NVD VT Secondary","Courier Number (voltage)",null,"4x00516",null,null,"G2",340,1,440,"Setting","80*V3","140*V3","1*V3",2,null,null,null,"*",{"$nulls":7},"NVD VT Secondary"]
[{"$nulls":28},"Label M3 = 0A05/0A06"]
["0A",7,"Phase CT Primary","Courier Number (current)",null,"4x00506",null,null,"G2",29999,1,1,"Setting",1,30000,1,2,"*","*","*","*","*",{"$nulls":6},"Label I1 = Phase CT secondary rating","*"]
["0A",8,"Phase CT Sec'y","Courier Number (current)",null,"4x00507",null,null,"G2",null,1,1,"Setting",1,5,4,2,"*","*","*","*","*",{"$nulls":6},"Label M4 = 0A07/0A08","*"]
["0A",9,"E/F CT Primary","Courier Number (current)",null,"4x00508",null,null,"G2",29999,1,1,"Setting",1,30000,1,2,"*","*","*","*","*",{"$nulls":6},"Label I2 = E/F CT secondary rating","*"]
["0A","0A","E/F CT Secondary","Courier Number (current)",null,"4x00509",null,null,"G2",null,1,1,"Setting",1,5,4,2,"*","*","*","*","*",{"$nulls":6},"Label M5 = 0A09/0A0A","*"]
["0A","0B","SEF CT Primary","Courier Number (current)",null,"4x00510",null,null,"G2",29999,1,1,"Setting",1,30000,1,2,"*","*","*","*","*",{"$nulls":6},"Label I3 = SEF CT secondary rating","*"]
["0A","0C","SEF CT Secondary","Courier Number (current)",null,"4x00511",null,null,"G2",null,1,1,"Setting",1,5,4,2,"*","*","*","*","*",{"$nulls":6},"Label M6 = 0A0B/0A0C","*"]
[{"$nulls":28},"Label NM1 = 0A08^1001"]
["0A","0F","C/S Input","Indexed String",null,"4x00512",null,"G40","G40",null,1,"A-N","Setting",0,5,1,2,null,null,"*",null,"*"]
["0A",10,"Main VT Location","Indexed String",null,"4x00513",null,"G89","G89",null,1,"Line","Setting",0,1,1,2,null,null,"*",null,"*"]
["0A",11,"I Derived Phase","Indexed String",null,"4x00517",null,"G121","G121",null,1,"IB","Setting",0,3,1,2,null,null,null,"*",{"$nulls":7},"Label NM1 = 0A08^1001"]
["0A",14,"C/S V kSM","Courier Number (decimal)",null,"4x00518",null,null,"G2",null,1,1,"Setting",0.1,5,0.001,2,null,null,"*",null,"*"]
["0A",15,"C/S Phase kSA","Courier Number (angle)",null,"4x00519",null,null,"G2",null,1,0,"Setting",-150,180,30,2,null,null,"*",null,"*"]
["0B",0,"RECORD CONTROL",{"$nulls":14},"*","*","*","*","*","0929 = 1",{"$nulls":6},"*"]
["0B",1,"Clear Events","Indexed String",null,null,null,"G11",null,null,null,"No","Command",0,1,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
["0B",2,"Clear Faults","Indexed String",null,null,null,"G11",null,null,null,"No","Command",0,1,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
["0B",3,"Clear Maint","Indexed String",null,null,null,"G11",null,null,null,"No","Command",0,1,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
["0B",4,"Alarm Event","Indexed String",null,"4x19000",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0B",5,"Relay O/P Event","Indexed String",null,"4x19001",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0B",6,"Opto Input Event","Indexed String",null,"4x19002",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0B",7,"General Event","Indexed String",null,"4x19003",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0B",8,"Fault Rec Event","Indexed String",null,"4x19004",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0B",9,"Maint Rec Event","Indexed String",null,"4x19005",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0B","0A","Protection Event","Indexed String",null,"4x19006",null,"G37","G37",null,null,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0B",30,"Clear Dist Recs","Indexed String",null,null,null,"G11",null,null,null,"No","Command",0,1,1,1,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
["0B",40,"DDB 31 - 0","Binary Flag (32 bits)",null,"4x19007","4x19008","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",41,"DDB 63 - 32","Binary Flag (32 bits)",null,"4x19009","4x19010","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",42,"DDB 95 - 64","Binary Flag (32 bits)",null,"4x19011","4x19012","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",43,"DDB 127 - 96","Binary Flag (32 bits)",null,"4x19013","4x19014","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",44,"DDB 159 - 128","Binary Flag (32 bits)",null,"4x19015","4x19016","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",45,"DDB 191 - 160","Binary Flag (32 bits)",null,"4x19017","4x19018","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",46,"DDB 223 - 192","Binary Flag (32 bits)",null,"4x19019","4x19020","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",47,"DDB 255 - 224","Binary Flag (32 bits)",null,"4x19021","4x19022","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",48,"DDB 287 - 256","Binary Flag (32 bits)",null,"4x19023","4x19024","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",49,"DDB 319 - 288","Binary Flag (32 bits)",null,"4x19025","4x19026","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","4A","DDB 351 - 320","Binary Flag (32 bits)",null,"4x19027","4x19028","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","4B","DDB 383 - 352","Binary Flag (32 bits)",null,"4x19029","4x19030","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","4C","DDB 415 - 384","Binary Flag (32 bits)",null,"4x19031","4x19032","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","4D","DDB 447 - 416","Binary Flag (32 bits)",null,"4x19033","4x19034","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","4E","DDB 479 - 448","Binary Flag (32 bits)",null,"4x19035","4x19036","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","4F","DDB 511 - 480","Binary Flag (32 bits)",null,"4x19037","4x19038","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",50,"DDB 543 - 512","Binary Flag (32 bits)",null,"4x19039","4x19040","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",51,"DDB 575 - 544","Binary Flag (32 bits)",null,"4x19041","4x19042","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",52,"DDB 607 - 576","Binary Flag (32 bits)",null,"4x19043","4x19044","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",53,"DDB 639 - 608","Binary Flag (32 bits)",null,"4x19045","4x19046","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",54,"DDB 671 - 640","Binary Flag (32 bits)",null,"4x19047","4x19048","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",55,"DDB 703 - 672","Binary Flag (32 bits)",null,"4x19049","4x19050","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",56,"DDB 735 - 704","Binary Flag (32 bits)",null,"4x19051","4x19052","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",57,"DDB 767 - 736","Binary Flag (32 bits)",null,"4x19053","4x19054","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",58,"DDB 799 - 768","Binary Flag (32 bits)",null,"4x19055","4x19056","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",59,"DDB 831 - 800","Binary Flag (32 bits)",null,"4x19057","4x19058","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","5A","DDB 863 - 832","Binary Flag (32 bits)",null,"4x19059","4x19060","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","5B","DDB 895 - 864","Binary Flag (32 bits)",null,"4x19061","4x19062","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","5C","DDB 927 - 896","Binary Flag (32 bits)",null,"4x19063","4x19064","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","5D","DDB 959 - 928","Binary Flag (32 bits)",null,"4x19065","4x19066","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","5E","DDB 991 - 960","Binary Flag (32 bits)",null,"4x19067","4x19068","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B","5F","DDB 1023 - 992","Binary Flag (32 bits)",null,"4x19069","4x19070","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",60,"DDB 1055 - 1024","Binary Flag (32 bits)",null,"4x19071","4x19072","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",61,"DDB 1087 - 1056","Binary Flag (32 bits)",null,"4x19073","4x19074","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",62,"DDB 1119 - 1088","Binary Flag (32 bits)",null,"4x19075","4x19076","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",63,"DDB 1151 - 1120","Binary Flag (32 bits)",null,"4x19077","4x19078","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",64,"DDB 1183 - 1152","Binary Flag (32 bits)",null,"4x19079","4x19080","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",65,"DDB 1215 - 1184","Binary Flag (32 bits)",null,"4x19081","4x19082","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",66,"DDB 1247 - 1216","Binary Flag (32 bits)",null,"4x19083","4x19084","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0B",67,"DDB 1279 - 1248","Binary Flag (32 bits)",null,"4x19085","4x19086","G27","G27",null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0B0A = 1",{"$nulls":6},"*"]
["0C",0,"DISTURB RECORDER",{"$nulls":14},"*","*","*","*","*","092A = 1",{"$nulls":5},"DISTURBANCE RECORDER","*"]
["0C",1,"Duration","Courier Number (time)",null,"4x00600",null,null,"G2",1050,1,1.5,"Setting",0.1,10.5,0.01,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0C",2,"Trigger Position","Courier Number (percentage)",null,"4x00601",null,null,"G2",1050,1,33.3,"Setting",0,100,0.1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0C",3,"Trigger Mode","Indexed String",null,"4x00602",null,"G34","G34",null,1,"Single",null,0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0C",4,"Analog Channel 1","Indexed String",null,"4x00603",null,"G31","G31",null,1,"VA","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1 ","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C",5,"Analog Channel 2","Indexed String",null,"4x00604",null,"G31","G31",null,1,"VB","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1 ","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C",6,"Analog Channel 3","Indexed String",null,"4x00605",null,"G31","G31",null,1,"VC","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C",7,"Analog Channel 4","Indexed String",null,"4x00606",null,"G31","G31",null,1,"IA","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C",8,"Analog Channel 5","Indexed String",null,"4x00607",null,"G31","G31",null,1,"IB","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1 ","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C",9,"Analog Channel 6","Indexed String",null,"4x00608",null,"G31","G31",null,1,"IC","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C","0A","Analog Channel 7","Indexed String",null,"4x00609",null,"G31","G31",null,1,"IN","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C","0B","Analog Channel 8","Indexed String",null,"4x00610",null,"G31","G31",null,1,"IN Sensitive","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},7,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},8,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},8,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C","0C","Analog Channel 9","Indexed String",null,"4x00611",null,"G31","G31",null,1,"Frequency","Setting",0,null,1,2,"*","*","*","*","*",{"$nulls":6},"MaxAC : Max = 7 for Model1","*"]
[{"$nulls":7},"G31-1","G31-1",{"$nulls":5},9,null,null,"*","*"]
[{"$nulls":7},"G31-2","G31-2",{"$nulls":5},10,{"$nulls":4},"*",null,"*"]
[{"$nulls":7},"G31-3","G31-3",{"$nulls":5},10,{"$nulls":5},"*",{"$nulls":7},"7 for Model2, 8 for Model3"]
["0C","0D","Digital Input 1","Indexed String",null,"4x00611",null,"G32","G32",null,1,"Relay 1","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
["0C","0E","Input 1 Trigger","Indexed String",null,"4x00612",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C0C <> Unassigned "]
["0C","0F","Digital Input 2","Indexed String",null,"4x00613",null,"G32","G32",null,1,"Relay 2","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
["0C",10,"Input 2 Trigger","Indexed String",null,"4x00614",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C0E <> Unassigned"]
["0C",11,"Digital Input 3","Indexed String",null,"4x00615",null,"G32","G32",null,1,"Relay 3","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
["0C",12,"Input 3 Trigger","Indexed String",null,"4x00616",null,"G66","G66",null,1,"Trigger L/H","Setting",0,2,1,2,"*","*","*","*","*","0C10 <> Unassigned"]
["0C",13,"Digital Input 4","Indexed String",null,"4x00617",null,"G32","G32",null,1,"Relay 4","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
["0C",14,"Input 4 Trigger","Indexed String",null,"4x00618",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C12 <> Unassigned"]
["0C",15,"Digital Input 5","Indexed String",null,"4x00619",null,"G32","G32",null,1,"Relay 5","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
["0C",16,"Input 5 Trigger","Indexed String",null,"4x00620",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C14 <> Unassigned"]
["0C",17,"Digital Input 6","Indexed String",null,"4x00621",null,"G32","G32",null,1,"Relay 6","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
["0C",18,"Input 6 Trigger","Indexed String",null,"4x00622",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C16 <> Unassigned"]
["0C",19,"Digital Input 7","Indexed String",null,"4x00623",null,"G32","G32",null,1,"Relay 7","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
["0C","1A","Input 7 Trigger","Indexed String",null,"4x00624",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C18 <> Unassigned"]
["0C","1B","Digital Input 8","Indexed String",null,"4x00625",null,"G32","G32",null,1,"Opto Input 1","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Relay 8",{"$nulls":7},"*",null,"*"]
["0C","1C","Input 8 Trigger","Indexed String",null,"4x00626",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C1A <> Unassigned"]
["0C","1D","Digital Input 9","Indexed String",null,"4x00627",null,"G32","G32",null,1,"Opto Input 2","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Relay 9",{"$nulls":7},"*",null,"*"]
["0C","1E","Input 9 Trigger","Indexed String",null,"4x00628",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C1C <> Unassigned","<>","Unassigned"]
["0C","1F","Digital Input 10","Indexed String",null,"4x00629",null,"G32","G32",null,1,"Opto Input 3","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Relay 10",{"$nulls":7},"*",null,"*"]
["0C",20,"Input 10 Trigger","Indexed String",null,"4x00630",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C1E <> Unassigned","<>","Unassigned"]
["0C",21,"Digital Input 11","Indexed String",null,"4x00631",null,"G32","G32",null,1,"Opto Input 4","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Relay 11",{"$nulls":7},"*",null,"*"]
["0C",22,"Input 11 Trigger","Indexed String",null,"4x00632",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C20 <> Unassigned","<>","Unassigned"]
["0C",23,"Digital Input 12","Indexed String",null,"4x00633",null,"G32","G32",null,1,"Opto Input 5","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Relay 12",{"$nulls":7},"*",null,"*"]
["0C",24,"Input 12 Trigger","Indexed String",null,"4x00634",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C22 <> Unassigned","<>","Unassigned"]
["0C",25,"Digital Input 13","Indexed String",null,"4x00635",null,"G32","G32",null,1,"Opto Input 6","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Relay 13",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 1",{"$nulls":9},"*"]
["0C",26,"Input 13 Trigger","Indexed String",null,"4x00636",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C24 <> Unassigned","<>","Unassigned"]
["0C",27,"Digital Input 14","Indexed String",null,"4x00637",null,"G32","G32",null,1,"Opto Input 7","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Relay 14",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 2",{"$nulls":9},"*"]
["0C",28,"Input 14 Trigger","Indexed String",null,"4x00638",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C26 <> Unassigned","<>","Unassigned"]
["0C",29,"Digital Input 15","Indexed String",null,"4x00639",null,"G32","G32",null,1,"Opto Input 8","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 1",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 3",{"$nulls":9},"*"]
["0C","2A","Input 15 Trigger","Indexed String",null,"4x00640",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C28 <> Unassigned","<>","Unassigned"]
["0C","2B","Digital Input 16","Indexed String",null,"4x00641",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 2",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 4",{"$nulls":9},"*"]
["0C","2C","Input 16 Trigger","Indexed String",null,"4x00642",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C2A <> Unassigned","<>","Unassigned"]
["0C","2D","Digital Input 17","Indexed String",null,"4x00643",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 3",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 5",{"$nulls":9},"*"]
["0C","2E","Input 17 Trigger","Indexed String",null,"4x00644",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C2C <> Unassigned","<>","Unassigned"]
["0C","2F","Digital Input 18","Indexed String",null,"4x00645",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 4",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 6",{"$nulls":9},"*"]
["0C",30,"Input 18 Trigger","Indexed String",null,"4x00646",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C2E <> Unassigned","<>","Unassigned"]
["0C",31,"Digital Input 19","Indexed String",null,"4x00647",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 5",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 7",{"$nulls":9},"*"]
["0C",32,"Input 19 Trigger","Indexed String",null,"4x00648",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C30 <> Unassigned","<>","Unassigned"]
["0C",33,"Digital Input 20","Indexed String",null,"4x00649",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 6",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 8",{"$nulls":9},"*"]
["0C",34,"Input 20 Trigger","Indexed String",null,"4x00650",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C32 <> Unassigned","<>","Unassigned"]
["0C",35,"Digital Input 21","Indexed String",null,"4x00651",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 7",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 9",{"$nulls":9},"*"]
["0C",36,"Input 21 Trigger","Indexed String",null,"4x00652",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C34 <> Unassigned","<>","Unassigned"]
["0C",37,"Digital Input 22","Indexed String",null,"4x00653",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 8",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 10",{"$nulls":9},"*"]
["0C",38,"Input 22 Trigger","Indexed String",null,"4x00654",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C36 <> Unassigned","<>","Unassigned"]
["0C",39,"Digital Input 23","Indexed String",null,"4x00655",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 9",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 11",{"$nulls":9},"*"]
["0C","3A","Input 23 Trigger","Indexed String",null,"4x00656",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C38 <> Unassigned","<>","Unassigned"]
["0C","3B","Digital Input 24","Indexed String",null,"4x00657",null,"G32","G32",null,1,"Unused ","Setting",0,"DDB Size",1,2,"*","*",null,"*",{"$nulls":7},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 10",{"$nulls":7},"*"]
[{"$nulls":11},"Opto Input 12",{"$nulls":9},"*"]
["0C","3C","Input 24 Trigger","Indexed String",null,"4x00658",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C3A <> Unassigned","<>","Unassigned"]
["0C","3D","Digital Input 25","Indexed String",null,"4x00659",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*","*",{"$nulls":6},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 11",{"$nulls":7},"*"]
["0C","3E","Input 25 Trigger","Indexed String",null,"4x00660",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C3C <> Unassigned","<>","Unassigned"]
["0C","3F","Digital Input 26","Indexed String",null,"4x00661",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*","*",{"$nulls":6},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 12",{"$nulls":7},"*"]
["0C",40,"Input 26 Trigger","Indexed String",null,"4x00662",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C3E <> Unassigned","<>","Unassigned"]
["0C",41,"Digital Input 27","Indexed String",null,"4x00663",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*","*",{"$nulls":6},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 13",{"$nulls":7},"*"]
["0C",42,"Input 27 Trigger","Indexed String",null,"4x00664",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C40 <> Unassigned","<>","Unassigned"]
["0C",43,"Digital Input 28","Indexed String",null,"4x00665",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*","*",{"$nulls":6},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 14",{"$nulls":7},"*"]
["0C",44,"Input 28 Trigger","Indexed String",null,"4x00666",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C42 <> Unassigned","<>","Unassigned"]
["0C",45,"Digital Input 29","Indexed String",null,"4x00667",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*",null,"*","*",{"$nulls":6},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 15",{"$nulls":7},"*"]
["0C",46,"Input 29 Trigger","Indexed String",null,"4x00668",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C44 <> Unassigned","<>","Unassigned"]
["0C",47,"Digital Input 30","Indexed String",null,"4x00669",null,"G32","G32",null,1,"Unused ","Setting",0,"DDB Size",1,2,"*","*",null,"*","*",{"$nulls":6},"DDB Size different for each model","*"]
[{"$nulls":11},"Opto Input 16",{"$nulls":7},"*"]
["0C",48,"Input 30 Trigger","Indexed String",null,"4x00670",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C46 <> Unassigned","<>","Unassigned"]
["0C",49,"Digital Input 31","Indexed String",null,"4x00671",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
[]
["0C","4A","Input 31 Trigger","Indexed String",null,"4x00672",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C48 <> Unassigned","<>","Unassigned"]
["0C","4B","Digital Input 32","Indexed String",null,"4x00673",null,"G32","G32",null,1,"Unused","Setting",0,"DDB Size",1,2,"*","*","*","*","*",{"$nulls":6},"DDB Size different for each model","*"]
[]
["0C","4C","Input 32 Trigger","Indexed String",null,"4x00674",null,"G66","G66",null,1,"No Trigger","Setting",0,2,1,2,"*","*","*","*","*","0C4A <> Unassigned","<>","Unassigned"]
["0D",0,"MEASURE'T SETUP",{"$nulls":14},"*","*","*","*","*","092B = 1",{"$nulls":5},"MEASUREMENT SETTINGS","*"]
["0D",1,"Default Display","Indexed String",null,"4x00700",null,"G52","G52",null,null,"Description","Setting",0,7,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["0D",2,"Local Values","Indexed String",null,"4x00701",null,"G54","G54",null,null,"Primary","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":6},"Local Measurement Values","*"]
["0D",3,"Remote Values","Indexed String",null,"4x00702",null,"G54","G54",null,null,"Primary","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":6},"Remote Measurement Values","*"]
["0D",4,"Measurement Ref","Indexed String",null,"4x00703",null,"G56","G56",null,1,"VA","Setting",0,5,1,1,"*","*","*","*","*",{"$nulls":6},"Measurement Phase Reference","*"]
["0D",5,"Measurement Mode","Unsigned Integer (16 bits)",null,"4x00705",null,null,"G1",3,1,0,"Setting",0,3,1,1,"*","*","*","*","*",{"$nulls":7},"*"]
["0D",6,"Fix Dem Period","Courier Number (time-minutes)",null,"4x00706",null,null,"G2",null,1,30,"Setting",1,99,1,2,"*","*","*","*","*",{"$nulls":6},"Fixed Demand Interval","*"]
["0D",7,"Roll Sub Period","Courier Number (time-minutes)",null,"4x00707",null,null,"G2",null,1,30,"Setting",1,99,1,2,"*","*","*","*","*",{"$nulls":6},"Rolling demand sub period","*"]
["0D",8,"Num Sub Periods","Unsigned Integer (16 bits)",null,"4x00708",null,null,"G1",null,1,1,"Setting",1,15,1,2,"*","*","*","*","*",{"$nulls":6},"Number of rolling sub periods","*"]
["0D",9,"Distance Unit","Indexed String",null,"4x00709",null,"G97","G97",null,1,"Miles","Setting",0,1,1,2,"*","*","*","*","*","0922 = 1",{"$nulls":6},"*"]
["0D","0A","Fault Location","Indexed String",null,"4x00710",null,"G51","G51",null,1,"Distance","Setting",0,2,1,2,"*","*","*","*","*","0922 = 1",{"$nulls":6},"*"]
["0D","0B","Remote 2 Values","Indexed String",null,"4x00711",null,"G54","G54",null,1,"Primary","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Rear Comms Card Fitted"]
["0E",0,"COMMUNICATIONS",{"$nulls":14},"*","*","*","*","*","092C = 1","=",1,{"$nulls":4},"*"]
["0E",1,"RP1 Protocol","Indexed String",null,null,null,"G71",{"$nulls":4},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0E",2,"RP1 Address","Unsigned Integer (16 bits) ",{"$nulls":7},255,"Setting",0,255,1,1,"*","*","*","*","*",{"$nulls":6},"Build = Courier","*"]
["0E",2,"RP1 Address","Unsigned Integer (16 bits) ",{"$nulls":7},1,"Setting",1,247,1,1,"*","*","*","*","*",{"$nulls":6},"Build = MODBUS","*"]
["0E",2,"RP1 Address","Unsigned Integer (16 bits) ",{"$nulls":7},1,"Setting",0,254,1,1,"*","*","*","*","*",{"$nulls":6},"Build = IEC60870-5-103","*"]
["0E",2,"RP1 Address","Unsigned Integer (16 bits) ",{"$nulls":7},1,"Setting",0,65534,1,1,"*","*","*","*","*",{"$nulls":6},"Build = DNP 3.0","*"]
["0E",3,"RP1 InactivTimer","Courier Number (time-minutes)",{"$nulls":7},15,"Setting",1,30,1,2,"*","*","*","*","*",{"$nulls":6},"Build = Courier","*"]
["0E",3,"RP1 InactivTimer","Courier Number (time-minutes)",{"$nulls":7},15,"Setting",1,30,1,2,"*","*","*","*","*",{"$nulls":6},"Build = MODBUS","*"]
["0E",3,"RP1 InactivTimer","Courier Number (time-minutes)",{"$nulls":7},15,"Setting",1,30,1,2,"*","*","*","*","*",{"$nulls":6},"Build = IEC60870-5-103","*"]
["0E",4,"RP1 Baud Rate","Indexed String",null,null,null,"G38m",null,null,null,"19200 bits/s","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Build = MODBUS","*"]
["0E",4,"RP1 Baud Rate","Indexed String",null,null,null,"G38v",null,null,null,"19200 bits/s","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Build = IEC60870-5-103","*"]
["0E",4,"RP1 Baud Rate","Indexed String",null,null,null,"G38d",null,null,null,"19200 bits/s","Setting",0,5,1,2,"*","*","*","*","*",{"$nulls":6},"Build = DNP 3.0","*"]
["0E",5,"RP1 Parity","Indexed String",null,null,null,"G39",null,null,null,"None","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Build = MODBUS","*"]
["0E",5,"RP1 Parity","Indexed String",null,null,null,"G39",null,null,null,"None","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Build = DNP 3.0","*"]
["0E",6,"RP1 Meas Period","Courier Number (time-seconds)",{"$nulls":7},15,"Setting",1,60,1,2,"*","*","*","*","*",{"$nulls":6},"Build = IEC60870-5-103","*"]
["0E",7,"RP1 PhysicalLink","Indexed String",null,null,null,"G21",null,null,null,"RS485","Setting",0,1,1,1,"*","*","*","*","*",{"$nulls":6},"With Non-Ethernet Builds, it’s a replication of RP1 communication protocol.  Fiber Optic board should be fitted.","*"]
["0E",8,"RP1 Time Sync","Indexed String",null,null,null,"G37",null,null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","0804 = 0","=",0,null,null,null,"Build = DNP 3.0","*"]
["0E",9,"Modbus IEC Time","Indexed String",null,"4x00306",null,"G238","G238","G1",1,"Standard","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Build = MODBUS","*"]
["0E","0A","RP1 CS103Blcking","Indexed String",null,null,null,"G210",null,null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Build = CS103","*"]
["0E","0B","RP1 Card Status","Indexed String",null,null,null,"G208",{"$nulls":4},"Data",{"$nulls":4},"*","*","*","*","*"]
["0E","0C","RP1 Port Config","Indexed String",null,null,null,"G207",null,null,null,"K-Bus","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Build = Courier"]
["0E","0D","RP1 Comms Mode","Indexed String",null,null,null,"G206",null,null,null,"IEC60870 FT1.2","Setting",0,1,1,2,"*","*","*","*","*","0E0C = 1",{"$nulls":5},"Build = Courier"]
["0E","0E","RP1 Baud Rate","Indexed String",null,null,null,"G38c",null,null,null,"19200 bits/s","Setting",0,2,1,2,"*","*","*","*","*","0E0C = 1",{"$nulls":5},"Build = Courier"]
["0E","0F","Meas Scaling","Indexed String",null,null,null,"G249",null,null,null,"Primary","Setting",0,2,1,2,"*","*","*","*","*","Build = DNP 3.0",{"$nulls":5},"Build = DNP 3.0"]
["0E",10,"Message Gap (ms)","Courier Number (time - ms)",{"$nulls":7},0,"Setting",0,50,1,2,"*","*","*","*","*","Build = DNP 3.0",{"$nulls":5},"Build = DNP 3.0"]
["0E",11,"DNP Need Time","Courier Number (time-minutes)",{"$nulls":7},10,"Setting",1,30,1,2,"*","*","*","*","*","Build = DNP 3.0",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_SERIAL"]
["0E",12,"DNP App Fragment","Unsigned Integer (16 bits) ",{"$nulls":7},2048,"Setting",100,2048,1,2,"*","*","*","*","*","Build = DNP 3.0",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_SERIAL"]
["0E",13,"DNP App Timeout","Courier Number (time-seconds)",{"$nulls":7},2,"Setting",1,120,1,2,"*","*","*","*","*","Build = DNP 3.0",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_SERIAL"]
["0E",14,"DNP SBO Timeout","Courier Number (time-seconds)",{"$nulls":7},10,"Setting",1,10,1,2,"*","*","*","*","*","Build = DNP 3.0",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_SERIAL"]
["0E",15,"DNP Link Timeout","Courier Number (time-seconds)",{"$nulls":7},0,"Setting",0,120,1,2,"*","*","*","*","*","Build = DNP 3.0",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_SERIAL"]
["0E","1F","NIC Protocol","Indexed String",null,null,null,"G235",{"$nulls":4},"Data",{"$nulls":4},"*","*","*","*","*","Build = DNP3oe & IEC61850",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E",22,"NIC MAC Address","ASCII Text (17 chars)",{"$nulls":7},"Ethernet MAC Address","Data",null,null,null,2,"*","*","*","*","*","Build = DNP3oe & IEC61850",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E",24,"Number of Routes","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Setting",0,4,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",25,"Router Address 1","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",26,"Target Network 1","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",27,"Router Address 2","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",28,"Target Network 2","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",29,"Router Address 3","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E","2A","Target Network 3","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E","2B","Router Address 4","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E","2C","Target Network 4","ASCII Text (16 chars)",{"$nulls":7},"000.000.000.000","Setting",48,57,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E","2E","Default Pass Lvl","Unsigned Integer (16 bits) ",{"$nulls":7},2,"Setting",0,2,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E","2F","GOOSE Min Cycle","Unsigned Integer (16 bits) ",{"$nulls":7},10,"Setting",1,50,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",30,"GOOSE Max Cycle","Unsigned Integer (16 bits) ",{"$nulls":7},1,"Setting",1,60,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",31,"GOOSE Increment","Unsigned Integer (16 bits) ",{"$nulls":7},900,"Setting",0,999,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",32,"GOOSE Startup","Indexed String",null,null,null,"G221",null,null,null,"Promiscuous","Setting",0,1,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",34,"GOOSE VIP Status","Binary Flag (32 bits)",{"$nulls":7},"0x00000000h","Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E","3F","GOOSE STATISTICS","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",40,"Enrolled Flags","Binary Flag (32 bits)",{"$nulls":7},"0x00000000h","Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",41,"Tx Msg Count","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",42,"Rx Msg Count","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",43,"DDB Changes","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",44,"Last Seq Tx","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",45,"Last Msg Tx","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",46,"Msg Reject Count","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",50,"IED View Select","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Setting",0,32,1,0,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",51,"IED Recvd Msgs","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",52,"IED Last Seq Rx","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",53,"IED Last Msg Rx","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",54,"IED Missed Msgs","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",55,"IED Missed Chngs","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",56,"IED Timeouts","Unsigned Integer (16 bits) ",{"$nulls":7},0,"Data",{"$nulls":4},"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E","5F","IED Stats Reset","Indexed String",null,null,null,"G223",null,null,null,"None","Setting",0,4,1,2,"*","*","*","*","*","Build = UCA2.0",{"$nulls":5},"Build = UCA2"]
["0E",61,"Reload Mode","Indexed String",null,null,null,"G225",null,null,null,"No Action","Setting",0,1,1,3,"*","*","*","*","*","Build = UCA2.0 - Normally HIDDEN",{"$nulls":5},"Build = UCA2"]
["0E",64,"NIC Tunl Timeout","Courier Number (time-minutes)",{"$nulls":7},"5.00 min","Setting",1,30,1,2,"*","*","*","*","*","Build = IEC61850",{"$nulls":5},"Build = IEC61850"]
["0E","6A","NIC Link Report","Indexed String",null,null,null,"G226",null,null,null,"Alarm","Setting",0,2,1,2,"*","*","*","*","*","Build = IEC61850",{"$nulls":5},"Build = IEC61850"]
["0E",80,"REAR PORT2 (RP2)","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E",81,"RP2 Protocol","Indexed String",null,null,null,"G71","G71","G1",null,"Courier","Data",{"$nulls":4},"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E",84,"RP2 Card Status","Indexed String",null,null,null,"G204","G204","G1",null,null,"Data",{"$nulls":4},"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E",88,"RP2 Port Config","Indexed String",null,null,null,"G205","G205","G1",null,"EIA232 (RS232)","Setting",0,1,1,2,"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E","8A","RP2 Comms Mode","Indexed String",null,null,null,"G206","G206","G1",null,"IEC60870 FT1.2","Setting",0,1,1,2,"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E",90,"RP2 Address","Unsigned Integer (16 bits) ",{"$nulls":5},"G1",null,255,"Setting",0,255,1,1,"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E",92,"RP2 InactivTimer","Courier Number (time-minutes)",{"$nulls":5},"G2",null,15,"Setting",1,30,1,2,"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E",94,"RP2 Baud Rate","Indexed String",null,null,null,"G38m","G38m","G1",null,"19200 bits/s","Setting",0,1,1,2,"*","*","*","*","*","SMF",{"$nulls":5},"Rear Comms Card Fitted"]
["0E","A1","IP Address","ASCII Text (16 chars)",{"$nulls":7},"0.0.0.0","Data",48,57,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","A2","Subnet Address","ASCII Text (16 chars)",{"$nulls":7},"0.0.0.0","Data",48,57,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","A4","Gateway","ASCII Text (16 chars)",{"$nulls":7},"0.0.0.0","Data",48,57,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","A5","DNP Time Synch","Indexed String",null,null,null,"G37",null,null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","SNTP not active",{"$nulls":5},"Ethernet Comms Card Fitted"]
[{"$nulls":22},"Build = DNP3oe"]
["0E","A6","Meas Scaling","Indexed String",null,null,null,"G249",null,null,null,"Primary","Setting",0,2,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","A7","NIC Tunl Timeout","Courier Number (time-minutes)",{"$nulls":7},"5 mins","Setting",1,30,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","A8","NIC Link Report","Indexed String",null,null,null,"G226",null,null,null,"Alarm","Setting",0,2,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","A9","NIC Link Timeout","Courier Number (time)",{"$nulls":7},"60s","Setting",0.1,60,0.1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","AA","SNTP PARAMETERS","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","AB","SNTP Server 1","Courier Number (time-minutes)",{"$nulls":7},"0.0.0.0","Data",48,57,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","AC","SNTP Server 2","Indexed String",{"$nulls":7},"0.0.0.0","Data",48,57,1,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","AD","SNTP Poll Rate","Courier Number (time)",{"$nulls":7},"64s","Data",null,null,null,2,"*","*","*","*","*","Build = DNP3oe",{"$nulls":5},"Ethernet Comms Card Fitted"]
["0E","B1","DNP Need Time","Courier Number (time-minutes)",{"$nulls":7},10,"Setting",1,30,1,2,"*","*","*","*","*","Build = DNP3oe",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_ETHERNET"]
["0E","B2","DNP App Fragment","Unsigned Integer (16 bits) ",{"$nulls":7},2048,"Setting",100,2048,1,2,"*","*","*","*","*","Build = DNP3oe",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_ETHERNET"]
["0E","B3","DNP App Timeout","Courier Number (time-seconds)",{"$nulls":7},2,"Setting",1,120,1,2,"*","*","*","*","*","Build = DNP3oe",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_ETHERNET"]
["0E","B4","DNP SBO Timeout","Courier Number (time-seconds)",{"$nulls":7},10,"Setting",1,10,1,2,"*","*","*","*","*","Build = DNP3oe",null,null,"No","Yes",null,"PDBCONF_DNP_FOR_SSE &&"]
[{"$nulls":28},"PLATFORM_DNPEV_ETHERNET"]
["0F",0,"COMMISSION TESTS",{"$nulls":14},"*","*","*","*","*","092D","=",1,{"$nulls":4},"*"]
["0F",1,"Opto I/P Status","Binary Flag (16 bits)",null,null,null,"G8","G8",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[null,null,null,"Indexed String"]
["0F",2,"Relay O/P Status","Binary Flag (32 bits)",null,null,null,"G9","G9",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[null,null,null,"Indexed String"]
["0F",3,"Test Port Status","Binary Flag (8 bits)",{"$nulls":6},1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[null,null,null,"Indexed String"]
["0F",4,"LED Status","Binary Flag (8 bits)",{"$nulls":6},1,null,"Data",{"$nulls":4},"*","*","*","*",{"$nulls":8},"*"]
["0F",5,"Monitor Bit 1","Unsigned Integer (16 bits)",null,"4x00850",null,null,"G1",null,1,64,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 1","*"]
[{"$nulls":11},640,{"$nulls":9},"*"]
["0F",6,"Monitor Bit 2","Unsigned Integer (16 bits)",null,"4x00851",null,null,"G1",null,1,65,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 2","*"]
[{"$nulls":11},642,{"$nulls":9},"*"]
["0F",7,"Monitor Bit 3","Unsigned Integer (16 bits)",null,"4x00852",null,null,"G1",null,1,66,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 3","*"]
[{"$nulls":11},644,{"$nulls":9},"*"]
["0F",8,"Monitor Bit 4","Unsigned Integer (16 bits)",null,"4x00853",null,null,"G1",null,1,67,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 4","*"]
[{"$nulls":11},646,{"$nulls":9},"*"]
["0F",9,"Monitor Bit 5","Unsigned Integer (16 bits)",null,"4x00854",null,null,"G1",null,1,68,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 5","*"]
[{"$nulls":11},648,{"$nulls":9},"*"]
["0F","0A","Monitor Bit 6","Unsigned Integer (16 bits)",null,"4x00855",null,null,"G1",null,1,69,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 6","*"]
[{"$nulls":11},650,{"$nulls":9},"*"]
["0F","0B","Monitor Bit 7","Unsigned Integer (16 bits)",null,"4x00856",null,null,"G1",null,1,70,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 7","*"]
[{"$nulls":11},652,{"$nulls":9},"*"]
["0F","0C","Monitor Bit 8","Unsigned Integer (16 bits)",null,"4x00857",null,null,"G1",null,1,71,"Setting",0,1279,1,2,"*","*","*","*",{"$nulls":7},"Default LED 8","*"]
[{"$nulls":11},654,{"$nulls":9},"*"]
["0F","0D","Test Mode","Indexed String",null,"4x00858",null,"G119","G119",null,1,"Disabled","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
["0F","0E","Test Pattern","Binary Flag (32 bits)",null,"4x00859","4x00860","G9","G9",null,2,0,"Setting",0,6,1,2,"*","*",null,"*",null,"0F0D = 2",null,null,null,"*",null,null,"*"]
[null,null,null,"Indexed String",{"$nulls":9},0,13,1,2,null,null,"*",null,"*"]
["0F","0F","Contact Test","Indexed String",null,"4x00861",null,"G93","G93",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*","0F0D = 2",null,null,null,"*",null,null,"*"]
["0F",10,"Test LEDs","Indexed String",null,"4x00862",null,"G94","G94",null,1,"No Operation","Command",0,1,1,2,"*","*","*","*","*",{"$nulls":4},"*",null,null,"*"]
["0F",11,"Test Autoreclose","Indexed String",null,"4x00863",null,"G36","G36",null,1,"No Operation","Command",0,1,1,2,null,"*","*","*","*",{"$nulls":4},"*",null,null,"*"]
[{"$nulls":28},"South Park Modifications"]
[null,null,null,"Binary Flag(16)","N/A","3x11001",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Relay Status (repeat of Courier status)"]
[null,null,null,"Courier Number (current)","N/A","3x11002","3x11003",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"IA Magnitude"]
[null,null,null,"Courier Number (current)","N/A","3x11004","3x11005",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"IB Magnitude"]
[null,null,null,"Courier Number (current)","N/A","3x11006","3x11007",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"IC Magnitude"]
[null,null,null,"Courier Number (voltage)","N/A","3x11008","3x11009",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"VAB Magnitude"]
[null,null,null,"Courier Number (voltage)","N/A","3x11010","3x11011",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"VBC Magnitude"]
[null,null,null,"Courier Number (voltage)","N/A","3x11012","3x11013",null,"G24",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"VCA Magnitude"]
[null,null,null,"Courier Number (power)","N/A","3x11014","3x11016",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"3 Phase Watts"]
[null,null,null,"Courier Number (power)","N/A","3x11017","3x11019",null,"G29",null,3,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"3 Phase VArs"]
[null,null,null,"Courier Number (decimal)","N/A","3x11020",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"3 Phase Power Factor"]
[null,null,null,"Courier Number (frequency)","N/A","3x11021",null,null,"G30",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Frequency"]
[null,null,null,"Binary Flag(8)","N/A","3x11022",null,null,"G1",null,1,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Relay Test Port Status"]
["0F",15,"Red LED Status","Binary Flag(18)",{"$nulls":6},1,null,"Data",{"$nulls":8},"*",{"$nulls":6},"Status of RED LED Elements","*"]
["0F",16,"Green LED Status","Binary Flag(18)",{"$nulls":6},1,null,"Data",{"$nulls":8},"*",{"$nulls":6},"Status of GREEN LED Elements","*"]
["0F",20,"DDB 31 - 0","Binary Flag(32)","N/A","3x11023","3x11024",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"DDB Elements 0-31","*"]
["0F",21,"DDB 63 - 32","Binary Flag(32)","N/A","3x11025","3x11026",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",22,"DDB 95 - 64","Binary Flag(32)","N/A","3x11027","3x11028",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",23,"DDB 127 - 96","Binary Flag(32)","N/A","3x11029","3x11030",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",24,"DDB 159 - 128","Binary Flag(32)","N/A","3x11031","3x11032",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",25,"DDB 191 - 160","Binary Flag(32)","N/A","3x11033","3x11034",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",26,"DDB 223 - 192","Binary Flag(32)","N/A","3x11035","3x11036",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",27,"DDB 255 - 224","Binary Flag(32)","N/A","3x11037","3x11038",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",28,"DDB 287 - 256","Binary Flag(32)","N/A","3x11039","3x11040",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",29,"DDB 319 - 288","Binary Flag(32)","N/A","3x11041","3x11042",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","2A","DDB 351 - 320","Binary Flag(32)","N/A","3x11043","3x11044",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","2B","DDB 383 - 352","Binary Flag(32)","N/A","3x11045","3x11046",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","2C","DDB 415 - 384","Binary Flag(32)","N/A","3x11047","3x11048",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","2D","DDB 447 - 416","Binary Flag(32)","N/A","3x11049","3x11050",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","2E","DDB 479 - 448","Binary Flag(32)","N/A","3x11051","3x11052",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","2F","DDB 511 - 480","Binary Flag(32)","N/A","3x11053","3x11054",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",30,"DDB 543 - 512","Binary Flag(32)","N/A","3x11055","3x11056",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",31,"DDB 575 - 544","Binary Flag(32)","N/A","3x11057","3x11058",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",32,"DDB 607 - 576","Binary Flag(32)","N/A","3x11059","3x11060",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",33,"DDB 639 - 608","Binary Flag(32)","N/A","3x11061","3x11062",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",34,"DDB 671 - 640","Binary Flag(32)","N/A","3x11063","3x11064",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",35,"DDB 703 - 672","Binary Flag(32)","N/A","3x11065","3x11066",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",36,"DDB 735 - 704","Binary Flag(32)","N/A","3x11067","3x11068",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",37,"DDB 767 - 736","Binary Flag(32)","N/A","3x11069","3x11070",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",38,"DDB 799 - 768","Binary Flag(32)","N/A","3x11071","3x11072",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",39,"DDB 831 - 800","Binary Flag(32)","N/A","3x11073","3x11074",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","3A","DDB 863 - 832","Binary Flag(32)","N/A","3x11075","3x11076",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","3B","DDB 895 - 864","Binary Flag(32)","N/A","3x11077","3x11078",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","3C","DDB 927 - 896","Binary Flag(32)","N/A","3x11079","3x11080",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","3D","DDB 959 - 928","Binary Flag(32)","N/A","3x11081","3x11082",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","3E","DDB 991 - 960","Binary Flag(32)","N/A","3x11083","3x11084",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F","3F","DDB 1023 - 992","Binary Flag(32)","N/A","3x11085","3x11086",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",40,"DDB 1055 - 1024","Binary Flag(32)","N/A","3x11087","3x11088",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",41,"DDB 1087 - 1056","Binary Flag(32)","N/A","3x11089","3x11090",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",42,"DDB 1119 - 1088","Binary Flag(32)","N/A","3x11091","3x11092",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",43,"DDB 1151 - 1120","Binary Flag(32)","N/A","3x11093","3x11094",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",44,"DDB 1183 - 1152","Binary Flag(32)","N/A","3x11095","3x11096",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",45,"DDB 1215 - 1184","Binary Flag(32)","N/A","3x11097","3x11098",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",46,"DDB 1247 - 1216","Binary Flag(32)","N/A","3x11099","3x11100",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
["0F",47,"DDB 1279 - 1248","Binary Flag(32)","N/A","3x11101","3x11102",null,"G27",null,2,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[10,0,"CB MONITOR SETUP",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[10,1,"Broken I^","Courier Number (decimal)",null,"4x00151",null,null,"G2",10,1,2,"Setting",1,2,0.1,2,"*","*","*","*","*",{"$nulls":6},"Broken Current Index","*"]
[10,2,"I^ Maintenance","Indexed String",null,"4x00152",null,"G88","G88",null,1,"Alarm Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Broken Current to cause maintenance alarm","*"]
[10,3,"I^ Maintenance","Courier Number (current)",null,"4x00153","4x00154",null,"G35",2500000000,2,1000,"Setting","1 * NM1","25000 * NM1","1 * NM1",2,"*","*","*","*","*","1002 = 1",{"$nulls":4},"M4^1001","IX Maintenance Alarm","*"]
[10,4,"I^ Lockout","Indexed String",null,"4x00155",null,"G88","G88",null,1,"Alarm Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Broken Current to cause lockout alarm","*"]
[10,5,"I^ Lockout","Courier Number (current)",null,"4x00156","4x00157",null,"G35",2500000000,2,2000,"Setting","1 * NM1","25000 * NM1","1 * NM1",2,"*","*","*","*","*","1004 = 1",{"$nulls":4},"M4^1001","IX Maintenance Lockout","*"]
[10,6,"No. CB Ops Maint","Indexed String",null,"4x00158",null,"G88","G88",null,1,"Alarm Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Circuit Breaker Trips to cause maintenance alarm","*"]
[10,7,"No. CB Ops Maint","Unsigned Integer (16 bits)",null,"4x00159",null,null,"G1",250,1,10,"Setting",1,10000,1,2,"*","*","*","*","*","1006 = 1",{"$nulls":5},"Number of Circuit Breaker Trips for maintenance alarm","*"]
[10,8,"No. CB Ops Lock","Indexed String",null,"4x00160",null,"G88","G88",null,1,"Alarm Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Circuit Breaker Trips to cause lockout alarm","*"]
[10,9,"No. CB Ops Lock","Unsigned Integer (16 bits)",null,"4x00161",null,null,"G1",250,1,20,"Setting",1,10000,1,2,"*","*","*","*","*","1008 = 1",{"$nulls":5},"Number of Circuit Breaker Trips for lockout alarm","*"]
[10,"0A","CB Time Maint","Indexed String",null,"4x00162",null,"G88","G88",null,1,"Alarm Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Circuit Breaker Operating Time to cause maintenance alarm","*"]
[10,"0B","CB Time Maint","Courier Number (time)",null,"4x00163","4x00164",null,"G35",500000,2,0.1,"Setting",0.005,0.5,0.001,2,"*","*","*","*","*","100A = 1",{"$nulls":5},"Circuit Breaker Operating time for maintenance alarm","*"]
[10,"0C","CB Time Lockout","Indexed String",null,"4x00165",null,"G88","G88",null,1,"Alarm Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Circuit Breaker Operating Time to cause lockout alarm","*"]
[10,"0D","CB Time Lockout","Courier Number (time)",null,"4x00166","4x00167",null,"G35",500000,2,0.2,"Setting",0.005,0.5,0.001,2,"*","*","*","*","*","100C = 1",{"$nulls":5},"Circuit Breaker Operating time for lockout alarm","*"]
[10,"0E","Fault Freq Lock","Indexed String",null,"4x00168",null,"G88","G88",null,1,"Alarm Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Excessive fault frequency","*"]
[10,"0F","Fault Freq Count","Unsigned Integer (16 bits)",null,"4x00169",null,null,"G1",9999,1,10,"Setting",1,9999,1,2,"*","*","*","*","*","100E = 1",{"$nulls":5},"Excessive Fault Frequency Counter","*"]
[10,10,"Fault Freq Time","Courier Number (time)",null,"4x00170","4x00171",null,"G35",999900,2,3600,"Setting",0,9999,1,2,"*","*","*","*","*","100E = 1",{"$nulls":5},"Excessive Fault Frequency Time","*"]
[11,0,"OPTO CONFIG",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[11,1,"Global Nominal V","Indexed String",null,"4x00900",null,"G200","G200",null,1,"48/54V","Setting",0,5,1,2,"*","*","*","*","*",{"$nulls":6},"Global Opto Input Voltage","*"]
[11,2,"Opto Input 1","Indexed String",null,"4x00901",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,3,"Opto Input 2","Indexed String",null,"4x00902",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,4,"Opto Input 3","Indexed String",null,"4x00903",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,5,"Opto Input 4","Indexed String",null,"4x00904",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,6,"Opto Input 5","Indexed String",null,"4x00905",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,7,"Opto Input 6","Indexed String",null,"4x00906",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,8,"Opto Input 7","Indexed String",null,"4x00907",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,9,"Opto Input 8","Indexed String",null,"4x00908",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,"*","*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"0A","Opto Input 9","Indexed String",null,"4x00909",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"0B","Opto Input 10","Indexed String",null,"4x00910",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"0C","Opto Input 11","Indexed String",null,"4x00911",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"0D","Opto Input 12","Indexed String",null,"4x00912",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"0E","Opto Input 13","Indexed String",null,"4x00913",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"0F","Opto Input 14","Indexed String",null,"4x00914",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,10,"Opto Input 15","Indexed String",null,"4x00915",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,11,"Opto Input 16","Indexed String",null,"4x00916",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,"*","*","*","*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,12,"Opto Input 17","Indexed String",null,"4x00917",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,13,"Opto Input 18","Indexed String",null,"4x00918",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,14,"Opto Input 19","Indexed String",null,"4x00919",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,15,"Opto Input 20","Indexed String",null,"4x00920",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,16,"Opto Input 21","Indexed String",null,"4x00921",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,17,"Opto Input 22","Indexed String",null,"4x00922",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,18,"Opto Input 23","Indexed String",null,"4x00923",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,19,"Opto Input 24","Indexed String",null,"4x00924",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"1A","Opto Input 25","Indexed String",null,"4x00925",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"1B","Opto Input 26","Indexed String",null,"4x00926",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"1C","Opto Input 27","Indexed String",null,"4x00927",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"1D","Opto Input 28","Indexed String",null,"4x00928",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"1E","Opto Input 29","Indexed String",null,"4x00929",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,"1F","Opto Input 30","Indexed String",null,"4x00930",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,20,"Opto Input 31","Indexed String",null,"4x00931",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,21,"Opto Input 32","Indexed String",null,"4x00932",null,"G201","G201",null,1,"48/54V","Setting",0,4,1,2,null,null,"*",null,"*","1101 = 5","=",5,null,null,null,"Individual Opto Input Voltage","*"]
[11,50,"Opto Filter Cntl","Binary Flag (32 bits)",null,"4x00933","4x00934","G8","G8",null,1,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*",{"$nulls":6},"Opto filter configuration","*"]
[null,null,null,"Indexed String"]
[11,80,"Characteristic","Indexed String",null,"4x00935",null,"G237","G1",null,1,"Standard 60%-80%","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Opto characteristic configuration","*"]
[12,0,"CONTROL INPUTS",{"$nulls":14},"*","*","*","*","*","092F = 1",{"$nulls":6},"*"]
[12,1,"Ctrl I/P Status","Binary Flag (32 bits)",null,"4x00950","4x00951","G202","G202",null,null,"0x00000000","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[null,null,null,"Indexed String"]
[12,2,"Control Input 1","Indexed String",null,"4x00952",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,3,"Control Input 2","Indexed String",null,"4x00953",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,4,"Control Input 3","Indexed String",null,"4x00954",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,5,"Control Input 4","Indexed String",null,"4x00955",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,6,"Control Input 5","Indexed String",null,"4x00956",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,7,"Control Input 6","Indexed String",null,"4x00957",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,8,"Control Input 7","Indexed String",null,"4x00958",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,9,"Control Input 8","Indexed String",null,"4x00959",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"0A","Control Input 9","Indexed String",null,"4x00960",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"0B","Control Input 10","Indexed String",null,"4x00961",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"0C","Control Input 11","Indexed String",null,"4x00962",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"0D","Control Input 12","Indexed String",null,"4x00963",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"0E","Control Input 13","Indexed String",null,"4x00964",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"0F","Control Input 14","Indexed String",null,"4x00965",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,10,"Control Input 15","Indexed String",null,"4x00966",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,11,"Control Input 16","Indexed String",null,"4x00967",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,12,"Control Input 17","Indexed String",null,"4x00968",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,13,"Control Input 18","Indexed String",null,"4x00969",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,14,"Control Input 19","Indexed String",null,"4x00970",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,15,"Control Input 20","Indexed String",null,"4x00971",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,16,"Control Input 21","Indexed String",null,"4x00972",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,17,"Control Input 22","Indexed String",null,"4x00973",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,18,"Control Input 23","Indexed String",null,"4x00974",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,19,"Control Input 24","Indexed String",null,"4x00975",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"1A","Control Input 25","Indexed String",null,"4x00976",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"1B","Control Input 26","Indexed String",null,"4x00977",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"1C","Control Input 27","Indexed String",null,"4x00978",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"1D","Control Input 28","Indexed String",null,"4x00979",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"1E","Control Input 29","Indexed String",null,"4x00980",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,"1F","Control Input 30","Indexed String",null,"4x00981",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,20,"Control Input 31","Indexed String",null,"4x00982",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[12,21,"Control Input 32","Indexed String",null,"4x00983",null,"G203","G203",null,1,"No Operation","Command",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[13,0,"CTRL I/P CONFIG",{"$nulls":14},"*","*","*","*","*","0935 = 1"]
[13,1,"Hotkey Enabled","Binary Flag (32 bits)",null,null,null,"G233",null,null,null,"0xFFFFFFFF","Setting","0xFFFFFFFF",32,1,2,"*","*","*","*","*","0939 = 1 OR 0939 = 2",{"$nulls":5},"Hotkey Menu - Control Input availability"]
[null,null,null,"Indexed String",{"$nulls":18},"0939 = 2"]
[13,10,"Control Input 1","Indexed String",null,"4x10002",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,11,"Ctrl Command 1","Indexed String",null,"4x10003",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,14,"Control Input 2","Indexed String",null,"4x10004",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,15,"Ctrl Command 2","Indexed String",null,"4x10005",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,18,"Control Input 3","Indexed String",null,"4x10006",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,19,"Ctrl Command 3","Indexed String",null,"4x10007",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"1C","Control Input 4","Indexed String",null,"4x10008",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"1D","Ctrl Command 4","Indexed String",null,"4x10009",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,20,"Control Input 5","Indexed String",null,"4x10010",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,21,"Ctrl Command 5","Indexed String",null,"4x10011",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,24,"Control Input 6","Indexed String",null,"4x10012",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,25,"Ctrl Command 6","Indexed String",null,"4x10013",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,28,"Control Input 7","Indexed String",null,"4x10014",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,29,"Ctrl Command 7","Indexed String",null,"4x10015",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"2C","Control Input 8","Indexed String",null,"4x10016",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"2D","Ctrl Command 8","Indexed String",null,"4x10017",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,30,"Control Input 9","Indexed String",null,"4x10018",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,31,"Ctrl Command 9","Indexed String",null,"4x10019",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,34,"Control Input 10","Indexed String",null,"4x10020",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,35,"Ctrl Command 10","Indexed String",null,"4x10021",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,38,"Control Input 11","Indexed String",null,"4x10022",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,39,"Ctrl Command 11","Indexed String",null,"4x10023",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"3C","Control Input 12","Indexed String",null,"4x10024",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"3D","Ctrl Command 12","Indexed String",null,"4x10025",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,40,"Control Input 13","Indexed String",null,"4x10026",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,41,"Ctrl Command 13","Indexed String",null,"4x10027",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,44,"Control Input 14","Indexed String",null,"4x10028",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,45,"Ctrl Command 14","Indexed String",null,"4x10029",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,48,"Control Input 15","Indexed String",null,"4x10030",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,49,"Ctrl Command 15","Indexed String",null,"4x10031",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"4C","Control Input 16","Indexed String",null,"4x10032",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"4D","Ctrl Command 16","Indexed String",null,"4x10033",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,50,"Control Input 17","Indexed String",null,"4x10034",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,51,"Ctrl Command 17","Indexed String",null,"4x10035",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,54,"Control Input 18","Indexed String",null,"4x10036",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,55,"Ctrl Command 18","Indexed String",null,"4x10037",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,58,"Control Input 19","Indexed String",null,"4x10038",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,59,"Ctrl Command 19","Indexed String",null,"4x10039",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"5C","Control Input 20","Indexed String",null,"4x10040",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"5D","Ctrl Command 20","Indexed String",null,"4x10041",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,60,"Control Input 21","Indexed String",null,"4x10042",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,61,"Ctrl Command 21","Indexed String",null,"4x10043",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,64,"Control Input 22","Indexed String",null,"4x10044",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,65,"Ctrl Command 22","Indexed String",null,"4x10045",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,68,"Control Input 23","Indexed String",null,"4x10046",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,69,"Ctrl Command 23","Indexed String",null,"4x10047",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"6C","Control Input 24","Indexed String",null,"4x10048",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"6D","Ctrl Command 24","Indexed String",null,"4x10049",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,70,"Control Input 25","Indexed String",null,"4x10050",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,71,"Ctrl Command 25","Indexed String",null,"4x10051",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,74,"Control Input 26","Indexed String",null,"4x10052",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,75,"Ctrl Command 26","Indexed String",null,"4x10053",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,78,"Control Input 27","Indexed String",null,"4x10054",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,79,"Ctrl Command 27","Indexed String",null,"4x10055",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"7C","Control Input 28","Indexed String",null,"4x10056",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"7D","Ctrl Command 28","Indexed String",null,"4x10057",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,80,"Control Input 29","Indexed String",null,"4x10058",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,81,"Ctrl Command 29","Indexed String",null,"4x10059",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,84,"Control Input 30","Indexed String",null,"4x10060",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,85,"Ctrl Command 30","Indexed String",null,"4x10061",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,88,"Control Input 31","Indexed String",null,"4x10062",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,89,"Ctrl Command 31","Indexed String",null,"4x10063",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[13,"8C","Control Input 32","Indexed String",null,"4x10064",null,"G234","G234",null,null,"Latched","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Type"]
[13,"8D","Ctrl Command 32","Indexed String",null,"4x10065",null,"G232","G232",null,null,"SET/RESET","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"Individual Control Input Command Text"]
[15,0,"INTERMICOM COMMS",{"$nulls":14},"*","*","*","*","*","0940 = 1"]
[15,1,"IM Input Status","Binary Flags (8 bits)",null,"3x10000",null,null,"G28",null,null,"00000000","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"InterMiCOM input status"]
[15,2,"IM Output Status","Binary Flags (8 bits)",null,"3x10001",null,null,"G28",null,null,"00000000","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"InterMiCOM Output status"]
[15,10,"Source Address","Unsigned Integer(16 bit)",null,"4x10500",null,null,"G1",null,null,1,"Setting",1,10,1,2,"*","*","*","*","*"]
[15,11,"Received Address","Unsigned Integer(16 bit)",null,"4x10501",null,null,"G1",null,null,2,"Setting",1,10,1,2,"*","*","*","*","*"]
[15,12,"Data Rate","Indexed String",null,"4x10502",null,"G213","G213",null,null,9600,"Setting",0,5,1,2,"*","*","*","*","*"]
[15,13,"Px30 Comms","Indexed String",null,"4x10503",null,"G218","G218",null,null,"Disable","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"When enabled an idle char is inserted between messages"]
[15,20,"Ch Statistics","Indexed String",null,"4x10504",null,"G80","G80",null,null,"Invisible","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Visble/invisible"]
[15,21,"Rx Direct Count","Unsigned Integer(32 bit)",null,"3x10002","3x10003",null,"G1",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1520 = 1",{"$nulls":5},"Number of messages received at Direct security level"]
[15,22,"Rx Perm Count","Unsigned Integer(32 bit)",null,"3x10004","3x10005",null,"G1",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1520 = 1",{"$nulls":5},"Number of messages received at permissive security level"]
[15,23,"Rx Block Count","Unsigned Integer(32 bit)",null,"3x10006","3x10007",null,"G1",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1520 = 1",{"$nulls":5},"Number of messages received at Blocking level"]
[15,24,"Rx NewDataCount","Unsigned Integer(32 bit)",null,"3x10008","3x10009",null,"G1",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1520 = 1",{"$nulls":5},"Number of messages received with new data"]
[15,25,"Rx ErroredCount","Unsigned Integer(32 bit)",null,"3x10010","3x10011",null,"G1",null,null,null,"Data"," "," "," "," ","*","*","*","*","*","1520 = 1",{"$nulls":5},"Number of errored messages"]
[15,26,"Lost Messages","Courier number (percent)",null,"3x10012",null,null,"G10",null,null,null,"Data"," "," "," "," ","*","*","*","*","*","1520 = 1",{"$nulls":5},"Number of lost messages.  Value compared with cell 0x1611. "]
[15,30,"Elapsed Time","Unsigned Integer(32 bit)",null,"3x10013","3x10014",null,"G1",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1520 = 1",{"$nulls":5},"Elapsed time since statistics were last reset"]
[15,31,"Reset Statistics","Indexed String",null,"4x10505",null,"G11","G11",null,null,"No","Setting",0,1,1,2,"*","*","*","*","*","1520 = 1",{"$nulls":5},"Reset Statistical counters to 0"]
[15,40,"Ch Diagnostics","Indexed String",null,"4x10506",null,"G80","G80",null,null,"Invisible","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"Channel diagnostics visibility"]
[15,41,"Data CD Status","Indexed String",null,"3x10015",null,"G217","G217",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1540 = 1",{"$nulls":5},"Data Carrier Detect status"]
[15,42,"FrameSync Status","Indexed String",null,"3x10016",null,"G217","G217",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1540 = 1",{"$nulls":5},"Frame synchronisation status"]
[15,43,"Message Status","Indexed String",null,"3x10017",null,"G217","G217",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1540 = 1",{"$nulls":5},"Message Alarm Status Linked to cell 0x1611"]
[15,44,"Channel Status","Indexed String",null,"3x10018",null,"G217","G217",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1540 = 1",{"$nulls":5},"Communication Link Fail status four power cycle test"]
[15,45,"IM H/W Status","Indexed String",null,"3x10019",null,"G216","G216",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1540 = 1",{"$nulls":5},"InterMiCOM hardware status"]
[15,50,"Loopback Mode","Indexed String",null,"4x10507",null,"G214","G214",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Internal / External loopback"]
[15,51,"Test Pattern","Binary Flags (8 bits)",null,"4x10508",null,null,"G1",null,null,"11111111","Setting",0,8,1,2,"*","*","*","*","*","1550 <> 0",{"$nulls":5},"Binary flags to set InterMiCOM signal "]
[null,null,null,"Indexed String"]
[15,52,"Loopback Status","Indexed Strings",null,"3x10020",null,"G217","G217",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*","1550 <> 0","<>",0,null,null,null,"Loopback test status OK/FAIL"]
[16,0,"INTERMICOM CONF",{"$nulls":14},"*","*","*","*","*","0940 = 1"]
[16,1,"IM Msg Alarm Lvl","Courier number (percent)",null,"4x10520","4x10521",null,"G35",null,null,25,"Setting",0,100,0.1,2,"*","*","*","*","*",{"$nulls":6},"Alarm level before default data is assigned in inputs "]
[16,10,"IM1 Cmd Type","Indexed Strings",null,"4x10522",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,11,"IM1 FallBackMode","Indexed Strings",null,"4x10523",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1610 <> 1",{"$nulls":5},"Latch or Default"]
[16,12,"IM1 DefaultValue","Unsigned Integer(16 bit)",null,"4x10524",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1611 = 1",{"$nulls":5},"Assign logic 0 or 1 to "]
[16,13,"IM1 FrameSyncTim","Courier number (time)",null,"4x10525","4x10526",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1611 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application "]
[16,18,"IM2 Cmd Type","Indexed Strings",null,"4x10527",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,19,"IM2 FallBackMode","Indexed Strings",null,"4x10528",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1618 <> 1",{"$nulls":5},"Latch or Default"]
[16,"1A","IM2 DefaultValue","Unsigned Integer(16 bit)",null,"4x10529",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1619 = 1",{"$nulls":5},"Assign logic 0 or 1 to InterMiCOM signal "]
[16,"1B","IM2 FrameSyncTim","Courier number (time)",null,"4x10530","4x10531",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1619 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application "]
[16,20,"IM3 Cmd Type","Indexed Strings",null,"4x10532",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,21,"IM3 FallBackMode","Indexed Strings",null,"4x10533",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1620 <> 1",{"$nulls":5},"Latch or Default"]
[16,22,"IM3 DefaultValue","Unsigned Integer(16 bit)",null,"4x10534",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1621 = 1",{"$nulls":5},"Assign logic 0 or 1 to InterMiCOM signal "]
[16,23,"IM3 FrameSyncTim","Courier number (time)",null,"4x10535","4x10536",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1621 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application "]
[16,28,"IM4 Cmd Type","Indexed Strings",null,"4x10537",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,29,"IM4 FallBackMode","Indexed Strings",null,"4x10538",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1628 <> 1",{"$nulls":5},"Latch or Default"]
[16,"2A","IM4 DefaultValue","Unsigned Integer(16 bit)",null,"4x10539",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1629 = 1",{"$nulls":5},"Assign logic 0 or 1 to InterMiCOM signal "]
[16,"2B","IM4 FrameSyncTim","Courier number (time)",null,"4x10540","4x10541",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1629 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application "]
[16,30,"IM5 Cmd Type","Indexed Strings",null,"4x10542",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,31,"IM5 FallBackMode","Indexed Strings",null,"4x10543",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1630 <> 1",{"$nulls":5},"Latch or Default"]
[16,32,"IM5 DefaultValue","Unsigned Integer(16 bit)",null,"4x10544",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1631 = 1",{"$nulls":5},"Assign logic 0 or 1 to InterMiCOM signal "]
[16,33,"IM5 FrameSyncTim","Courier number (time)",null,"4x10545","4x10546",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1632 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application "]
[16,38,"IM6 Cmd Type","Indexed Strings",null,"4x10547",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,39,"IM6 FallBackMode","Indexed Strings",null,"4x10548",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1638 <> 1",{"$nulls":5},"Latch or Default"]
[16,"3A","IM6 DefaultValue","Unsigned Integer(16 bit)",null,"4x10549",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1639 = 1",{"$nulls":5},"Assign logic 0 or 1 to InterMiCOM signal"]
[16,"3B","IM6 FrameSyncTim","Courier number (time)",null,"4x10550","4x10551",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1639 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application"]
[16,40,"IM7 Cmd Type","Indexed Strings",null,"4x10552",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,41,"IM7 FallBackMode","Indexed Strings",null,"4x10553",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1640 <> 1",{"$nulls":5},"Latch or Default"]
[16,42,"IM7 DefaultValue","Unsigned Integer(16 bit)",null,"4x10554",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1641 = 1",{"$nulls":5},"Assign logic 0 or 1 to InterMiCOM signal "]
[16,43,"IM7 FrameSyncTim","Courier number (time)",null,"4x10555","4x10556",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1641 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application "]
[16,48,"IM8 Cmd Type","Indexed Strings",null,"4x10557",null,"G219","G219",null,null,"Direct ","Setting",0,3,1,2,"*","*","*","*","*",{"$nulls":6},"InterMiCOM signal 1"]
[16,49,"IM8 FallBackMode","Indexed Strings",null,"4x10558",null,"G215","G215",null,null,"Default","Setting",0,1,1,2,"*","*","*","*","*","1648 <> 1",{"$nulls":5},"Latch or Default"]
[16,"4A","IM8 DefaultValue","Unsigned Integer(16 bit)",null,"4x10559",null,null,"G1",null,null,0,"Setting",0,1,1,2,"*","*","*","*","*","1649 = 1",{"$nulls":5},"Assign logic 0 or 1 to InterMiCOM signal "]
[16,"4B","IM8 FrameSyncTim","Courier number (time)",null,"4x10560","4x10561",null,"G35",null,null,"1.5s","Setting",0.01,1.5,0.01,2,"*","*","*","*","*","1649 = 1",{"$nulls":5},"Upper, Lower and Step values defined by application "]
[17,0,"FUNCTION KEYS",{"$nulls":18},"*","0950 = 1"]
[17,1,"Fn Key Status","Binary Flag (10 bits)",{"$nulls":7},0,"Data",{"$nulls":8},"*",{"$nulls":7},"*"]
[null,null,null,"Indexed String"]
[17,2,"Fn Key 1","Indexed String",null,"4x10775",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":6},"Disabled/Unlocked/Locked","*"]
[17,3,"Fn Key 1 Mode","Indexed String",null,"4x10776",null,"G243","G243",null,1,"Toggled","Setting",0,1,1,2,{"$nulls":4},"*","1702 = 1",{"$nulls":5},"Normal/Toggled","*"]
[17,4,"Fn Key 1 Label","ASCII Text (16 chars)",null,"4x10777","4x10784",null,"G3",null,8,"Function Key 1","Setting",32,163,1,2,{"$nulls":4},"*","1702 <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,5,"Fn Key 2","Indexed String",null,"4x10785",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,6,"Fn Key 2 Mode","Indexed String",null,"4x10786",null,"G243","G243",null,1,"Normal","Setting",0,1,1,2,{"$nulls":4},"*","1705 = 1",{"$nulls":6},"*"]
[17,7,"Fn Key 2 Label","ASCII Text (16 chars)",null,"4x10787","4x10794",null,"G3",null,8,"Function Key 2","Setting",32,163,1,2,{"$nulls":4},"*","1705 <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,8,"Fn Key 3","Indexed String",null,"4x10795",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,9,"Fn Key 3 Mode","Indexed String",null,"4x10796",null,"G243","G243",null,1,"Normal","Setting",0,1,1,2,{"$nulls":4},"*","1708 = 1",{"$nulls":6},"*"]
[17,"0A","Fn Key 3 Label","ASCII Text (16 chars)",null,"4x10797","4x10804",null,"G3",null,8,"Function Key 3","Setting",32,163,1,2,{"$nulls":4},"*","1708 <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,"0B","Fn Key 4","Indexed String",null,"4x10805",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,"0C","Fn Key 4 Mode","Indexed String",null,"4x10806",null,"G243","G243",null,1,"Toggled","Setting",0,1,1,2,{"$nulls":4},"*","170B = 1",{"$nulls":6},"*"]
[17,"0D","Fn Key 4 Label","ASCII Text (16 chars)",null,"4x10807","4x10814",null,"G3",null,8,"Function Key 4","Setting",32,163,1,2,{"$nulls":4},"*","170B <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,"0E","Fn Key 5","Indexed String",null,"4x10815",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,"0F","Fn Key 5 Mode","Indexed String",null,"4x10816",null,"G243","G243",null,1,"Toggled","Setting",0,1,1,2,{"$nulls":4},"*","170E = 1",{"$nulls":6},"*"]
[17,10,"Fn Key 5 Label","ASCII Text (16 chars)",null,"4x10817","4x10824",null,"G3",null,8,"Function Key 5","Setting",32,163,1,2,{"$nulls":4},"*","170E <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,11,"Fn Key 6","Indexed String",null,"4x10825",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,12,"Fn Key 6 Mode","Indexed String",null,"4x10826",null,"G243","G243",null,1,"Toggled","Setting",0,1,1,2,{"$nulls":4},"*","1711 = 1",{"$nulls":6},"*"]
[17,13,"Fn Key 6 Label","ASCII Text (16 chars)",null,"4x10827","4x10834",null,"G3",null,8,"Function Key 6","Setting",32,163,1,2,{"$nulls":4},"*","1711 <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,14,"Fn Key 7","Indexed String",null,"4x10835",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,15,"Fn Key 7 Mode","Indexed String",null,"4x10836",null,"G243","G243",null,1,"Toggled","Setting",0,1,1,2,{"$nulls":4},"*","1714 = 1",{"$nulls":6},"*"]
[17,16,"Fn Key 7 Label","ASCII Text (16 chars)",null,"4x10837","4x10844",null,"G3",null,8,"Function Key 7","Setting",32,163,1,2,{"$nulls":4},"*","1714 <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,17,"Fn Key 8","Indexed String",null,"4x10845",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,18,"Fn Key 8 Mode","Indexed String",null,"4x10846",null,"G243","G243",null,1,"Normal","Setting",0,1,1,2,{"$nulls":4},"*","1717 = 1",{"$nulls":6},"*"]
[17,19,"Fn Key 8 Label","ASCII Text (16 chars)",null,"4x10847","4x10854",null,"G3",null,8,"Function Key 8","Setting",32,163,1,2,{"$nulls":4},"*","1717 <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,"1A","Fn Key 9","Indexed String",null,"4x10855",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,"1B","Fn Key 9 Mode","Indexed String",null,"4x10856",null,"G243","G243",null,1,"Normal","Setting",0,1,1,2,{"$nulls":4},"*","171A = 1",{"$nulls":6},"*"]
[17,"1C","Fn Key 9 Label","ASCII Text (16 chars)",null,"4x10857","4x10864",null,"G3",null,8,"Function Key 9","Setting",32,163,1,2,{"$nulls":4},"*","171A <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[17,"1D","Fn Key 10","Indexed String",null,"4x10865",null,"G242","G242",null,1,"Unlocked","Setting",0,2,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
[17,"1E","Fn Key 10 Mode","Indexed String",null,"4x10866",null,"G243","G243",null,1,"Normal","Setting",0,1,1,2,{"$nulls":4},"*","171D = 1",{"$nulls":6},"*"]
[17,"1F","Fn Key 10 Label","ASCII Text (16 chars)",null,"4x10867","4x10874",null,"G3",null,8,"Function Key 10","Setting",32,163,1,2,{"$nulls":4},"*","171D <> 0",{"$nulls":5},"Default PSL Text for Function Key DDB"]
[19,0,"IED CONFIGURATOR",{"$nulls":14},"*","*","*","*","*","0949  =  1",{"$nulls":5},"Build=IEC61850","*"]
[{"$nulls":22},"Build = IEC61850",{"$nulls":5},"Downloaded using IED Configurator"]
[19,5,"Switch Conf.Bank","Indexed String",null,null,null,"G248",null,null,null,"No Action","Command",0,1,1,2,"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,"0A","Restore MCL","Indexed String",null,null,null,"G256",null,null,null,"No Action","Command",0,1,1,2,"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,10,"Active Conf.Name","ASCII Text",{"$nulls":7},"Not Available","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,11,"Active Conf.Rev","ASCII Text",{"$nulls":7},"Not Available","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850"]
[19,20,"Inact.Conf.Name","ASCII Text",{"$nulls":7},"Not Available","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,21,"Inact.Conf.Rev","ASCII Text",{"$nulls":7},"Not Available","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,30,"IP PARAMETERS","Sub Heading",{"$nulls":13},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850"]
[19,31,"IP Address","ASCII Text",{"$nulls":7},"0.0.0.0","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,32,"Subnet mask","ASCII Text",{"$nulls":7},"0.0.0.0","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,33,"Gateway","ASCII Text",{"$nulls":7},"0.0.0.0","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850"]
[19,40,"SNTP PARAMETERS","Sub Heading",{"$nulls":13},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,41,"SNTP Server 1","ASCII Text",{"$nulls":7},"0.0.0.0","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,42,"SNTP Server 2","ASCII Text ",{"$nulls":7},"0.0.0.0","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850"]
[19,50,"IEC 61850 SCL","Sub Heading",{"$nulls":13},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,51,"IED Name","ASCII Text ",{"$nulls":7},"Not Available","Data",{"$nulls":4},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,60,"IEC 61850 GOOSE","Sub Heading",{"$nulls":13},"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850"]
[19,70,"GoEna","Binary Flag (32 bits)",{"$nulls":7},"0x00000000","Setting",0,1,1,2,"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850","*"]
[19,71,"Test Mode","Indexed String",null,null,null,"G246",null,null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850"]
[19,73,"Ignore Test Flag","ASCII Text ",null,null,null,"G11",null,null,null,"No","Setting",0,1,1,2,"*","*","*","*","*","Build=IEC61850",{"$nulls":5},"Build=IEC61850"]
[29,0,"CTRL I/P LABELS",{"$nulls":14},"*","*","*","*","*","0936 = 1"]
[29,1,"Control Input 1","ASCII Text (16 chars)",null,"4x10100","4x10107",null,"G3",null,8,"Control Input 1","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,2,"Control Input 2","ASCII Text (16 chars)",null,"4x10108","4x10115",null,"G3",null,8,"Control Input 2","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,3,"Control Input 3","ASCII Text (16 chars)",null,"4x10116","4x10123",null,"G3",null,8,"Control Input 3","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,4,"Control Input 4","ASCII Text (16 chars)",null,"4x10124","4x10131",null,"G3",null,8,"Control Input 4","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,5,"Control Input 5","ASCII Text (16 chars)",null,"4x10132","4x10139",null,"G3",null,8,"Control Input 5","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,6,"Control Input 6","ASCII Text (16 chars)",null,"4x10140","4x10147",null,"G3",null,8,"Control Input 6","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,7,"Control Input 7","ASCII Text (16 chars)",null,"4x10148","4x10155",null,"G3",null,8,"Control Input 7","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,8,"Control Input 8","ASCII Text (16 chars)",null,"4x10156","4x10163",null,"G3",null,8,"Control Input 8","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,9,"Control Input 9","ASCII Text (16 chars)",null,"4x10164","4x10171",null,"G3",null,8,"Control Input 9","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"0A","Control Input 10","ASCII Text (16 chars)",null,"4x10172","4x10179",null,"G3",null,8,"Control Input 10","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"0B","Control Input 11","ASCII Text (16 chars)",null,"4x10180","4x10187",null,"G3",null,8,"Control Input 11","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"0C","Control Input 12","ASCII Text (16 chars)",null,"4x10188","4x10195",null,"G3",null,8,"Control Input 12","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"0D","Control Input 13","ASCII Text (16 chars)",null,"4x10196","4x10203",null,"G3",null,8,"Control Input 13","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"0E","Control Input 14","ASCII Text (16 chars)",null,"4x10204","4x10211",null,"G3",null,8,"Control Input 14","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"0F","Control Input 15","ASCII Text (16 chars)",null,"4x10212","4x10219",null,"G3",null,8,"Control Input 15","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,10,"Control Input 16","ASCII Text (16 chars)",null,"4x10220","4x10227",null,"G3",null,8,"Control Input 16","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,11,"Control Input 17","ASCII Text (16 chars)",null,"4x10228","4x10235",null,"G3",null,8,"Control Input 17","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,12,"Control Input 18","ASCII Text (16 chars)",null,"4x10236","4x10243",null,"G3",null,8,"Control Input 18","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,13,"Control Input 19","ASCII Text (16 chars)",null,"4x10244","4x10251",null,"G3",null,8,"Control Input 19","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,14,"Control Input 20","ASCII Text (16 chars)",null,"4x10252","4x10259",null,"G3",null,8,"Control Input 20","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,15,"Control Input 21","ASCII Text (16 chars)",null,"4x10260","4x10267",null,"G3",null,8,"Control Input 21","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,16,"Control Input 22","ASCII Text (16 chars)",null,"4x10268","4x10275",null,"G3",null,8,"Control Input 22","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,17,"Control Input 23","ASCII Text (16 chars)",null,"4x10276","4x10283",null,"G3",null,8,"Control Input 23","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,18,"Control Input 24","ASCII Text (16 chars)",null,"4x10284","4x10291",null,"G3",null,8,"Control Input 24","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,19,"Control Input 25","ASCII Text (16 chars)",null,"4x10292","4x10299",null,"G3",null,8,"Control Input 25","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"1A","Control Input 26","ASCII Text (16 chars)",null,"4x10300","4x10307",null,"G3",null,8,"Control Input 26","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"1B","Control Input 27","ASCII Text (16 chars)",null,"4x10308","4x10315",null,"G3",null,8,"Control Input 27","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"1C","Control Input 28","ASCII Text (16 chars)",null,"4x10316","4x10323",null,"G3",null,8,"Control Input 28","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"1D","Control Input 29","ASCII Text (16 chars)",null,"4x10324","4x10331",null,"G3",null,8,"Control Input 29","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"1E","Control Input 30","ASCII Text (16 chars)",null,"4x10332","4x10339",null,"G3",null,8,"Control Input 30","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,"1F","Control Input 31","ASCII Text (16 chars)",null,"4x10340","4x10347",null,"G3",null,8,"Control Input 31","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[29,20,"Control Input 32","ASCII Text (16 chars)",null,"4x10348","4x10355",null,"G3",null,8,"Control Input 32","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":6},"Default PSL Text for Control Input DDB"]
[30,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","090B = 1",{"$nulls":6},"*"]
[null,null,"SYSTEM CONFIG"]
[30,2,"Phase Sequence","Indexed String",null,"4x01201",null,"G163","G163",null,null,"Standard ABC","Setting",0,1,1,2,"*","*","*","*","*"]
[30,3,"2NDHARM BLOCKING","(Sub-heading)"]
[30,4,"2nd Harmonic","Indexed String",null,"4x01202",null,"G37","G37",1,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[30,5,"2ndHarm Thresh ","Courier Number (percentage)",null,"4x01203",null,null,"G2",null,1,20,"Setting",5,70,1,2,"*","*","*","*","*","3004 = 1",{"$nulls":6},"*"]
[30,6,"I>lift 2H","Courier Number (current)",null,"4x01204",null,null,"G2",null,1,10,"Setting",4,32,0.01,2,"*","*","*","*","*","3004 = 1",{"$nulls":4},"M4",null,"*"]
[35,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0910 = 1","=",1,{"$nulls":4},"*"]
[null,null,"OVERCURRENT"]
[35,20,{"$nulls":26},"Spare "]
[35,21,{"$nulls":26},"Spare","*"]
[35,22,{"$nulls":26},"Spare (e.g. I>1 Status)","*"]
[35,23,"I>1 Function","Indexed String",null,"4x01250",null,"G150","G150",12,1,"IEC S Inverse","Setting",0,12,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[35,24,"I>1 Direction","Indexed String",null,"4x01251",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3523 <> 0",{"$nulls":6},"*"]
[35,25,{"$nulls":26},"Spare (e.g. I>1 RCA)","*"]
[35,26,{"$nulls":26},"Spare (e.g. I>1 Boundary)","*"]
[35,27,"I>1 Current Set","Courier Number (current)",null,"4x01252",null,null,"G2",392,1,1,"Setting",0.08,4,0.01,2,"*","*","*","*","*","3523 <> 0",{"$nulls":4},"M4",null,"*"]
[35,28,{"$nulls":26},"Spare (I>1 Current Set2)","*"]
[35,29,"I>1 Time Delay","Courier Number (time)",null,"4x01253",null,null,"G2",10000,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","3523 = 1",{"$nulls":6},"*"]
[35,"2A","I>1 TMS","Courier Number (decimal)",null,"4x01254",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","6>=3523>=2",{"$nulls":5},"Operate TMS","*"]
[35,"2B","I>1 Time Dial","Courier Number (decimal)",null,"4x01255",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","12>=3523>=8",{"$nulls":5},"Operate Time Dial","*"]
[35,"2C","I>1 k (RI)","Courier Number (decimal)",null,"4x01256",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","3523 = 7",{"$nulls":5},"Operate Time Multiplier","*"]
[35,"2D","I>1 DT Adder","Courier Number (time)",null,"4x01281",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3523 > = 2",">=",2,{"$nulls":4},"*"]
[35,"2E","I>1 Reset Char","Indexed String",null,"4x01257",null,"G60","G60",1,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","12>=3523>=8",{"$nulls":6},"*"]
[35,"2F","I>1 tRESET","Courier Number (time)",null,"4x01258",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF 7>=3523>=1 OR 352E=0",{"$nulls":6},"*"]
[35,30,{"$nulls":26},"Spare (e.g.I>1  K1 reset multiplier)","*"]
[35,31,{"$nulls":26},"Spare (e.g. I>2 Status)","*"]
[35,32,"I>2 Function","Indexed String",null,"4x01259",null,"G150","G150",12,1,"Disabled","Setting",0,12,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[35,33,"I>2 Direction","Indexed String",null,"4x01260",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3532 <> 0",{"$nulls":6},"*"]
[35,34,{"$nulls":26},"Spare (e.g. I>2 RCA)","*"]
[35,35,{"$nulls":26},"Spare (e.g. I>2 Boundary)","*"]
[35,36,"I>2 Current Set","Courier Number (current)",null,"4x01261",null,null,"G2",392,1,1,"Setting",0.08,4,0.01,2,"*","*","*","*","*","3532 <> 0",{"$nulls":4},"M4",null,"*"]
[35,37,{"$nulls":26},"Spare I>2 Current Set2)","*"]
[35,38,"I>2 Time Delay","Courier Number (time)",null,"4x01262",null,null,"G2",10000,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","3532 = 1",{"$nulls":6},"*"]
[35,39,"I>2 TMS","Courier Number (decimal)",null,"4x01263",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","6>=3532>=2",{"$nulls":5},"Operate TMS","*"]
[35,"3A","I>2 Time Dial","Courier Number (decimal)",null,"4x01264",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","12>=3532>=8",{"$nulls":5},"Operate Time Dial","*"]
[35,"3B","I>2 k (RI)","Courier Number (decimal)",null,"4x01265",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","3532 = 7",{"$nulls":6},"*"]
[35,"3C","I>2 DT Adder","Courier Number (time)",null,"4x01282",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,{"$nulls":5},"3532 > 1",">",1,null,null,null,"Spare (e.g. Operate k multiplier)","*"]
[35,"3D","I>2 Reset Char","Indexed String",null,"4x01266",null,"G60","G60",1,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","12>=3532>=8",{"$nulls":6},"*"]
[35,"3E","I>2 tRESET","Courier Number (time)",null,"4x01267",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF  7>=3532>=1 OR 353D=0",{"$nulls":6},"*"]
[35,"3F",{"$nulls":26},"Spare (e.g.I>2  K1 reset multiplier)","*"]
[35,40,"I>3 Status","Indexed String",null,"4x01268",null,"G37","G37",1,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[35,41,"I>3 Direction","Indexed String",null,"4x01269",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3540 = 1","=",1,{"$nulls":4},"*"]
[35,42,{"$nulls":26},"Spare (e.g. I>3 RCA)","*"]
[35,43,{"$nulls":26},"Spare (e.g. I>3 Boundary)","*"]
[35,44,"I>3 Current Set","Courier Number (current)",null,"4x01270",null,null,"G2",3192,1,20,"Setting",0.08,32,0.01,2,"*","*","*","*","*","3540 = 1","=",1,null,null,"M4",null,"*"]
[35,45,"I>3 Time Delay","Courier Number (time)",null,"4x01271",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3540 = 1","=",1,{"$nulls":4},"*"]
[35,46,{"$nulls":26},"Spare","*"]
[35,47,"I>4 Status","Indexed String",null,"4x01272",null,"G37","G37",1,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[35,48,"I>4 Direction","Indexed String",null,"4x01273",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3547 = 1",{"$nulls":6},"*"]
[35,49,{"$nulls":26},"Spare (e.g. I>4 RCA)","*"]
[35,"4A",{"$nulls":26},"Spare (e.g. I>4 Boundary)","*"]
[35,"4B","I>4 Current Set","Courier Number (current)",null,"4x01274",null,null,"G2",3192,1,20,"Setting",0.08,32,0.01,2,"*","*","*","*","*","3547 = 1",{"$nulls":4},"M4",null,"*"]
[35,"4C","I>4 Time Delay","Courier Number (time)",null,"4x01275",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3547 = 1",{"$nulls":6},"*"]
[35,"4D",{"$nulls":26},"Spare"]
[35,"4E","I> Blocking","Binary Flag (8 bits) ",null,"4x01276",null,"G14","G14",190,1,15,"Setting",null,"011111001111",1,2,"*",{"$nulls":10},"VTS Block/----/2nd Harm Block per stage","*"]
[{"$nulls":11},15,null,null,"011111111111",1,2,null,"*","*","*","*",{"$nulls":6},"VTS Block/AR/2nd Harm Block per stage"]
[35,"4F","I> Char Angle","Courier Number (angle)",null,"4x01277",null,null,"G2",190,1,45,"Setting",-95,95,1,2,"*","*","*","*","*",{"$nulls":6},"I> Characteristic Angle","*"]
[35,50,{"$nulls":26},"Spare"]
[35,51,"V CONTROLLED O/C","(Sub-heading)",{"$nulls":13},"*","*","*","*","*"]
[35,52,"VCO Status","Indexed String",null,"4x01278",null,"G100","G100",3,1,"Disabled","Setting",0,3,1,2,"*","*","*","*","*"]
[35,53,"VCO V< Setting","Courier Number (voltage)",null,"4x01279",null,null,"G2",100,1,60,"Setting",20,120,1,2,"*","*","*","*","*","3552 <> 0","<>",0,null,null,"M1"]
[35,54,"VCO k Setting","Courier Number (decimal)",null,"4x01280",null,null,"G2",15,1,0.25,"Setting",0.25,1,0.05,2,"*","*","*","*","*","3552 <> 0","<>",0]
[36,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0911 = 1","=",1,{"$nulls":4},"*"]
[null,null,"NEG SEQ O/C"]
[{"$nulls":28},"Previous menu cells removed"]
[36,10,"I2>1 Status","Indexed String",null,"4x01300",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[36,11,"I2>1 Function","Indexed String",null,"4x01301",null,"G166","G166",null,null,"DT","Setting",0,9,1,2,"*","*","*","*","*","3610 = 1","=",1,{"$nulls":4},"*"]
[36,12,"I2>1 Direction","Indexed String",null,"4x01302",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3610 = 1","=",1,{"$nulls":4},"*"]
[null,13,{"$nulls":26},"Spare (e.g. I2>1 RCA)"]
[null,14,{"$nulls":26},"Spare (e.g. I2>1 Boundary)"]
[36,15,"I2>1 Current Set","Courier Number (current)",null,"4x01303",null,null,"G2",null,1,0.2,"Setting","0.08*I1","4*I1","0.01*I1",2,"*","*","*","*","*","3610 = 1",{"$nulls":4},"M4",null,"*"]
[null,16,{"$nulls":26},"Spare I2>1 Current Set2)"]
[36,17,"I2>1 Time Delay","Courier Number (time)",null,"4x01304",null,null,"G2",null,1,10,"Setting",0,100,0.01,2,"*","*","*","*","*","(3610=1) AND (3611=0)",{"$nulls":6},"*"]
[36,18,"I2>1 TMS","Courier Number (decimal)",null,"4x01305",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","(3610=1) AND (4>=3611>=1)",{"$nulls":5},"IEC/UK only","*"]
[36,19,"I2>1 Time Dial","Courier Number (decimal)",null,"4x01306",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","(3610=1) AND (9>=3611>=5)",{"$nulls":5},"IEEE/US only","*"]
[36,"1A",{"$nulls":26},"Spare (e.g. I2>1 k (RI))"]
[36,"1B","I2>1 DT Adder","Courier Number (time)",null,"4x01307",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(3610=1) AND (3611>=1)",{"$nulls":5},"Not available for DT selection","*"]
[36,"1C","I2>1 Reset Char","Indexed String",null,"4x01308",null,"G60","G60",1,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","(3610=1) AND (9>=3611>=5)",{"$nulls":5},"Reset Characteristic","*"]
[36,"1D","I2>1 tRESET","Courier Number (time)",null,"4x01309",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(3610=1) AND (4>=3611>=0 OR",{"$nulls":6},"*"]
[{"$nulls":22},"(9>=3611>=5 AND 361C=0))"]
[36,"1E",{"$nulls":26},"Spare (e.g. I2>1 K1 reset multiplier)"]
[36,"1F",{"$nulls":26},"Spare"]
[36,20,"I2>2 Status","Indexed String",null,"4x01310",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[36,21,"I2>2 Function","Indexed String",null,"4x01311",null,"G166","G166",null,null,"DT","Setting",0,9,1,2,"*","*","*","*","*","3620 = 1","=",1,{"$nulls":4},"*"]
[36,22,"I2>2 Direction","Indexed String",null,"4x01312",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3620 = 1","=",1,{"$nulls":4},"*"]
[null,23,{"$nulls":26},"Spare (e.g. I2>2 RCA)"]
[null,24,{"$nulls":26},"Spare (e.g. I2>2 Boundary)"]
[36,25,"I2>2 Current Set","Courier Number (current)",null,"4x01313",null,null,"G2",null,1,0.2,"Setting","0.08*I1","4*I1","0.01*I1",2,"*","*","*","*","*","3620 = 1","=",1,null,null,"M4",null,"*"]
[null,26,{"$nulls":26},"Spare I2>2 Current Set2)"]
[36,27,"I2>2 Time Delay","Courier Number (time)",null,"4x01314",null,null,"G2",null,1,10,"Setting",0,100,0.01,2,"*","*","*","*","*","(3620=1) AND (3621=0)",{"$nulls":6},"*"]
[36,28,"I2>2 TMS","Courier Number (decimal)",null,"4x01315",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","(3620=1) AND (4>=3621>=1)",{"$nulls":6},"*"]
[{"$nulls":28},"Operate TMS"]
[36,29,"I2>2 Time Dial","Courier Number (decimal)",null,"4x01316",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","(3620=1) AND (9>=3621>=5)",{"$nulls":5},"Operate Time Dial","*"]
[36,"2A",{"$nulls":26},"Spare (e.g. I2>2 k (RI))"]
[36,"2B","I2>2 DT Adder","Courier Number (time)",null,"4x01317",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(3620=1) AND (3621>=1)",{"$nulls":5},"Not available for DT selection","*"]
[36,"2C","I2>2 Reset Char","Indexed String",null,"4x01318",null,"G60","G60",1,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","(3620=1) AND (9>=3621>=5)",{"$nulls":5},"Reset Characteristic","*"]
[36,"2D","I2>2 tRESET","Courier Number (time)",null,"4x01319",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(3620=1) AND (4>=3621>=0 OR",{"$nulls":6},"*"]
[{"$nulls":22},"(9>=3621>=5 AND 362C=0))"]
[36,"2E",{"$nulls":26},"Spare"]
[36,"2F",{"$nulls":26},"Spare"]
[36,30,"I2>3 Status","Indexed String",null,"4x01320",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[null,31,{"$nulls":26},"Spare e.g. I2>3 function"]
[36,32,"I2>3 Direction","Indexed String",null,"4x01321",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3630 = 1","=",1,{"$nulls":4},"*"]
[null,33,{"$nulls":26},"Spare (e.g. I2>3 RCA)"]
[null,34,{"$nulls":26},"Spare (e.g. I2>3 Boundary)"]
[36,35,"I2>3 Current Set","Courier Number (current)",null,"4x01322",null,null,"G2",null,1,0.2,"Setting","0.08*I1","32*I1","0.01*I1",2,"*","*","*","*","*","3630 = 1","=",1,null,null,"M4",null,"*"]
[null,36,{"$nulls":26},"Spare I2>3 Current Set2)"]
[36,37,"I2>3 Time Delay","Courier Number (time)",null,"4x01323",null,null,"G2",null,1,10,"Setting",0,100,0.01,2,"*","*","*","*","*","3630 = 1","=",1,{"$nulls":4},"*"]
[36,38,{"$nulls":26},"Spare (e.g. I2>3 TMS)"]
[36,39,{"$nulls":26},"Spare (e.g. I2>3 Time Dial)"]
[36,"3A",{"$nulls":26},"Spare (e.g. I2>3 k (RI))"]
[36,"3B",{"$nulls":26},"Spare (e.g. I2>3 k multiplier"]
[36,"3C",{"$nulls":26},"Spare (e.g. I2>3 Reset Char)"]
[36,"3D",{"$nulls":26},"Spare (e.g. I2>3 tRESET)"]
[36,"3E",{"$nulls":26},"Spare (e.g. I2>3 K1 reset multiplier)"]
[36,"3F",{"$nulls":26},"Spare"]
[36,40,"I2>4 Status","Indexed String",null,"4x01324",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[null,41,{"$nulls":26},"Spare e.g. I2>4 function"]
[36,42,"I2>4 Direction","Indexed String",null,"4x01325",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3640 = 1","=",1,{"$nulls":4},"*"]
[null,43,{"$nulls":26},"Spare (e.g. I2>4 RCA)"]
[null,44,{"$nulls":26},"Spare (e.g. I2>4 Boundary)"]
[36,45,"I2>4 Current Set","Courier Number (current)",null,"4x01326",null,null,"G2",null,1,0.2,"Setting","0.08*I1","32*I1","0.01*I1",2,"*","*","*","*","*","3640 = 1","=",1,null,null,"M4",null,"*"]
[null,46,{"$nulls":26},"Spare I2>4 Current Set2)"]
[36,47,"I2>4 Time Delay","Courier Number (time)",null,"4x01327",null,null,"G2",null,1,10,"Setting",0,100,0.01,2,"*","*","*","*","*","3640 = 1","=",1,{"$nulls":4},"*"]
[36,48,{"$nulls":26},"Spare (e.g. I2>4 TMS)"]
[36,49,{"$nulls":26},"Spare (e.g. I2>4 Time Dial)"]
[36,"4A",{"$nulls":26},"Spare (e.g. I2>4 k (RI))"]
[36,"4B",{"$nulls":26},"Spare (e.g. I2>4 k multiplier"]
[36,"4C",{"$nulls":26},"Spare (e.g. I2>4 Reset Char)"]
[36,"4D",{"$nulls":26},"Spare (e.g. I2>4 tRESET)"]
[36,"4E",{"$nulls":26},"Spare (e.g. I2>4 K1 reset multiplier)"]
[36,"4F",{"$nulls":26},"Spare"]
[36,50,"I2> Blocking","Binary Flag (8 bits) ",null,"4x01328",null,"G158","G158",190,1,"0x0F","Setting",null,11111111,1,2,"*","*","*","*","*",{"$nulls":6},"VTS/2nd Harmonic Block per stage","*"]
[36,51,"I2> Char Angle","Courier Number (angle)",null,"4x01329",null,null,"G2",360,1,-60,"Setting",-95,95,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[36,52,"I2> V2pol Set","Courier Number (voltage)",null,"4x01330",null,null,"G2",49,1,5,"Setting","0.5*V1","25*V1","0.5*V1",2,"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[37,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0912 = 1","=",1,{"$nulls":4},"*"]
[null,null,"BROKEN CONDUCTOR"]
[37,1,"Broken Conductor","Indexed String",null,"4x01350",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[37,2,"I2/I1 Setting","Courier Number (decimal)",null,"4x01351",null,null,"G2",80,1,0.2,"Setting",0.2,1,0.01,2,"*","*","*","*","*","3701 = 1",{"$nulls":6},"*"]
[37,3,"I2/I1 Time Delay","Courier Number (time)",null,"4x01352",null,null,"G2",1000,1,60,"Setting",0,100,0.1,2,"*","*","*","*","*","3701 = 1","=",1,{"$nulls":4},"*"]
[38,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0913 = 1",{"$nulls":6},"*"]
[null,null,"EARTH FAULT 1"]
[38,1,"IN1> Input","Indexed String",null,null,null,"G49","G49",null,1,"Measured","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"0=Measured","*"]
[38,22,{"$nulls":26},"Spare","*"]
[38,23,{"$nulls":26},"Spare","*"]
[38,24,{"$nulls":26},"Spare (e.g. IN1>1 Status)","*"]
[38,25,"IN1>1 Function","Indexed String",null,"4x01400",null,"G151","G151",12,1,"IEC S Inverse","Setting",0,12,1,2,"*","*","*","*","*",{"$nulls":6},"0=Disabled, 1=DT, 2 to 6=IDMT(UK), 7 to 11=IDMT(US), 12=IDG","*"]
[38,26,"IN1>1 Direction","Indexed String",null,"4x01401",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3825 <> 0","<>",0,{"$nulls":4},"*"]
[38,27,{"$nulls":26},"Spare (e.g. IN1>1 RCA)","*"]
[38,28,{"$nulls":26},"Spare (e.g. IN1>1 Boundary)","*"]
[38,29,"IN1>1 Current ","Courier Number (current)",null,"4x01402",null,null,"G2",392,1,0.2,"Setting",0.08,4,0.01,2,"*","*","*","*","*","3825 <> 0","<>",0,null,null,"M5","I>1 Current Setting","*"]
[38,"2A","IN1>1 IDG Is","Courier Number (decimal)",null,"4x01403",null,null,"G2",392,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","3825 = 12",{"$nulls":4},"M5","I>1 IDG Current Multiplier Setting","*"]
[38,"2B",{"$nulls":26},"Spare (IN1>1 Current Set2)","*"]
[38,"2C","IN1>1 Time Delay","Courier Number (time)",null,"4x01404",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","3825 = 1",{"$nulls":5},"I>1 Definite Time","*"]
[38,"2D","IN1>1 TMS","Courier Number (decimal)",null,"4x01405",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","SMF  5>=3825>=2",{"$nulls":6},"*"]
[38,"2E","IN1>1 Time Dial","Courier Number (decimal)",null,"4x01406",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","SMF  11>=3825>=7",{"$nulls":6},"*"]
[38,"2F","IN1>1 k (RI)","Courier Number (decimal)",null,"4x01407",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","3825 = 6",{"$nulls":6},"*"]
[38,30,"IN1>1 IDG Time","Courier Number (time)",null,"4x01408",null,null,"G2",100,1,1.2,"Setting",1,2,0.01,2,"*","*","*","*","*","3825 = 12",{"$nulls":6},"*"]
[38,31,"IN1>1 DT Adder","Courier Number (time)",null,"4x01436",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3825 >= 2 && 3825 <> 12",{"$nulls":5},"DT Adder","*"]
[38,32,"IN1>1 Reset Char","Indexed String",null,"4x01409",null,"G60","G60",1,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","SMF  11>=3825>=7",{"$nulls":6},"*"]
[38,33,"IN1>1 tRESET","Courier Number (time)",null,"4x01410",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF (6>=3825>=1) OR (3832=0 AND (11>=3825>=7)) ",{"$nulls":6},"*"]
[38,34,{"$nulls":26},"Spare (e.g. K1 reset multiplier)","*"]
[38,35,{"$nulls":26},"Spare (e.g. IN>2 Status)","*"]
[38,36,"IN1>2 Function","Indexed String",null,"4x01411",null,"G151","G151",12,1,"Disabled","Setting",0,12,1,2,"*","*","*","*","*",{"$nulls":6},"I>2 Overcurrent Status","*"]
[38,37,"IN1>2 Direction","Indexed String",null,"4x01412",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3836 <> 0","<>",0,{"$nulls":4},"*"]
[38,38,{"$nulls":26},"Spare (e.g. IN1>2 RCA)","*"]
[38,39,{"$nulls":26},"Spare (e.g. IN1>2 Boundary)","*"]
[38,"3A","IN1>2 Current","Courier Number (current)",null,"4x01413",null,null,"G2",392,1,0.2,"Setting",0.08,4,0.01,2,"*","*","*","*","*","3836 <> 0","<>",0,null,null,"M5","IN1>2 Current Setting","*"]
[38,"3B","IN1>2 IDG Is","Courier Number (decimal)",null,"4x01414",null,null,"G2",30,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","3836 = 12",{"$nulls":4},"M5","IN1>2 IDG Current Multiplier Setting","*"]
[38,"3C",{"$nulls":26},"Spare (IN1>2 Current Set2)","*"]
[38,"3D","IN1>2 Time Delay","Courier Number (time)",null,"4x01415",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","3836 = 1",{"$nulls":6},"*"]
[38,"3E","IN1>2 TMS","Courier Number (decimal)",null,"4x01416",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","SMF  5>=3836>=2",{"$nulls":6},"*"]
[38,"3F","IN1>2 Time Dial","Courier Number (decimal)",null,"4x01417",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","SMF  11>=3836>=7",{"$nulls":6},"*"]
[38,40,"IN1>2 k (RI)","Courier Number (decimal)",null,"4x01418",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","3836 = 6",{"$nulls":6},"*"]
[38,41,"IN1>2 IDG Time","Courier Number (time)",null,"4x01419",null,null,"G2",100,1,1.2,"Setting",1,2,0.01,2,"*","*","*","*","*","3836 = 12",{"$nulls":6},"*"]
[38,42,"IN1>2 DT Adder","Courier Number (time)",null,"4x01437",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3836 >= 2 && 3836 <> 12",{"$nulls":5},"DT Adder","*"]
[38,43,"IN1>2 Reset Char","Indexed String",null,"4x01420",null,"G60","G60",1,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","SMF  11>=3836>=7",{"$nulls":6},"*"]
[38,44,"IN1>2 tRESET","Courier Number (time)",null,"4x01421",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF  (6>=3836>=1) OR ",{"$nulls":6},"*"]
[{"$nulls":22},"(3843=0 AND (11>=3836>=7))"]
[38,45,{"$nulls":26},"Spare (e.g. K1 reset multiplier)","*"]
[38,46,"IN1>3 Status","Indexed String",null,"4x01422",null,"G37","G37",1,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[38,47,"IN1>3 Direction","Indexed String",null,"4x01423",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3846 = 1",{"$nulls":6},"*"]
[38,48,{"$nulls":26},"Spare (e.g. IN1>3 RCA)","*"]
[38,49,{"$nulls":26},"Spare (e.g. IN1>3 Boundary)","*"]
[38,"4A","IN1>3 Current","Courier Number (current)",null,"4x01424",null,null,"G2",3192,1,0.2,"Setting",0.08,32,0.01,2,"*","*","*","*","*","3846 = 1",{"$nulls":4},"M5",null,"*"]
[38,"4B","IN1>3 Time Delay","Courier Number (time)",null,"4x01425",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","3846 = 1",{"$nulls":6},"*"]
[38,"4C",{"$nulls":26},"Spare ","*"]
[38,"4D","IN1>4 Status","Indexed String",null,"4x01426",null,"G37","G37",1,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[38,"4E","IN1>4 Direction","Indexed String",null,"4x01427",null,"G44","G44",2,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","384D = 1",{"$nulls":6},"*"]
[38,"4F",{"$nulls":26},"Spare (e.g. IN1>4 RCA)","*"]
[38,50,{"$nulls":26},"Spare (e.g. IN1>4 Boundary)","*"]
[38,51,"IN1>4 Current","Courier Number (current)",null,"4x01428",null,null,"G2",3192,1,0.2,"Setting",0.08,32,0.01,2,"*","*","*","*","*","384D = 1",{"$nulls":4},"M5",null,"*"]
[38,52,"IN1>4 Time Delay","Courier Number (time)",null,"4x01429",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","384D = 1",{"$nulls":6},"*"]
[38,53,{"$nulls":26},"Spare ","*"]
[38,54,"IN1> Blocking","Binary Flag (8 bits)",null,"4x01430",null,"G63","G63",190,1,15,"Setting",null,"001111001111",1,2,"*",{"$nulls":10},"VTS Block/----/2nd Harm Block per stage","*"]
[{"$nulls":11},15,null,null,"001111111111",1,2,null,"*","*","*","*",{"$nulls":6},"VTS Block/AR/2nd Harm Block per stage"]
[38,55,"IN1> POL","(Sub Heading)",{"$nulls":12},2,"*","*","*","*","*",{"$nulls":7},"*"]
[38,56,"IN1> Char Angle","Courier Number (angle)",null,"4x01431",null,null,"G2",190,1,-45,"Setting",-95,95,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[38,57,"IN1> Pol","Indexed String",null,"4x01432",null,"G46","G46",1,1,"Zero Sequence","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"0=Zero Seq, 1=Neg Seq","*"]
[38,58,{"$nulls":26},"Spare "]
[38,59,"IN1> VNpol Set","Courier Number (voltage)",null,"4x01433",null,null,"G2",159,1,5,"Setting",0.5,80,0.5,2,"*","*","*",null,"*","3857 = 0",{"$nulls":4},"M1","IN1> VN Polarising Setting","*"]
[{"$nulls":11},20,null,0.5,80,0.5,{"$nulls":4},"*",{"$nulls":6},"M3"]
[38,"5A","IN1> V2pol Set","Courier Number (voltage)",null,"4x01434",null,null,"G2",49,1,5,"Setting",0.5,25,0.5,2,"*","*","*","*","*","3857 = 1",{"$nulls":4},"M1","IN1> V2 Polarising Setting","*"]
[38,"5B","IN1> I2pol Set","Courier Number (current)",null,"4x01435",null,null,"G2",92,1,0.08,"Setting",0.08,1,0.01,2,"*","*","*","*","*","3857 = 1",{"$nulls":4},"M4","IN1> I2 Polarising Setting","*"]
[39,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0914 = 1"]
[null,null,"EARTH FAULT 2"]
[39,1,"IN2> Input","Indexed String",null,null,null,"G49","G49",null,1,"Derived","Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":7},"*"]
[39,22,{"$nulls":26},"Spare","*"]
[39,23,{"$nulls":26},"Spare","*"]
[39,24,{"$nulls":26},"Spare (e.g. IN2>1 Status)","*"]
[39,25,"IN2>1 Function","Indexed String",null,"4x01450",null,"G151","G151",null,1,"IEC S Inverse","Setting",0,12,1,2,"*","*","*","*","*",{"$nulls":6},"0=Disabled, 1=DT, 2 to 6=IDMT(UK)","*"]
[{"$nulls":28},"7 to 11=IDMT(US), 12=IDG"]
[39,26,"IN2>1 Direction","Indexed String",null,"4x01451",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3925 <> 0",{"$nulls":6},"*"]
[39,27,{"$nulls":26},"Spare (e.g. IN2>1 RCA)","*"]
[39,28,{"$nulls":26},"Spare (e.g. IN2>1 Boundary)","*"]
[39,29,"IN2>1 Current ","Courier Number (current)",null,"4x01452",null,null,"G2",392,1,0.2,"Setting",0.08,4,0.01,2,"*","*","*","*","*","3925 <> 0",{"$nulls":4},"M4","I>1 Current Setting","*"]
[39,"2A","IN2>1 IDG Is","Courier Number (decimal)",null,"4x01453",null,null,"G2",392,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","3925 = 12",{"$nulls":4},"M4","I>1 IDG Current Multiplier Setting","*"]
[39,"2B",{"$nulls":26},"Spare (IN2>1 Current Set2)","*"]
[39,"2C","IN2>1 Time Delay","Courier Number (time)",null,"4x01454",null,null,"G2",10000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","3925 = 1",{"$nulls":5},"I>1 Definite Time","*"]
[39,"2D","IN2>1 TMS","Courier Number (decimal)",null,"4x01455",null,null,"G2",47,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","SMF  5>=3925>=2",{"$nulls":6},"*"]
[39,"2E","IN2>1 Time Dial","Courier Number (decimal)",null,"4x01456",null,null,"G2",47,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","SMF  11>=3925>=7",{"$nulls":6},"*"]
[39,"2F","IN2>1 k (RI)","Courier Number (decimal)",null,"4x01457",null,null,"G2",47,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","3925 = 6",{"$nulls":6},"*"]
[39,30,"IN2>1 IDG Time","Courier Number (time)",null,"4x01458",null,null,"G2",47,1,1.2,"Setting",1,2,0.01,2,"*","*","*","*","*","3925 = 12",{"$nulls":6},"*"]
[39,31,"IN2>1 DT Adder","Courier Number (time)",null,"4x01486",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3925 >= 2 && 3925 <> 12",{"$nulls":5},"DT Adder","*"]
[39,32,"IN2>1 Reset Char","Indexed String",null,"4x01459",null,"G60","G60",null,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","SMF  11>=3925>=7",{"$nulls":6},"*"]
[39,33,"IN2>1 tRESET","Courier Number (time)",null,"4x01460",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF  6>=3925>=1 OR",{"$nulls":6},"*"]
[{"$nulls":22},"(3932=0 AND (11>=3925>=7))"]
[39,34,{"$nulls":26},"Spare (e.g. K1 reset multiplier)","*"]
[39,35,{"$nulls":26},"Spare (e.g. IN>2 Status)","*"]
[39,36,"IN2>2 Function","Indexed String",null,"4x01461",null,"G151","G151",null,1,"Disabled","Setting",0,12,1,2,"*","*","*","*","*",{"$nulls":6},"I>2 Overcurrent Status","*"]
[39,37,"IN2>2 Direction","Indexed String",null,"4x01462",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3936 <> 0",{"$nulls":6},"*"]
[39,38,{"$nulls":26},"Spare (e.g. IN2>2 RCA)","*"]
[39,39,{"$nulls":26},"Spare (e.g. IN2>2 Boundary)","*"]
[39,"3A","IN2>2 Current","Courier Number (current)",null,"4x01463",null,null,"G2",392,1,0.2,"Setting",0.08,4,0.01,2,"*","*","*","*","*","3936 <> 0",{"$nulls":4},"M4","IN2>2 Current Setting","*"]
[39,"3B","IN2>2 IDG Is","Courier Number (decimal)",null,"4x01464",null,null,"G2",30,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","3936 = 12","=",12,null,null,"M4","IN2>2 IDG Current Multiplier Setting","*"]
[39,"3C",{"$nulls":26},"Spare (IN2>2 Current Set2)","*"]
[39,"3D","IN2>2 Time Delay","Courier Number (time)",null,"4x01465",null,null,"G2",10000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","3936 = 1",{"$nulls":6},"*"]
[39,"3E","IN2>2 TMS","Courier Number (decimal)",null,"4x01466",null,null,"G2",47,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*"," 5>=3936>=2",{"$nulls":6},"*"]
[39,"3F","IN2>2 Time Dial","Courier Number (decimal)",null,"4x01467",null,null,"G2",47,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","11>=3936>=7",{"$nulls":6},"*"]
[39,40,"IN2>2 k (RI)","Courier Number (decimal)",null,"4x01468",null,null,"G2",47,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","3936 = 6",{"$nulls":6},"*"]
[39,41,"IN2>2 IDG Time","Courier Number (time)",null,"4x01469",null,null,"G2",47,1,1.2,"Setting",1,2,0.01,2,"*","*","*","*","*","3936 = 12",{"$nulls":6},"*"]
[39,42,"IN2>2 DT Adder","Courier Number (time)",null,"4x01487",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,{"$nulls":5},"3936 >= 2 && 3936 <> 12",{"$nulls":5},"DT Adder","*"]
[39,43,"IN2>2 Reset Char","Indexed String",null,"4x01470",null,"G60","G60",null,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","11>=3936>=7",{"$nulls":6},"*"]
[39,44,"IN2>2 tRESET","Courier Number (time)",null,"4x01471",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF  6>=3936>=1 OR",{"$nulls":6},"*"]
[{"$nulls":22},"(3943=0 AND (11>=3936>=7))"]
[39,45,{"$nulls":26},"Spare (e.g. K1 reset multiplier)","*"]
[39,46,"IN2>3 Status","Indexed String",null,"4x01472",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[39,47,"IN2>3 Direction","Indexed String",null,"4x01473",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","3946 = 1",{"$nulls":6},"*"]
[39,48,{"$nulls":26},"Spare (e.g. IN2>3 RCA)","*"]
[39,49,{"$nulls":26},"Spare (e.g. IN2>3 Boundary)","*"]
[39,"4A","IN2>3 Current","Courier Number (current)",null,"4x01474",null,null,"G2",3192,1,0.2,"Setting",0.08,32,0.01,2,"*","*","*","*","*","3946 = 1",{"$nulls":4},"M4",null,"*"]
[39,"4B","IN2>3 Time Delay","Courier Number (time)",null,"4x01475",null,null,"G2",10000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","3946 = 1",{"$nulls":6},"*"]
[39,"4C",{"$nulls":26},"Spare ","*"]
[39,"4D","IN2>4 Status","Indexed String",null,"4x01476",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[39,"4E","IN2>4 Direction","Indexed String",null,"4x01477",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","394D = 1",{"$nulls":6},"*"]
[39,"4F",{"$nulls":26},"Spare (e.g. IN2>4 RCA)","*"]
[39,50,{"$nulls":26},"Spare (e.g. IN2>4 Boundary)","*"]
[39,51,"IN2>4 Current","Courier Number (current)",null,"4x01478",null,null,"G2",3192,1,0.2,"Setting",0.08,32,0.01,2,"*","*","*","*","*","394D = 1",{"$nulls":4},"M4",null,"*"]
[39,52,"IN2>4 Time Delay","Courier Number (time)",null,"4x01479",null,null,"G2",10000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","394D = 1",{"$nulls":6},"*"]
[39,53,{"$nulls":26},"Spare ","*"]
[39,54,"IN2> Blocking","Binary Flag (8 bits)",null,"4x01480",null,"G63","G63",190,1,15,"Setting",null,"001111001111",1,2,"*",{"$nulls":10},"VTS Block/----/2nd Harm Block per stage","*"]
[{"$nulls":11},15,null,null,"001111111111",1,2,null,"*","*","*","*",{"$nulls":6},"VTS Block/AR/2nd Harm Block per stage"]
[39,55,"IN2> POL","(Sub Heading)",{"$nulls":12},2,"*","*","*","*","*",{"$nulls":7},"*"]
[39,56,"IN2> Char Angle","Courier Number (angle)",null,"4x01481",null,null,"G2",190,1,-45,"Setting",-95,95,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[39,57,"IN2> Pol","Indexed String",null,"4x01482",null,"G46","G46",null,1,"Zero Sequence","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":6},"0=Zero Seq, 1=Neg Seq","*"]
[39,58,{"$nulls":26},"Spare "]
[39,59,"IN2> VNpol Set","Courier Number (voltage)",null,"4x01483",null,null,"G2",43,1,5,"Setting",0.5,80,0.5,2,"*","*","*","*","*","3957 = 1",{"$nulls":4},"M1","IN2> VN Polarising Setting","*"]
[{"$nulls":11},20,null,0.5,80,0.5,{"$nulls":4},"*",{"$nulls":6},"M3"]
[39,"5A","IN2> V2pol Set","Courier Number (voltage)",null,"4x01484",null,null,"G2",49,1,5,"Setting",0.5,25,0.5,2,"*","*","*","*","*","3957 = 1",{"$nulls":4},"M1","IN2> V2 Polarising Setting","*"]
[]
[39,"5B","IN2> I2pol Set","Courier Number (current)",null,"4x01485",null,null,"G2",92,1,0.08,"Setting",0.08,1,0.01,2,"*","*","*","*","*","3957 = 1",{"$nulls":4},"M4","IN2> I2 Polarising Setting","*"]
["3A",0,"GROUP 1",{"$nulls":14},"*","*","*",null,"*","0915 = 1",{"$nulls":6},"*"]
[null,null,"SEF/REF PROT'N"]
["3A",1,"SEF/REF Options","Indexed String",null,"4x01500",null,"G58","G58",null,1,"SEF","Setting",0,7,1,2,"*","*","*",null,"*",{"$nulls":6},"Sensitive Earth Fault Options","*"]
[null,null,"SEF Options","Indexed String",null,"4x01500",null,"G58","G58",null,1,"SEF",null,0,3,1,2,null,null,null,"*"]
["3A",27,{"$nulls":26},"Spare","*"]
["3A",28,{"$nulls":26},"Spare ","*"]
["3A",29,{"$nulls":26},"Spare (e.g. ISEF>1 Status)","*"]
["3A","2A","ISEF>1 Function","Indexed String",null,"4x01501",null,"G152","G152",null,1,"DT","Setting",0,12,1,2,"*","*","*","*","*","SMF  (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
["3A","2B","ISEF>1 Direction","Indexed String",null,"4x01502",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,{"$nulls":5},"SMF  (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>1 Directionality","*"]
["3A","2C",{"$nulls":26},"Spare (e.g. ISEF>1 RCA)"]
["3A","2D",{"$nulls":26},"Spare (e.g. ISEF>1 Boundary)"]
["3A","2E","ISEF>1 Current","Courier Number (current)",null,"4x01503",null,null,"G2",392,1,0.05,"Setting",0.005,0.1,0.00025,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":4},"M6","ISEF>1 Current Setting including EPATR","*"]
[{"$nulls":22},"AND (3A2A<>=0)"]
["3A","2F","ISEF>1 IDG Is","Courier Number (decimal)",null,"4x01504",null,null,"G2",392,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>1 IDG Current Multiplier Setting","*"]
[{"$nulls":22},"AND (3A2A=11)"]
["3A",30]
["3A",31,"ISEF>1 Delay","Courier Number (time)",null,"4x01505",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>1 Definite Time","*"]
[{"$nulls":22},"AND (3A2A=1)","AND (3A2A=1)"]
["3A",32,"ISEF>1 TMS","Courier Number (decimal)",null,"4x01506",null,null,"G2",47,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","SMF  (3A01<=3 OR 3A01>=6) AND",{"$nulls":5},"ISEF>1 TMS","*"]
[{"$nulls":22},"((3A2A>=2 AND 3A2A<=5) OR 3A2A=12)"]
["3A",33,"ISEF>1 Time Dial","Courier Number (decimal)",null,"4x01507",null,null,"G2",47,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>1 Time Dial","*"]
[{"$nulls":22},"AND (3A2A>=6 AND 3A2A<=10)"]
["3A",34,"ISEF>1 IDG Time","Courier Number (time)",null,"4x01508",null,null,"G2",47,1,1.2,"Setting",1,2,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>1 IDG","*"]
[{"$nulls":22},"AND (3A2A=11)","AND (3A2A=11)"]
["3A",35,"ISEF>1 DT Adder","Courier Number (time)",null,"4x01538",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3A2A >= 2 && 3A2A<> 11",{"$nulls":5},"DT Adder","*"]
["3A",36,"ISEF>1 Reset Chr","Indexed String",null,"4x01509",null,"G60","G60",null,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
[{"$nulls":22},"AND (3A2A>=6 AND 3A2A<=10)"]
["3A",37,"ISEF>1 tRESET","Courier Number (time)",null,"4x01510",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
[{"$nulls":22},"AND (5>=3A2A>=1 OR "]
[{"$nulls":22},"(3A36=0 AND 10>=3A2A>=6))"]
["3A",38,{"$nulls":26},"Spare (e.g. K1 reset multiplier)","*"]
["3A",39,{"$nulls":26},"Spare (e.g. ISEF>2 Status)","*"]
["3A","3A","ISEF>2 Function","Indexed String",null,"4x01511",null,"G152","G152",null,1,"Disabled","Setting",0,12,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
["3A","3B","ISEF>2 Direction","Indexed String",null,"4x01512",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
[{"$nulls":22},"AND (3A3A<>0)"]
["3A","3C",{"$nulls":26},"Spare (e.g. ISEF>2 RCA)","*"]
["3A","3D",{"$nulls":26},"Spare (e.g. ISEF>2 Boundary)","*"]
["3A","3E","ISEF>2 Current","Courier Number (current)",null,"4x01513",null,null,"G2",392,1,0.05,"Setting",0.005,0.1,0.00025,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":4},"M6",null,"*"]
[{"$nulls":22},"AND (3A3A<>0)"]
["3A","3F","ISEF>2 IDG Is","Courier Number (decimal)",null,"4x01514",null,null,"G2",392,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>2 IDG Current Multiplier Setting","*"]
[{"$nulls":22},"AND (3A3A=11)"]
["3A",40,{"$nulls":27},"*"]
["3A",41,"ISEF>2 Delay","Courier Number (time)",null,"4x01515",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
[{"$nulls":22},"AND 3A3A=1"]
["3A",42,"ISEF>2 TMS","Courier Number (decimal)",null,"4x01516",null,null,"G2",47,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6) AND",{"$nulls":6},"*"]
[{"$nulls":22},"((3A3A>=2 AND 3A3A<=5) OR 3A3A=12)"]
["3A",43,"ISEF>2 Time Dial","Courier Number (decimal)",null,"4x01517",null,null,"G2",47,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"((3A01<=3) OR (3A01>=6)) & (3A0A >= 6)","*"]
[{"$nulls":22},"AND (3A3A>=6 AND 3A3A<=10)"]
["3A",44,"ISEF>2 IDG Time","Courier Number (time)",null,"4x01518",null,null,"G2",47,1,1.2,"Setting",1,2,0.01,2,"*","*","*",null,"*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>1 TMS","*"]
[{"$nulls":22},"AND (3A3A=11)",{"$nulls":5},"((3A01<=3) | (3A01>=6)) & (3A02 >= 6)"]
["3A",45,"ISEF>2 DT Adder","Courier Number (time)",null,"4x01539",null,null,"G2",null,null,0,"Setting",0,100,0.01,2,{"$nulls":5},"3A3A >= 2 && 3A3A<> 11",{"$nulls":5},"DT Adder","*"]
["3A",46,"ISEF>2 Reset Chr","Indexed String",null,"4x01519",null,"G60","G60",null,1,"DT","Setting",0,1,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
[{"$nulls":22},"AND (10>=3A3A>=6)"]
["3A",47,"ISEF>2 tRESET","Courier Number (time)",null,"4x01520",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
[{"$nulls":22},"AND (5>=3A3A>=1 OR "]
[{"$nulls":22},"(3A46=0 AND 10>=3A3A>=6))"]
["3A",48,{"$nulls":26},"Spare (e.g. K1 reset multiplier)"]
["3A",49,"ISEF>3 Status","Indexed String",null,"4x01521",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>3 Status ","*"]
["3A","4A","ISEF>3 Direction","Indexed String",null,"4x01522",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>3 Directionality","*"]
[{"$nulls":22},"AND (3A49=1)"]
["3A","4B",{"$nulls":26},"Spare (e.g. ISEF>3 RCA)"]
["3A","4C",{"$nulls":26},"Spare (e.g. ISEF>3 Boundary)"]
["3A","4D","ISEF>3 Current","Courier Number (current)",null,"4x01523",null,null,"G2",399,1,0.4,"Setting",0.005,2,0.001,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":4},"M6","ISEF>3 Current Setting","*"]
[{"$nulls":22},"AND (3A49=1)"]
["3A","4E","ISEF>3 Delay","Courier Number (time)",null,"4x01524",null,null,"G2",20000,1,0.5,"Setting",0,200,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>3 Definite Time","*"]
[{"$nulls":22},"AND (3A49=1)"]
["3A","4F",{"$nulls":26},"Spare"]
["3A",50,"ISEF>4 Status","Indexed String",null,"4x01525",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>4 Status ","*"]
["3A",51,"ISEF>4 Direction","Indexed String",null,"4x01526",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>4 Directionality","*"]
[{"$nulls":22},"AND (3A50=1)"]
["3A",52,{"$nulls":26},"Spare (e.g. ISEF>4 RCA)"]
["3A",53,{"$nulls":26},"Spare (e.g. ISEF>4 Boundary)"]
["3A",54,"ISEF>4 Current","Courier Number (current)",null,"4x01527",null,null,"G2",399,1,0.6,"Setting",0.005,2,0.001,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":4},"M6","ISEF>4 Current Setting","*"]
[{"$nulls":22},"AND (3A50=1)"]
["3A",55,"ISEF>4 Delay","Courier Number (time)",null,"4x01528",null,null,"G2",20000,1,0.25,"Setting",0,200,0.01,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF>4 Definite Time","*"]
[{"$nulls":22},"AND (3A50=1)",{"$nulls":5},"((3A01<=3) | (3A01>=6)) & (3A16 ==1)"]
["3A",56,{"$nulls":26},"Spare"]
["3A",57,"ISEF> Blocking","Binary Flag (8 bits)",null,"4x01529",null,"G64","G64",190,1,15,"Setting",null,"001111001111",1,2,"*",{"$nulls":4},"SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"VTS Block/----/2nd Harm Block per stage","*"]
[{"$nulls":11},15,"Setting",null,"001111111111",1,2,null,"*","*","*","*",{"$nulls":6},"VTS Block/AR/2nd Harm Block per stage"]
["3A",58,"ISEF POL","(Sub Heading)",{"$nulls":12},2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"ISEF> Directional","*"]
["3A",59,"ISEF> Char Angle","Courier Number (angle)",null,"4x01530",null,null,"G2",190,1,90,"Setting",-95,95,1,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":5},"Characteristic Angle","*"]
["3A","5A",{"$nulls":26},"Spare"]
["3A","5B","ISEF> VNpol Set","Courier Number (voltage)",null,"4x01531",null,null,"G2",43,1,5,"Setting",0.5,80,0.5,2,"*","*","*","*","*","SMF (3A01<=3 OR 3A01>=6)",{"$nulls":4},"M1","Polarisation Voltage Vop>","*"]
[{"$nulls":11},20,"Setting",0.5,80,0.5,2,null,null,null,"*",{"$nulls":6},"M3"]
["3A","5C",{"$nulls":26},"Spare"]
["3A","5D","WATTMETRIC SEF","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","SMF (3A01=7 OR 3A01=3)",{"$nulls":5},"Wattmetric Earth Fault","*"]
["3A","5E","PN> Setting","Courier Number (power)",null,"4x01532",null,null,"G2",400,1,9,"Setting",0,20,0.05,2,"*","*","*",null,"*","SMF (3A01=7 OR 3A01=3)",{"$nulls":4},"M1*M6","PN> Power Setting","*"]
[{"$nulls":11},36,"Setting",0,80,2,2,null,null,null,"*",{"$nulls":6},"M3*M6"]
["3A","5F",{"$nulls":26},"Spare"]
["3A",60,"RESTRICTED E/F","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","(3A01>=4 AND 3A01<=7)",{"$nulls":5},"Restricted Earth Fault","*"]
["3A",61,"IREF> k1","Courier Number (percentage)",null,"4x01533",null,null,"G2",20,1,20,"Setting",0,20,1,2,"*","*","*","*","*","(3A01>=5 AND 3A01<=7)",{"$nulls":5},"REF K1  (Low Impedance REF)","*"]
["3A",62,"IREF> k2","Courier Number (percentage)",null,"4x01534",null,null,"G2",150,1,150,"Setting",0,150,1,2,"*","*","*","*","*","(3A01>=5 AND 3A01<=7)",{"$nulls":5},"REF K2  (Low Impedance REF)","*"]
["3A",63,"IREF> Is1","Courier Number (current)",null,"4x01535",null,null,"G2",92,1,0.2,"Setting",0.08,1,0.01,2,"*","*","*","*","*","(3A01>=5 AND 3A01<=7)",{"$nulls":4},"M4","REF Is1  (Low Impedance REF)","*"]
["3A",64,"IREF> Is2","Courier Number (current)",null,"4x01536",null,null,"G2",140,1,1,"Setting",0.1,1.5,0.01,2,"*","*","*","*","*","(3A01>=5 AND 3A01<=7)",{"$nulls":4},"M4","REF Is2  (Low Impedance REF)","*"]
["3A",65,"IREF> Is","Courier Number (current)",null,"4x01537",null,null,"G2",95,1,0.2,"Setting",0.05,1,0.01,2,"*","*","*","*","*","3A01 = 4",{"$nulls":4},"M6","REF Is  (High Impedance REF)","*"]
["3B",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0916 = 1","=",1,{"$nulls":4},"*"]
[null,null,"RESIDUAL O/V NVD"]
["3B",1,"VN Input","Indexed String",null,null,null,"G49","G49",null,1,"Derived","Data",{"$nulls":4},"*","*","*",null,"*",{"$nulls":6},"Derived VN Input only","*"]
[{"$nulls":11},"Measured",{"$nulls":8},"*"]
["3B",2,"VN>1 Function","Indexed String",null,"4x01550",null,"G23","G23",null,1,"DT","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["3B",3,"VN>1 Voltage Set","Courier Number (voltage)",null,"4x01551",null,null,"G2",49,1,5,"Setting","1*V1","80*V1","1*V1",2,"*","*","*",null,"*","3B02 <> 0","<>",0,null,null,"M1",null,"*"]
[{"$nulls":11},20,null,"1*V3","80*V3","1*V3",{"$nulls":4},"*",{"$nulls":6},"M3"]
["3B",4,"VN>1 Time Delay","Courier Number (time)",null,"4x01552",null,null,"G2",1000,1,5,"Setting",0,100,0.01,2,"*","*","*","*","*","3B02 = 1",{"$nulls":6},"*"]
["3B",5,"VN>1 TMS","Courier Number (decimal)",null,"4x01553",null,null,"G2",199,1,1,"Setting",0.5,100,0.5,2,"*","*","*","*","*","3B02 = 2",{"$nulls":6},"*"]
["3B",6,"VN>1 tReset","Courier Number (time)",null,"4x01554",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","3B02 <> 0",{"$nulls":6},"*"]
["3B",7,"VN>2 Status","Indexed String",null,"4x01555",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["3B",8,"VN>2 Voltage Set","Courier Number (voltage)",null,"4x01556",null,null,"G2",49,1,10,"Setting","1*V1","80*V1","1*V1",2,"*","*","*",null,"*","3B07 = 1","=",1,null,null,"M1",null,"*"]
[{"$nulls":11},40,null,"1*V3","80*V3","1*V3",{"$nulls":4},"*",{"$nulls":6},"M3"]
["3B",9,"VN>2 Time Delay","Courier Number (time)",null,"4x01557",null,null,"G2",1000,1,10,"Setting",0,100,0.01,2,"*","*","*","*","*","3B07 = 1","=",1,{"$nulls":4},"*"]
["3C",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0917 = 1","=",1]
[null,null,"THERMAL OVERLOAD"]
["3C",1,"Characteristic","Indexed String",null,"4x01600",null,"G67","G67",null,1,"Single","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":6},"Thermal overload options"]
["3C",2,"Thermal Trip","Courier Number (current)",null,"4x01601",null,null,"G2",null,1,1,"Setting","0.08*I1","4.0*I1","0.01*I1",2,"*","*","*","*","*","3C01 >= 1",{"$nulls":4},"M4"]
["3C",3,"Thermal Alarm","Courier Number (percentage)",null,"4x01602",null,null,"G2",null,1,70,"Setting",50,100,1,2,"*","*","*","*","*","3C01 >= 1"]
["3C",4,"Time Constant 1","Courier Number (time-minutes)",null,"4x01603",null,null,"G2",null,1,10,"Setting",1,200,1,2,"*","*","*","*","*","3C01 >= 1"]
["3C",5,"Time Constant 2","Courier Number (time-minutes)",null,"4x01604",null,null,"G2",null,1,5,"Setting",1,200,1,2,"*","*","*","*","*","3C01 = 2"]
["3D",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0918 = 1","=",1]
[null,null,"NEG SEQUENCE O/V"]
["3D",1,"V2> Status","Indexed String",null,"4x01650",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*"]
["3D",2,"V2> Voltage Set","Courier Number (voltage)",null,"4x01651",null,null,"G2",null,1,15,"Setting","1*V1","110*V1","1*V1",2,"*","*","*","*","*","3D01 = 1","=",1,null,null,"M1"]
["3D",3,"V2> Time Delay","Courier Number (time)",null,"4x01652",null,null,"G2",null,1,5,"Setting",0,100,0.01,2,"*","*","*","*","*","3D01 = 1","=",1]
["3E",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0919 = 1","=",1]
[null,null,"COLD LOAD PICKUP"]
["3E",1,"tcold Time Delay","Courier Number (time)",null,"4x01700",null,null,"G2",null,1,7200,"Setting",0,14400,1,2,"*","*","*","*","*",{"$nulls":6},"CB open time for load to become cold"]
["3E",2,"tclp Time Delay","Courier Number (time)",null,"4x01701",null,null,"G2",null,1,7200,"Setting",0,14400,1,2,"*","*","*","*","*",{"$nulls":6},"CB closed time after which load is warm"]
["3E",20,"OVERCURRENT","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","(0910=1)"]
["3E",21,"I>1 Status","Indexed String",null,"4x01702",null,"G106","G106",1,1,"Enable","Setting",0,1,1,2,"*","*","*","*","*","(3523<>0) && (0910=1)"]
["3E",22,"I>1 Current Set","Courier Number (current)",null,"4x01703",null,null,"G2",392,1,1.5,"Setting",0.08,4,0.01,2,"*","*","*","*","*","(3E21=1) && (0910=1)",{"$nulls":4},"M4"]
["3E",23,{"$nulls":26},"Spare"]
["3E",24,"I>1 Time Delay","Courier Number (time)",null,"4x01704",null,null,"G2",10000,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(3E21=1) && (3523=1) && (0910=1)"]
["3E",25,"I>1 TMS","Courier Number (decimal)",null,"4x01705",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","(3E21=1) && (6>=3523>=2) && (0910=1)"]
["3E",26,"I>1 Time Dial","Courier Number (decimal)",null,"4x01706",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","(3E21=1) && (12>=3523>=8) && (0910=1)"]
["3E",27,"I>1 k (RI)","Courier Number (decimal)",null,"4x01707",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","(3E21=1) && (3523=7) && (0910=1)"]
["3E",28]
["3E",29,"I>2 Status","Indexed String",null,"4x01708",null,"G106","G106",1,1,"Enable","Setting",0,1,1,2,"*","*","*","*","*","(3532<>0) && (0910=1)"]
["3E","2A","I>2 Current Set","Courier Number (current)",null,"4x01709",null,null,"G2",392,1,1.5,"Setting",0.08,4,0.01,2,"*","*","*","*","*","(3E29=1) && (0910=1)",{"$nulls":4},"M4"]
["3E","2B",{"$nulls":26},"Spare"]
["3E","2C","I>2 Time Delay","Courier Number (time)",null,"4x01710",null,null,"G2",10000,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(3E29=1) && (3532=1) && (0910=1)"]
["3E","2D","I>2 TMS","Courier Number (decimal)",null,"4x01711",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","(3E29=1) && (6>=3532>=2) && (0910=1)"]
["3E","2E","I>2 Time Dial","Courier Number (decimal)",null,"4x01712",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","(3E29=1) && (12>=3532>=8) && (0910=1)"]
["3E","2F","I>2 k (RI)","Courier Number (decimal)",null,"4x01713",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","(3E29=1) && (3532=7) && (0910=1)"]
["3E",30]
["3E",31,"I>3 Status","Indexed String",null,"4x01714",null,"G106","G106",1,1,"Block","Setting",0,1,1,2,"*","*","*","*","*","(3540=1) && (0910=1)"]
["3E",32,"I>3 Current Set","Courier Number (current)",null,"4x01715",null,null,"G2",3192,1,25,"Setting",0.08,32,0.01,2,"*","*","*","*","*","(3E31=1) && (0910=1)",{"$nulls":4},"M4"]
["3E",33,"I>3 Time Delay","Courier Number (time)",null,"4x01716",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(3E31=1) && (0910=1)"]
["3E",34,{"$nulls":26},"Spare"]
["3E",35,"I>4 Status","Indexed String",null,"4x01717",null,"G106","G106",1,1,"Block","Setting",0,1,1,2,"*","*","*","*","*","(3547=1) && (0910=1)",{"$nulls":5},"(3516=1) && (0910=1)"]
["3E",36,"I>4 Current Set","Courier Number (current)",null,"4x01718",null,null,"G2",3192,1,25,"Setting",0.08,32,0.01,2,"*","*","*","*","*","(3E35=1) && (0910=1)",{"$nulls":4},"M4","(3E11=1) && (0910=1)"]
["3E",37,"I>4 Time Delay","Courier Number (time)",null,"4x01719",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(3E35=1) && (0910=1)"]
["3E",38,{"$nulls":26},"Spare"]
["3E",39,"STAGE 1 E/F 1","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","(0913=1)"]
["3E","3A","IN1>1 Status","Indexed String",null,"4x01720",null,"G106","G106",1,1,"Enable","Setting",0,1,1,2,"*","*","*","*","*","(3825<>0) && (0913=1)"]
["3E","3B","IN1>1 Current ","Courier Number (current)",null,"4x01721",null,null,"G2",392,1,0.2,"Setting",0.08,4,0.01,2,"*","*","*","*","*","(3E3A=1) && (0913=1)",{"$nulls":4},"M5","Measured E/F Current"]
["3E","3C","IN1>1 IDG Is","Courier Number (decimal)",null,"4x01722",null,null,"G2",30,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","(3E3A=1) && (3825=12) && (0913=1)",{"$nulls":5},"I>1 IDG Current Multiplier Setting","*"]
["3E","3D",{"$nulls":26},"Spare (IN1>1 Current Set2)","*"]
["3E","3E","IN1>1 Time Delay","Courier Number (time)",null,"4x01723",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","(3E3A=1) && (3825=1) && (0913=1)"]
["3E","3F","IN1>1 TMS","Courier Number (decimal)",null,"4x01724",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","(3E3A=1) && (5>=3825>=2) && (0913=1)"]
["3E",40,"IN1>1 Time Dial","Courier Number (decimal)",null,"4x01725",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","(3E3A=1) && (11>=3825>=7) && (0913=1)"]
["3E",41,"IN1>1 k (RI)","Courier Number (decimal)",null,"4x01726",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","(3E3A=1) && (3825=6) && (0913=1)",{"$nulls":6},"*"]
["3E",42,{"$nulls":27},"*"]
["3E",43,"STAGE 1 E/F 2","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","(0914=1)"]
["3E",44,"IN2>1 Status","Indexed String",null,"4x01727",null,"G106","G106",1,1,"Enable","Setting",0,1,1,2,"*","*","*","*","*","(3925<>0) && (0914=1)"]
["3E",45,"IN2>1 Current ","Courier Number (current)",null,"4x01728",null,null,"G2",392,1,0.2,"Setting",0.08,4,0.01,2,"*","*","*","*","*","(3E44=1) && (0914=1)",{"$nulls":4},"M4","Derived E/F Current"]
["3E",46,"IN2>1 IDG Is","Courier Number (decimal)",null,"4x01729",null,null,"G2",30,1,1.5,"Setting",1,4,0.1,2,"*","*","*","*","*","(3E44=1) && (3925=12) && (0914=1)",{"$nulls":5},"IN2>1 IDG Current Multiplier Setting","*"]
["3E",47,{"$nulls":26},"Spare (IN1>1 Current Set2)","*"]
["3E",48,"IN2>1 Time Delay","Courier Number (time)",null,"4x01730",null,null,"G2",20000,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","(3E44=1) && (3925=1) && (0914=1)"]
["3E",49,"IN2>1 TMS","Courier Number (decimal)",null,"4x01731",null,null,"G2",235,1,1,"Setting",0.025,1.2,0.005,2,"*","*","*","*","*","(3E44=1) && (5>=3925>=2) && (0914=1)"]
["3E","4A","IN2>1 Time Dial","Courier Number (decimal)",null,"4x01732",null,null,"G2",9999,1,1,"Setting",0.01,100,0.01,2,"*","*","*","*","*","(3E44=1) && (11>=3925>=7) && (0914=1)"]
["3E","4B","IN2>1 k (RI)","Courier Number (decimal)",null,"4x01733",null,null,"G2",198,1,1,"Setting",0.1,10,0.05,2,"*","*","*","*","*","(3E44=1) && (3925=6) && (0914=1)"]
["3F",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","091A = 1","=",1]
[null,null,"SELECTIVE LOGIC"]
["3F",1,"OVERCURRENT","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","(0910=1) AND (3540=1)","=",1]
["3F",2,"I>3 Time Delay","Courier Number (time)",null,"4x01750",null,null,"G2",null,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(0910=1) AND (3540=1)"]
["3F",3,"I>4 Time Delay","Courier Number (time)",null,"4x01751",null,null,"G2",null,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(0910=1) AND (3547=1)"]
["3F",4,"EARTH FAULT 1","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","0913 =1","=",1]
["3F",5,"IN1>3 Time Delay","Courier Number (time)",null,"4x01752",null,null,"G2",null,1,2,"Setting",0,200,0.01,2,"*","*","*","*","*","(0913=1) AND (3846=1)"]
["3F",6,"IN1>4 Time Delay","Courier Number (time)",null,"4x01753",null,null,"G2",null,1,2,"Setting",0,200,0.01,2,"*","*","*","*","*","(0913=1) AND (384D=1)"]
["3F",7,"EARTH FAULT 2","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","0914 =1","=",1]
["3F",8,"IN2>3 Time Delay","Courier Number (time)",null,"4x01754",null,null,"G2",null,1,2,"Setting",0,200,0.01,2,"*","*","*","*","*","(0914=1) AND (3946=1)"]
["3F",9,"IN2>4 Time Delay","Courier Number (time)",null,"4x01755",null,null,"G2",null,1,2,"Setting",0,200,0.01,2,"*","*","*","*","*","(0914=1) AND (394D=1)"]
["3F","0A","SENSITIVE E/F","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","0915 =1","=",1]
["3F","0B","ISEF>3 Delay","Courier Number (time)",null,"4x01756",null,null,"G2",null,1,1,"Setting",0,200,0.01,2,"*","*","*","*","*","(0915=1) AND (3A49=1)"]
["3F","0C","ISEF>4 Delay","Courier Number (time)",null,"4x01757",null,null,"G2",null,1,0.5,"Setting",0,200,0.01,2,"*","*","*","*","*","(0915=1) AND (3A50=1)"]
[40,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","091B = 1",{"$nulls":6},"*"]
[null,null,"ADMIT PROTECTION"]
[40,1,"VN Threshold","Courier Number (voltage)",null,"4x01800",null,null,"G2",null,1,10,"Setting","1*V1","40*V1","1*V1",2,"*","*","*",null,"*",{"$nulls":5},"M1"]
[{"$nulls":11},40,null,"1*V3","40*V3","1*V3",{"$nulls":4},"*",{"$nulls":6},"M3"]
[40,2,"CT Input Type","Indexed String",null,"4x01801",null,"G120","G120",null,1,"SEF CT","Setting",0,1,1,2,"*","*","*","*","*"]
[40,3,"Correction Angle","Courier Number (angle)",null,"4x01802",null,null,"G2",null,1,0,"Setting",-30,30,1,2,"*","*","*","*","*"]
[40,4,"OVER ADMITTANCE","(Sub Heading)",null,"(xding)"]
[40,5,"YN> Status","Indexed String",null,"4x01803",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
[40,6,"YN> Set","Courier Number (inverse ohms)",null,"4x01804",null,null,"G2",null,1,0.005,"Setting","0.0001*I3/V1","0.01*I3/V1","0.0001*I3/V1",2,"*","*","*",null,"*","(4005=1) && (4002=0)",{"$nulls":4},"M6/M1"]
[{"$nulls":11},0.00125,null,"0.0001*I3/V3","0.01*I3/V3","0.0001*I3/V3",{"$nulls":4},"*",{"$nulls":6},"M6/M3"]
[40,7,"YN> Set","Courier Number (inverse ohms)",null,"4x01805",null,null,"G2",null,1,0.05,"Setting","0.001*I2/V1","0.1*I2/V1","0.001*I2/V1",2,"*","*","*","*","*","(4005=1) && (4002=1)",{"$nulls":4},"M5/M1"]
[{"$nulls":11},0.0125,null,"0.001*I2/V3","0.1*I2/V3","0.001*I2/V3",{"$nulls":11},"M5/M3"]
[40,8,"YN> Time Delay","Courier Number (time)",null,"4x01806",null,null,"G2",null,1,1,"Setting",0.05,100,0.01,2,"*","*","*","*","*","(4005=1)"]
[40,9,"YN> tRESET","Courier Number (time)",null,"4x01807",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(4005=1)",{"$nulls":6},"*"]
[40,"0A","OVER CONDUCTANCE","(Sub Heading)",null,"(xding)"]
[40,"0B","GN> Status","Indexed String",null,"4x01808",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
[40,"0C","GN> Direction","Indexed String",null,"4x01809",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","(400B=1)"]
[40,"0D","GN> Set","Courier Number (inverse ohms)",null,"4x01810",null,null,"G2",null,1,0.0008,"Setting","0.0001*I3/V1","0.005*I3/V1","0.0001*I3/V1",2,"*","*","*",null,"*","(400B=1) && (4002=0)",{"$nulls":4},"M6/M1"]
[{"$nulls":11},0.0002,null,"0.0001*I3/V3","0.01*I3/V3","0.0001*I3/V3",{"$nulls":4},"*",{"$nulls":6},"M6/M3"]
[40,"0E","GN> Set","Courier Number (inverse ohms)",null,"4x01811",null,null,"G2",null,1,0.002,"Setting","0.001*I2/V1","0.05*I2/V1","0.001*I2/V1",2,"*","*","*",null,"*","(400B=1) && (4002=1)",{"$nulls":4},"M5/M1"]
[{"$nulls":11},0.0005,null,"0.001*I2/V3","0.1*I2/V3","0.001*I2/V3",{"$nulls":4},"*",{"$nulls":6},"M5/M3"]
[40,"0F","GN> Time Delay","Courier Number (time)",null,"4x01812",null,null,"G2",null,1,1,"Setting",0.05,100,0.01,2,"*","*","*","*","*","(400B=1)"]
[40,10,"GN> tRESET","Courier Number (time)",null,"4x01813",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(400B=1)",{"$nulls":6},"*"]
[40,11,"OVER SUSCEPTANCE","(Sub Heading)",null,"(xding)"]
[40,12,"BN> Status","Indexed String",null,"4x01814",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
[40,13,"BN> Direction","Indexed String",null,"4x01815",null,"G44","G44",null,1,"Non-Directional","Setting",0,2,1,2,"*","*","*","*","*","(4012=1)"]
[40,14,"BN> Set","Courier Number (inverse ohms)",null,"4x01816",null,null,"G2",null,1,0.0008,"Setting","0.0001*I3/V1","0.005*I3/V1","0.0001*I3/V1",2,"*","*","*",null,"*","(4012=1) && (4002=0)",{"$nulls":4},"M6/M1"]
[{"$nulls":11},0.0002,null,"0.0001*I3/V3","0.01*I3/V3","0.0001*I3/V3",{"$nulls":4},"*",{"$nulls":6},"M6/M3"]
[40,15,"BN> Set","Courier Number (inverse ohms)",null,"4x01817",null,null,"G2",null,1,0.002,"Setting","0.001*I2/V1","0.05*I2/V1","0.001*I2/V1",2,"*","*","*","*","*","(4012=1) && (4002=1)",{"$nulls":4},"M5/M1"]
[{"$nulls":11},0.0005,null,"0.001*I2/V3","0.1*I2/V3","0.001*I2/V3",{"$nulls":4},"*",{"$nulls":6},"M5/M3"]
[40,16,"BN> Time Delay","Courier Number (time)",null,"4x01818",null,null,"G2",null,1,1,"Setting",0.05,100,0.01,2,"*","*","*","*","*","(4012=1)"]
[40,17,"BN> tRESET","Courier Number (time)",null,"4x01819",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(4012=1)",{"$nulls":6},"*"]
[41,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","091C = 1","=",1,{"$nulls":4},"*"]
[null,null,"POWER PROTECTION"]
[41,1,"OVER POWER","(Sub Heading)",{"$nulls":13},"*","*","*","*","*"]
[41,2,"Power>1 Status","Indexed String",null,"4x01820",null,"G37","G1",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[41,3,"Power>1 Direction","Indexed String",null,"4x01821",null,"G257","G1",null,1,"Forward","Setting",0,1,1,2,"*","*","*","*","*","(4102=1)",{"$nulls":6},"*"]
[41,4,"Power>1 Mode","Indexed String",null,"4x01822",null,"G258","G1",null,1,"Active","Setting",0,1,1,2,"*","*","*","*","*","(4102=1)",{"$nulls":6},"*"]
[41,5,"Power>1 TimeDelay","Courier Number (time)",null,"4x01823",null,null,"G2",null,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(4102=1)",{"$nulls":6},"*"]
[41,6,"Power>1 tRESET","Courier Number (time)",null,"4x01824",null,null,"G2",null,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(4102=1)",{"$nulls":6},"*"]
[41,7,"Power>1 1Ph Watt","Courier Number (power Watts)",null,"4x01825",null,null,"G2",null,1,40,"Setting",1,325,1,2,"*","*","*","*","*","(4102=1) && (4104=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,8,"Power>1 1Ph VAR","Courier Number (power VARs)",null,"4x01826",null,null,"G2",null,1,24,"Setting",1,325,1,2,"*","*","*","*","*","(4102=1) && (4104=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,9,"Power>1 3Ph Watt","Courier Number (power Watts)",null,"4x01827",null,null,"G2",null,1,120,"Setting",1,325,1,2,"*","*","*","*","*","(4102=1) && (4104=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,"0A","Power>1 3Ph VAR","Courier Number (power VARs)",null,"4x01828",null,null,"G2",null,1,72,"Setting",1,325,1,2,"*","*","*","*","*","(4102=1) && (4104=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,"0B","Power>2 Status","Indexed String",null,"4x01829",null,"G37","G1",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[41,"0C","Power>2 Direction","Indexed String",null,"4x01830",null,"G257","G1",null,1,"Forward","Setting",0,1,1,2,"*","*","*","*","*","(410B=1)",{"$nulls":6},"*"]
[41,"0D","Power>2 Mode","Indexed String",null,"4x01831",null,"G258","G1",null,1,"Active","Setting",0,1,1,2,"*","*","*","*","*","(410B=1)",{"$nulls":6},"*"]
[41,"0E","Power>2 TimeDelay","Courier Number (time)",null,"4x01832",null,null,"G2",null,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(410B=1)",{"$nulls":6},"*"]
[41,"0F","Power>2 tRESET","Courier Number (time)",null,"4x01833",null,null,"G2",null,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(410B=1)",{"$nulls":6},"*"]
[41,10,"Power>2 1Ph Watt","Courier Number (power Watts)",null,"4x01834",null,null,"G2",null,1,40,"Setting",1,325,1,2,"*","*","*","*","*","(410B=1) && (410D=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,11,"Power>2 1Ph VAR","Courier Number (power VARs)",null,"4x01835",null,null,"G2",null,1,24,"Setting",1,325,1,2,"*","*","*","*","*","(410B=1) && (410D=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,12,"Power>2 3Ph Watt","Courier Number (power Watts)",null,"4x01836",null,null,"G2",null,1,120,"Setting",1,325,1,2,"*","*","*","*","*","(410B=1) && (410D=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,13,"Power>2 3Ph VAR","Courier Number (power VARs)",null,"4x01837",null,null,"G2",null,1,72,"Setting",1,325,1,2,"*","*","*","*","*","(410B=1) && (410D=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,14,"UNDER POWER","(Sub Heading)",{"$nulls":13},"*","*","*","*","*"]
[41,15,"Power<1 Status","Indexed String",null,"4x01838",null,"G37","G1",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[41,16,"Power<1 Direction","Indexed String",null,"4x01839",null,"G257","G1",null,1,"Forward","Setting",0,1,1,2,"*","*","*","*","*","(4115=1)",{"$nulls":6},"*"]
[41,17,"Power<1 Mode","Indexed String",null,"4x01840",null,"G258","G1",null,1,"Active","Setting",0,1,1,2,"*","*","*","*","*","(4115=1)",{"$nulls":6},"*"]
[41,18,"Power<1 TimeDelay","Courier Number (time)",null,"4x01841",null,null,"G2",null,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(4115=1)",{"$nulls":6},"*"]
[41,19,"Power<1 tRESET","Courier Number (time)",null,"4x01842",null,null,"G2",null,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(4115=1)",{"$nulls":6},"*"]
[41,"1A","Power<1 1Ph Watt","Courier Number (power Watts)",null,"4x01843",null,null,"G2",null,1,10,"Setting",1,325,1,2,"*","*","*","*","*","(4115=1) && (4117=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,"1B","Power<1 1Ph VAR","Courier Number (power VARs)",null,"4x01844",null,null,"G2",null,1,6,"Setting",1,325,1,2,"*","*","*","*","*","(4115=1) && (4117=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,"1C","Power<1 3Ph Watt","Courier Number (power Watts)",null,"4x01845",null,null,"G2",null,1,30,"Setting",1,325,1,2,"*","*","*","*","*","(4115=1) && (4117=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,"1D","Power<1 3Ph VAR","Courier Number (power VARs)",null,"4x01846",null,null,"G2",null,1,18,"Setting",1,325,1,2,"*","*","*","*","*","(4115=1) && (4117=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,"1E","Power<2 Status","Indexed String",null,"4x01847",null,"G37","G1",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[41,"1F","Power<2 Direction","Indexed String",null,"4x01848",null,"G257","G1",null,1,"Forward","Setting",0,1,1,2,"*","*","*","*","*","(411E=1)",{"$nulls":6},"*"]
[41,20,"Power<2 Mode","Indexed String",null,"4x01849",null,"G258","G1",null,1,"Active","Setting",0,1,1,2,"*","*","*","*","*","(411E=1)",{"$nulls":6},"*"]
[41,21,"Power<2 TimeDelay","Courier Number (time)",null,"4x01850",null,null,"G2",null,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","(411E=1)",{"$nulls":6},"*"]
[41,22,"Power<2 tRESET","Courier Number (time)",null,"4x01851",null,null,"G2",null,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","(411E=1)",{"$nulls":6},"*"]
[41,23,"Power<2 1Ph Watt","Courier Number (power Watts)",null,"4x01852",null,null,"G2",null,1,10,"Setting",1,325,1,2,"*","*","*","*","*","(411E=1) && (4120=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,24,"Power<2 1Ph VAR","Courier Number (power VARs)",null,"4x01853",null,null,"G2",null,1,6,"Setting",1,325,1,2,"*","*","*","*","*","(411E=1) && (4120=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,25,"Power<2 3Ph Watt","Courier Number (power Watts)",null,"4x01854",null,null,"G2",null,1,30,"Setting",1,325,1,2,"*","*","*","*","*","(411E=1) && (4120=0)",{"$nulls":4},"M1*M4",null,"*"]
[41,26,"Power<2 3Ph VAR","Courier Number (power VARs)",null,"4x01855",null,null,"G2",null,1,18,"Setting",1,325,1,2,"*","*","*","*","*","(411E=1) && (4120=1)",{"$nulls":4},"M1*M4",null,"*"]
[41,27,"Power Blocking","Binary Flag (2 bits) ",null,"4x01856",null,"G259","G1",null,1,15,"Setting",0,11,1,2,"*","*","*","*","*",{"$nulls":6},"Poledead Block","*"]
[41,28,"SENSITIVE POWER","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[41,29,"Aph Sens Power","Indexed String",null,"4x01857",null,"G37","G1",1,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","091C = 1","=",1,{"$nulls":4},"*"]
[41,"2A","Comp Angle","Courier Number (Angle)",null,"4x01858",null,null,"G2",50,1,0,"Setting",-5,5,0.1,2,"*","*","*","*","*","4129 = 1","=",1,{"$nulls":4},"*"]
[41,"2B","Sens P1 Function","Indexed String",null,"4x01859",null,"G260","G1",3,1,"Reverse","Setting",0,3,1,2,"*","*","*","*","*","4129 = 1","=",1,{"$nulls":4},"*"]
[41,"2C","Sens -P>1 Setting","Courier Number (Power)",null,"4x01860",null,null,"G2",997,1,"0.5*V1*I3","Setting","0.3*V1*I3","100*V1*I3","0.1*V1*I3",2,"*","*","*","*","*","412B = 1","=",1,null,null,"M1*M6",null,"*"]
[41,"2D","Sens P<1 Setting","Courier Number (Power)",null,"4x01861",null,null,"G2",997,1,"0.5*V1*I3","Setting","0.3*V1*I3","100*V1*I3","0.1*V1*I3",2,"*","*","*","*","*","412B = 2","=",2,null,null,"M1*M6",null,"*"]
[41,"2E","Sens P>1 Setting","Courier Number (Power)",null,"4x01862",null,null,"G2",997,1,"50*V1*I3","Setting","0.3*V1*I3","100*V1*I3","0.1*V1*I3",2,"*","*","*","*","*","412B = 3","=",3,null,null,"M1*M6",null,"*"]
[41,"2F","Sens P1 Delay","Courier Number (Time)",null,"4x01863",null,null,"G2",10000,1,5,"Setting",0,100,0.01,2,"*","*","*","*","*","412B <> 0","<>",0,{"$nulls":4},"*"]
[41,30,"Sens P1 tRESET","Courier Number (Time)",null,"4x01864",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","412B <> 0","<>",0,{"$nulls":4},"*"]
[41,31,"P1 PoleDead Inh","Indexed String",null,"4x01865",null,"G37","G1",1,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*","412B <> 0","<>",0,{"$nulls":4},"*"]
[41,32,"Sens P2 Function","Indexed String",null,"4x01866",null,"G260","G1",3,1,"Low Forward","Setting",0,3,1,2,"*","*","*","*","*","4129 = 1",{"$nulls":6},"*"]
[41,33,"Sens -P>2 Setting","Courier Number (Power)",null,"4x01867",null,null,"G2",997,1,"0.5*V1*I3","Setting","0.3*V1*I3","100*V1*I3","0.1*V1*I3",2,"*","*","*","*","*","4132 = 1",{"$nulls":4},"M1*M6",null,"*"]
[41,34,"Sens P<2 Setting","Courier Number (Power)",null,"4x01868",null,null,"G2",997,1,"0.5*V1*I3","Setting","0.3*V1*I3","100*V1*I3","0.1*V1*I3",2,"*","*","*","*","*","4132 = 2",{"$nulls":4},"M1*M6",null,"*"]
[41,35,"Sens P>2 Setting","Courier Number (Power)",null,"4x01869",null,null,"G2",997,1,"50*V1*I3","Setting","0.3*V1*I3","100*V1*I3","0.1*V1*I3",2,"*","*","*","*","*","4132 = 3",{"$nulls":4},"M1*M6",null,"*"]
[41,36,"Sens P2 Delay","Courier Number (Time)",null,"4x01870",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4132 <> 0",{"$nulls":6},"*"]
[41,37,"Sens P2 tRESET","Courier Number (Time)",null,"4x01871",null,null,"G2",10000,1,0,"Setting",0,100,0.01,2,"*","*","*","*","*","4132 <> 0",{"$nulls":6},"*"]
[41,38,"P2 PoleDead Inh","Indexed String",null,"4x01872",null,"G37","G1",1,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*","4132 <> 0",{"$nulls":6},"*"]
[42,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","091D","=",1,{"$nulls":4},"*"]
[null,null,"VOLT PROTECTION"]
[42,1,"UNDER VOLTAGE","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[42,2,"V< Measur't Mode","Indexed String",null,"4x01950",null,"G47","G47",null,1,"Phase-Phase","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,3,"V< Operate Mode","Indexed String",null,"4x01951",null,"G48","G48",null,1,"Any Phase","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,4,"V<1 Function","Indexed String",null,"4x01952",null,"G23","G23",null,1,"DT","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,5,"V<1 Voltage Set","Courier Number (voltage)",null,"4x01953",null,null,"G2",60,1,80,"Setting","10*V1","120*V1","1*V1",2,"*","*","*","*","*","4204 <> 0",{"$nulls":4},"M1","Range covers Ph-N & Ph-Ph","*"]
[42,6,"V<1 Time Delay","Courier Number (time)",null,"4x01954",null,null,"G2",10000,1,10,"Setting",0,100,0.01,2,"*","*","*","*","*","4204 = 1",{"$nulls":6},"*"]
[42,7,"V<1 TMS","Courier Number (decimal)",null,"4x01955",null,null,"G2",199,1,1,"Setting",0.5,100,0.5,2,"*","*","*","*","*","4204 = 2",{"$nulls":6},"*"]
[42,8,"V<1 Poledead Inh","Indexed String",null,"4x01956",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*","4204 <> 0",{"$nulls":6},"*"]
[42,9,"V<2 Status","Indexed String",null,"4x01957",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,"0A","V<2 Voltage Set","Courier Number (voltage)",null,"4x01958",null,null,"G2",60,1,60,"Setting","10*V1","120*V1","1*V1",2,"*","*","*","*","*","4209 = 1",{"$nulls":4},"M1","Phase-Neutral","*"]
[42,"0B","V<2 Time Delay","Courier Number (time)",null,"4x01959",null,null,"G2",10000,1,5,"Setting",0,100,0.01,2,"*","*","*","*","*","4209 = 1",{"$nulls":6},"*"]
[42,"0C","V<2 Poledead Inh","Indexed String",null,"4x01960",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*","4209 = 1",{"$nulls":6},"*"]
[42,"0D","OVERVOLTAGE","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[42,"0E","V> Measur't Mode","Indexed String",null,"4x01961",null,"G47","G47",null,1,"Phase-Phase","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,"0F","V> Operate Mode","Indexed String",null,"4x01962",null,"G48","G48",null,1,"Any Phase","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,10,"V>1 Function","Indexed String",null,"4x01963",null,"G23","G23",null,1,"DT","Setting",0,2,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,11,"V>1 Voltage Set","Courier Number (voltage)",null,"4x01964",null,null,"G2",50,1,130,"Setting","60*V1","185*V1","1*V1",2,"*","*","*","*","*","4210 <> 0",{"$nulls":4},"M1",null,"*"]
[42,12,"V>1 Time Delay","Courier Number (time)",null,"4x01965",null,null,"G2",10000,1,10,"Setting",0,100,0.01,2,"*","*","*","*","*","4210 = 1",{"$nulls":6},"*"]
[42,13,"V>1 TMS","Courier Number (decimal)",null,"4x01966",null,null,"G2",199,1,1,"Setting",0.5,100,0.5,2,"*","*","*","*","*","4210 = 2",{"$nulls":6},"*"]
[42,14,"V>2 Status","Indexed String",null,"4x01967",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[42,15,"V>2 Voltage Set","Courier Number (voltage)",null,"4x01968",null,null,"G2",50,1,150,"Setting","60*V1","185*V1","1*V1",2,"*","*","*","*","*","4214 = 1",{"$nulls":4},"M1",null,"*"]
[42,16,"V>2 Time Delay","Courier Number (time)",null,"4x01969",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4214 = 1",{"$nulls":6},"*"]
[43,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","091E = 1",{"$nulls":6},"*"]
[null,null,"FREQ PROTECTION"]
[43,1,"UNDER FREQUENCY","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[43,2,"F<1 Status","Indexed String",null,"4x02000",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[43,3,"F<1 Setting","Courier Number (Frequency)",null,"4x02001",null,null,"G2",2000,1,49.5,"Setting",45,65,0.01,2,"*","*","*","*","*","4302 = 1",{"$nulls":6},"*"]
[43,4,"F<1 Time Delay","Courier Number (Time)",null,"4x02002",null,null,"G2",10000,1,4,"Setting",0,100,0.01,2,"*","*","*","*","*","4302 = 1",{"$nulls":6},"*"]
[43,5,"F<2 Status","Indexed String",null,"4x02003",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[43,6,"F<2 Setting","Courier Number (Frequency)",null,"4x02004",null,null,"G2",2000,1,49,"Setting",45,65,0.01,2,"*","*","*","*","*","4305 = 1",{"$nulls":6},"*"]
[43,7,"F<2 Time Delay","Courier Number (Time)",null,"4x02005",null,null,"G2",10000,1,3,"Setting",0,100,0.01,2,"*","*","*","*","*","4305 = 1",{"$nulls":6},"*"]
[43,8,"F<3 Status","Indexed String",null,"4x02006",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[43,9,"F<3 Setting","Courier Number (Frequency)",null,"4x02007",null,null,"G2",2000,1,48.5,"Setting",45,65,0.01,2,"*","*","*","*","*","4308 = 1",{"$nulls":6},"*"]
[43,"0A","F<3 Time Delay","Courier Number (Time)",null,"4x02008",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4308 = 1",{"$nulls":6},"*"]
[43,"0B","F<4 Status","Indexed String",null,"4x02009",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[43,"0C","F<4 Setting","Courier Number (Frequency)",null,"4x02010",null,null,"G2",2000,1,48,"Setting",45,65,0.01,2,"*","*","*","*","*","430B = 1",{"$nulls":6},"*"]
[43,"0D","F<4 Time Delay","Courier Number (Time)",null,"4x02011",null,null,"G2",10000,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","430B = 1",{"$nulls":6},"*"]
[43,"0E","F< Function Link","Binary Flag (4 bits)",null,"4x02012",null,"G65","G65"," ",1,0,"Setting",15,4,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[43,"0F","OVER FREQUENCY","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[43,10,"F>1 Status","Indexed String",null,"4x02013",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[43,11,"F>1 Setting","Courier Number (Frequency)",null,"4x02014",null,null,"G2",2000,1,50.5,"Setting",45,65,0.01,2,"*","*","*","*","*","4310 = 1",{"$nulls":6},"*"]
[43,12,"F>1 Time Delay","Courier Number (Time)",null,"4x02015",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4310 = 1",{"$nulls":6},"*"]
[43,13,"F>2 Status","Indexed String",null,"4x02016",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[43,14,"F>2 Setting","Courier Number (Frequency)",null,"4x02017",null,null,"G2",2000,1,51,"Setting",45,65,0.01,2,"*","*","*","*","*","4313 = 1",{"$nulls":6},"*"]
[43,15,"F>2 Time Delay","Courier Number (Time)",null,"4x02018",null,null,"G2",10000,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","4313 = 1",{"$nulls":6},"*"]
[44,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","091F","=",1,{"$nulls":4},"*"]
[null,null,"DF/DT PROTECTION"]
[44,1,"df/dt Avg.Cycles","Unsigned Integer (16 bits)",null,"4x02053",null,null,"G1",null,1,6,"Setting",6,12,6,2,"*","*","*","*","*",{"$nulls":7},"*"]
[]
[]
[]
[]
[]
[44,4,"df/dt>1 Status","Indexed String",null,"4x02056",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[]
[44,5,"df/dt>1 Setting","Courier Number (Hz/sec)",null,"4x02057",null,null,"G2",99,1,2,"Setting",0.1,10,0.1,2,"*","*","*","*","*",4404,"=",1,{"$nulls":4},"*"]
[]
[44,6,"df/dt>1 Dir'n","Indexed String",null,"4x02058",null,"G157","G157",2,1,"Negative","Setting",0,2,1,2,"*","*","*","*","*",4404,"=",1,{"$nulls":4},"*"]
[]
[44,7,"df/dt>1 Time","Courier Number (Time)",null,"4x02059",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*",4404,"=",1,{"$nulls":4},"*"]
{"$rows_empty":7}
[44,"0B","df/dt>2 Status","Indexed String",null,"4x02063",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[]
[44,"0C","df/dt>2 Setting","Courier Number (Hz/sec)",null,"4x02064",null,null,"G2",99,1,2,"Setting",0.1,10,0.1,2,"*","*","*","*","*","440B","=",1,{"$nulls":4},"*"]
[]
[44,"0D","df/dt>2 Dir'n","Indexed String",null,"4x02065",null,"G157","G157",2,1,"Negative","Setting",0,2,1,2,"*","*","*","*","*","440B","=",1,{"$nulls":4},"*"]
[]
[44,"0E","df/dt>2 Time","Courier Number (Time)",null,"4x02066",null,null,"G2",10000,1,1,"Setting",0,100,0.01,2,"*","*","*","*","*","440B","=",1,{"$nulls":4},"*"]
{"$rows_empty":7}
[44,12,"df/dt>3 Status","Indexed String",null,"4x02070",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[]
[44,13,"df/dt>3 Setting","Courier Number (Hz/sec)",null,"4x02071",null,null,"G2",99,1,2,"Setting",0.1,10,0.1,2,"*","*","*","*","*",4412,"=",1,{"$nulls":4},"*"]
[]
[44,14,"df/dt>3 Dir'n","Indexed String",null,"4x02072",null,"G157","G157",2,1,"Negative","Setting",0,2,1,2,"*","*","*","*","*",4412,"=",1,{"$nulls":4},"*"]
[]
[44,15,"df/dt>3 Time","Courier Number (Time)",null,"4x02073",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*",4412,"=",1,{"$nulls":4},"*"]
{"$rows_empty":7}
[44,19,"df/dt>4 Status","Indexed String",null,"4x02077",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[]
[44,"1A","df/dt>4 Setting","Courier Number (Hz/sec)",null,"4x02078",null,null,"G2",99,1,2,"Setting",0.1,10,0.1,2,"*","*","*","*","*",4419,"=",1,{"$nulls":4},"*"]
[]
[44,"1B","df/dt>4 Dir'n","Indexed String",null,"4x02079",null,"G157","G157",2,1,"Negative","Setting",0,2,1,2,"*","*","*","*","*",4419,"=",1,{"$nulls":4},"*"]
[]
[44,"1C","df/dt>4 Time","Courier Number (Time)",null,"4x02080",null,null,"G2",10000,1,3,"Setting",0,100,0.01,2,"*","*","*","*","*",4419,"=",1,{"$nulls":4},"*"]
[]
[]
[]
[null,null,"DF/DT PROTECTION"]
[45,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*",{"$nulls":7},"*"]
[null,null,"CB FAIL & I<"]
[45,1,"BREAKER FAIL","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","0920 = 1","=",1,{"$nulls":4},"*"]
[45,2,"CB Fail 1 Status","Indexed String",null,"4x02100",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,"*","*","*","*","*","0920 = 1","=",1,{"$nulls":4},"*"]
[45,3,"CB Fail 1 Timer","Courier Number (time)",null,"4x02101",null,null,"G2",1000,1,0.2,"Setting",0,10,0.01,2,"*","*","*","*","*","4502 = 1","=",1,"*",null,null,null,"*"]
[45,4,"CB Fail 2 Status","Indexed String",null,"4x02102",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","0920 = 1","=",1,{"$nulls":4},"*"]
[45,5,"CB Fail 2 Timer","Courier Number (time)",null,"4x02103",null,null,"G2",1000,1,0.4,"Setting",0,10,0.01,2,"*","*","*","*","*","4504 = 1","=",1,"*",null,null,null,"*"]
[45,6,"Volt Prot Reset","Indexed String",null,"4x02104",null,"G68","G68",2,1,"CB Open & I<","Setting",0,2,1,2,"*","*","*","*","*","0920 = 1","=",1,{"$nulls":4},"*"]
[45,7,"Ext Prot Reset","Indexed String",null,"4x02105",null,"G68","G68",2,1,"CB Open & I<","Setting",0,2,1,2,"*","*","*","*","*","0920 = 1",{"$nulls":6},"*"]
[45,8,"UNDER CURRENT","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[45,9,"I< Current Set","Courier Number (current)",null,"4x02106",null,null,"G2",318,1,0.1,"Setting","0.02*I1","3.2*I1","0.01*I1",2,"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[45,"0A","IN< Current Set","Courier Number (current)",null,"4x02107",null,null,"G2",318,1,0.1,"Setting","0.02*I2","3.2*I2","0.01*I2",2,"*","*","*","*","*",{"$nulls":5},"M5",null,"*"]
[45,"0B","ISEF< Current","Courier Number (current)",null,"4x02108",null,null,"G2",1598,1,0.02,"Setting","0.001*I3","0.8*I3","0.0005*I3",2,"*","*","*","*","*",{"$nulls":5},"M6",null,"*"]
[45,"0C","BLOCKED O/C","(Sub Heading)",{"$nulls":13},"*","*","*","*","*","0920 = 1",{"$nulls":5},"Blocked Overcurrent Schemes"]
[45,"0D","Remove I> Start","Indexed String",null,"4x02109",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","0920 = 1"]
[45,"0E","Remove IN> Start","Indexed String",null,"4x02110",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","0920 = 1","=",1]
[46,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0921 = 1","=",1,{"$nulls":4},"*"]
[null,null,"SUPERVISION"]
[46,1,"VT SUPERVISION","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[46,2,"VTS Status","Indexed String",null,"4x02150",null,"G7","G7",null,1,"Blocking","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[46,3,"VTS Reset Mode","Indexed String",null,"4x02151",null,"G69","G69",null,1,"Manual","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[46,4,"VTS Time Delay","Courier Number (time)",null,"4x02152",null,null,"G2",90,1,5,"Setting",1,10,0.1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[46,5,"VTS I> Inhibit","Courier Number (current)",null,"4x02153",null,null,"G2",392,1,10,"Setting","0.08*I1","32*I1","0.01*I1",2,"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[46,6,"VTS I2> Inhibit","Courier Number (current)",null,"4x02154",null,null,"G2",392,1,0.05,"Setting","0.05*I1","0.5*I1","0.01*I1",2,"*","*","*","*","*",{"$nulls":5},"M4",null,"*"]
[46,7,"CT SUPERVISION","(Sub Heading)",{"$nulls":13},"*","*","*","*","*",{"$nulls":7},"*"]
[46,8,"CTS Status","Indexed String",null,"4x02155",null,"G37","G37",43,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*",{"$nulls":5},"M1",null,"*"]
[46,9,"CTS VN< Inhibit","Courier Number (voltage)",null,"4x02156",null,null,"G2",43,1,5,"Setting","0.5*V1","22*V1","0.5*V1",2,"*","*","*",null,"*","4608 = 1",{"$nulls":4},"M1",null,"*"]
[{"$nulls":11},20,null,"0.5*V3","22*V3","0.5*V3",{"$nulls":4},"*",{"$nulls":6},"M3"]
[46,"0A","CTS IN> Set","Courier Number (current)",null,"4x02157",null,null,"G2",392,1,0.1,"Setting","0.08*I1","4*I1","0.01*I1",2,"*","*","*","*","*","4608 = 1",{"$nulls":4},"M4",null,"*"]
[46,"0B","CTS Time Delay","Courier Number (time)",null,"4x02158",null,null,"G2",10,1,5,"Setting",0,10,1,2,"*","*","*","*","*","4608 = 1",{"$nulls":6},"*"]
[47,0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0922 = 1",{"$nulls":6},"*"]
[null,null,"FAULT LOCATOR"]
[47,1,"Line Length","Courier Number (metres)",null,"4x02200","4x02201",null,"G35",119999,2,16000,"Setting",10,1000000,1,2,"*","*","*","*","*","0D09 = 0","=",0,null,null,null,"Length in km","*"]
[47,2,"Line Length","Courier Number (miles)",null,"4x02202","4x02203",null,"G35",99999,2,10,"Setting",0.005,621,0.005,2,"*","*","*","*","*","0D09 = 1","=",1,null,null,null,"Setting stored in km, displayed using miles","*"]
[47,3,"Line Impedance","Courier Number (impedance)",null,"4x02204",null,null,"G2",24990,1,6,"Setting","0.1*V1/I1","250*V1/I1","0.01*V1/I1",2,"*","*","*","*","*",{"$nulls":5},"M1/M4",null,"*"]
[47,4,"Line Angle","Courier Number (angle)",null,"4x02205",null,null,"G2",65,1,70,"Setting",20,85,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[47,5,"KZN Residual","Courier Number (decimal)",null,"4x02206",null,null,"G2",24990,1,1,"Setting",0,7,0.01,2,"*","*","*","*","*",{"$nulls":6},"Multiplier","*"]
[47,6,"KZN Res Angle","Courier Number (angle)",null,"4x02207",null,null,"G2",125,1,0,"Setting",-90,90,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
[48,0,"GROUP 1",{"$nulls":15},"*","*","*","*","0923 = 1",{"$nulls":6},"*"]
[null,null,"SYSTEM CHECKS"]
[48,14,"VOLTAGE MONITORS","(Sub Heading)",{"$nulls":14},"*","*","*","*"]
[48,15,"Live Voltage","Courier Number (voltage)",null,"4x02250","4x02250",null,"G2",null,1,32,"Setting","1*V1","132*V1","0.5*V1",2,null,"*","*","*","*"]
[48,16,"Dead Voltage","Courier Number (voltage)",null,"4x02251","4x02251",null,"G2",null,1,13,"Setting","1*V1","132*V1","0.5*V1",2,null,"*","*","*","*"]
[48,17,"CHECK SYNC.","(Sub Heading)",{"$nulls":15},"*",null,"*"]
[48,18,"CS1 Status","Indexed String",null,"4x02252","4x02252","G37","G1",null,1,"Enabled","Setting",0,1,1,2,null,null,"*",null,"*"]
[48,19,"CS1 Phase Angle","Courier Number (angle)",null,"4x02253","4x02253",null,"G2",null,1,20,"Setting",5,90,1,2,null,null,"*",null,"*","4818 = 1"]
[48,"1A","CS1 Slip Control","Indexed String",null,"4x02254","4x02254","G42","G1",null,1,"Frequency","Setting",0,3,1,2,null,null,"*",null,"*","4818 = 1"]
[48,"1B","CS1 Slip Freq","Courier Number (frequency)",null,"4x02255","4x02255",null,"G2",null,1,0.05,"Setting",0.01,1,0.01,2,null,null,"*",null,"*","4818=1 AND (481A=2 OR 481A=3)"]
[48,"1C","CS1 Slip Timer","Courier Number (time)",null,"4x02256","4x02256",null,"G2",null,1,1,"Setting",0,99,0.01,2,null,null,"*",null,"*","4818=1 AND (481A=1 OR 481A=3)"]
[48,"1D","CS2 Status","Indexed String",null,"4x02257","4x02257","G37","G1",null,1,"Disabled","Setting",0,1,1,2,null,null,"*",null,"*"]
[48,"1E","CS2 Phase Angle","Courier Number (angle)",null,"4x02258","4x02258",null,"G2",null,1,20,"Setting",5,90,1,2,null,null,"*",null,"*","481D = 1"]
[48,"1F","CS2 Slip Control","Indexed String",null,"4x02259","4x02259","G156","G1",null,1,"Frequency","Setting",0,4,1,2,null,null,"*",null,"*","481D = 1"]
[48,20,"CS2 Slip Freq","Courier Number (frequency)",null,"4x02260","4x02260",null,"G2",null,1,0.05,"Setting",0.01,1,0.01,2,null,null,"*",null,"*","481D=1 AND (481F=2 OR 481F=3)"]
[48,21,"CS2 Slip Timer","Courier Number (time)",null,"4x02261","4x02261",null,"G2",null,1,1,"Setting",0,99,0.01,2,null,null,"*",null,"*","481D=1 AND (481F=1 OR 481F=3)"]
[48,22,"CS Undervoltage","Courier Number (voltage)",null,"4x02262","4x02262",null,"G2",null,1,54,"Setting",10,132,0.5,2,null,null,"*",null,"*","4818=1 OR 481D=1"]
[48,23,"CS Overvoltage","Courier Number (voltage)",null,"4x02263","4x02263",null,"G2",null,1,130,"Setting",60,185,0.5,2,null,null,"*",null,"*","4818=1 OR 481D=1"]
[48,24,"CS Diff Voltage","Courier Number (voltage)",null,"4x02264","4x02264",null,"G2",null,1,6.5,"Setting",1,132,0.5,2,null,null,"*",null,"*","4818=1 OR 481D=1"]
[48,25,"CS Voltage Block","Indexed String",null,"4x02265","4x02265","G41","G1",null,1,"V<","Setting",0,7,1,2,null,null,"*",null,"*","4818=1 OR 481D=1"]
[48,26,"SYSTEM SPLIT","(Sub Heading)",{"$nulls":15},"*",null,"*"]
[48,27,"SS Status","Indexed String",null,"4x02266","4x02266","G37","G1",null,1,"Enabled","Setting",0,1,1,2,null,null,"*",null,"*"]
[48,28,"SS Phase Angle","Courier Number (angle)",null,"4x02267","4x02267",null,"G2",null,1,120,"Setting",90,175,1,2,null,null,"*",null,"*","4827 = 1"]
[48,29,"SS Under V Block","Indexed String",null,"4x02268","4x02268","G37","G1",null,1,"Enabled","Setting",0,1,1,2,null,null,"*",null,"*","4827 = 1"]
[48,"2A","SS Undervoltage","Courier Number (voltage)",null,"4x02269","4x02269",null,"G2",null,1,54,"Setting",10,132,0.5,2,null,null,"*",null,"*","4827 = 1"]
[48,"2B","SS Timer","Courier Number (time)",null,"4x02270","4x02270",null,"G2",null,1,1,"Setting",0,99,0.01,2,null,null,"*",null,"*","4827 = 1"]
[48,"2F","CB Close Time","Courier Number (time)",null,"4x02271",null,null,"G2",null,1,0.05,"Setting",0,0.5,0.001,2,null,null,"*",null,"*","481D=1 && 481F=4"]
[49,0,"GROUP 1",{"$nulls":15},"*","*","*","*","0924 = 1","=",1,{"$nulls":4},"*"]
[null,null,"AUTORECLOSE"]
[49,1,"AR Mode Select","Indexed String",null,"4x02300",null,"G70","G70",null,1,"Command Mode","Setting",0,3,1,2,null,"*","*","*","*",{"$nulls":7},"*"]
[49,2,"Number of Shots","Unsigned Integer (16 bits)",null,"4x02301",null,null,"G1",3,1,1,"Setting",1,4,1,2,null,"*","*","*","*",{"$nulls":7},"*"]
[49,3,"Number SEF Shots","Unsigned Integer (16 bits)",null,"4x02302",null,null,"G1",3,1,0,"Setting",0,4,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6)",{"$nulls":6},"*"]
[49,4,"Sequence Co-ord","Indexed String",null,"4x02303",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":7},"*"]
[49,5,"CS AR Immediate","Indexed String",null,"4x02304",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,null,null,"*",null,"*"]
[49,6,"Dead Time 1","Courier Number (time)",null,"4x02305",null,null,"G2",29999,1,10,"Setting",0.01,300,0.01,2,null,"*","*","*","*",{"$nulls":6},"Dead Time1","*"]
[49,7,"Dead Time 2","Courier Number (time)",null,"4x02306",null,null,"G2",29999,1,60,"Setting",0.01,300,0.01,2,null,"*","*","*","*",{"$nulls":6},"Dead Time2","*"]
[49,8,"Dead Time 3","Courier Number (time)",null,"4x02307","4x02308",null,"G35",999899,2,180,"Setting",0.01,9999,0.01,2,null,"*","*","*","*",{"$nulls":6},"Dead Time3","*"]
[49,9,"Dead Time 4","Courier Number (time)",null,"4x02309","4x02310",null,"G35",999899,2,180,"Setting",0.01,9999,0.01,2,null,"*","*","*","*",{"$nulls":6},"Dead Time4","*"]
[49,"0A","CB Healthy Time","Courier Number (time)",null,"4x02311","4x02312",null,"G35",999899,2,5,"Setting",0.01,9999,0.01,2,null,"*","*","*","*",{"$nulls":7},"*"]
[49,"0B","Start Dead t On","Indexed String",null,"4x02313",null,"G72","G72",null,1,"Protection Reset","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":7},"*"]
[49,"0C","tReclaim Extend","Indexed String",null,"4x02314",null,"G73","G73",null,1,"No Operation","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":7},"*"]
[49,"0D","Reclaim Time 1","Courier Number (time)",null,"4x02315",null,null,"G2",59900,1,180,"Setting",1,600,0.01,2,null,"*","*","*","*",{"$nulls":6},"Reclaim Time 1","*"]
[49,"0E","Reclaim Time 2","Courier Number (time)",null,"4x02316",null,null,"G2",59900,1,180,"Setting",1,600,0.01,2,null,"*","*","*","*",{"$nulls":6},"Reclaim Time 2","*"]
["NEW"]
[49,"0F","Reclaim Time 3","Courier Number (time)",null,"4x02317",null,null,"G2",59900,1,180,"Setting",1,600,0.01,2,null,"*","*","*","*",{"$nulls":6},"Reclaim Time 3","*"]
["NEW"]
[49,10,"Reclaim Time 4","Courier Number (time)",null,"4x02318",null,null,"G2",59900,1,180,"Setting",1,600,0.01,2,null,"*","*","*","*",{"$nulls":6},"Reclaim Time 4","*"]
["NEW"]
[49,11,"AR Inhibit Time","Courier Number (time)",null,"4x02319",null,null,"G2",59999,1,5,"Setting",0.01,600,0.01,2,null,"*","*","*","*",{"$nulls":6},"AR Inhibit Time Delay"]
[49,12,"AR Lockout","Indexed String",null,"4x02320",null,"G91","G91",null,1,"No Block","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Trips on Lockout","*"]
[49,13,"EFF Maint Lock","Indexed String",null,"4x02321",null,"G91","G91",null,1,"No Block","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Protection Trips when Maint/EFF Locked Out","*"]
[49,14,"AR Deselected","Indexed String",null,"4x02322",null,"G91","G91",null,1,"No Block","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Protection Trips if Auto Mode Deselected","*"]
[49,15,"Manual Close","Indexed String",null,"4x02323",null,"G91","G91",null,1,"No Block","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Protection Trips after Control Close","*"]
[49,16,"Trip 1 Main","Indexed String",null,"4x02324",null,"G82","G82",5,1,"No Block","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Main Prot for 1st Trip","*"]
[49,17,"Trip 2 Main","Indexed String",null,"4x02325",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Main Prot for 2nd Trip","*"]
[49,18,"Trip 3 Main","Indexed String",null,"4x02326",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Main Prot for 3rd Trip","*"]
[49,19,"Trip 4 Main","Indexed String",null,"4x02327",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Main Prot for 4th Trip","*"]
[49,"1A","Trip 5 Main","Indexed String",null,"4x02328",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Block Main Prot for 5th Trip","*"]
[49,"1B","Trip 1 SEF","Indexed String",null,"4x02329",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6)",{"$nulls":5},"Block SEF Prot for 1st Trip","*"]
[49,"1C","Trip 2 SEF","Indexed String",null,"4x02330",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6)",{"$nulls":5},"Block SEF Prot for 2nd Trip","*"]
[49,"1D","Trip 3 SEF","Indexed String",null,"4x02331",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6)",{"$nulls":5},"Block SEF Prot for 3rd Trip","*"]
[49,"1E","Trip 4 SEF","Indexed String",null,"4x02332",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6)",{"$nulls":5},"Block SEF Prot for 4th Trip","*"]
[49,"1F","Trip 5 SEF","Indexed String",null,"4x02333",null,"G82","G82",5,1,"Block Inst Prot","Setting",0,1,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6)",{"$nulls":5},"Block SEF Prot for 5th Trip","*"]
[49,20,"Man Close on Flt","Indexed String",null,"4x02334",null,"G92","G92",null,1,"Lockout","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Lockout for Control Close onto Fault","*"]
[49,21,"Trip AR Inactive","Indexed String",null,"4x02335",null,"G92","G92",null,1,"No Lockout","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Lockout if Protection Operates in Non Auto or Liveline modes","*"]
[49,22,"Reset Lockout by","Indexed String",null,"4x02336",null,"G74","G74",null,1,"User Interface","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Reset Lockout","*"]
[49,24,"AR on Man Close","Indexed String",null,"4x02337",null,"G75","G75",null,1,"Inhibited","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Auto-Reclose after Control Close","*"]
[49,25,"Sys Check Time","Courier Number (time)",null,"4x02338","4x02339",null,"G35",999899,2,5,"Setting",0.01,9999,0.01,2,null,"*","*","*","*",null,null,null,"*",null,null,"Check Sync Window","*"]
[49,26,"AR Skip Shot 1","Indexed String",null,"4x02340",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"Setting to enable AR Skip Shot DDB Signal","*"]
["NEW"]
[49,28,"AR INITIATION","(Sub Heading)",{"$nulls":14},"*","*","*","*"]
[49,29,"I>1 AR","Indexed String",null,"4x02341",null,"G101","G101",null,1,"Initiate Main AR","Setting",0,1,1,2,null,"*","*","*","*","0910=1 AND 3523>=1"]
[49,"2A","I>2 AR","Indexed String",null,"4x02342",null,"G101","G101",null,1,"Initiate Main AR","Setting",0,1,1,2,null,"*","*","*","*","0910=1 AND 3532>=1"]
[49,"2B","I>3 AR","Indexed String",null,"4x02343",null,"G102","G102",null,1,"Initiate Main AR","Setting",0,2,1,2,null,"*","*","*","*","0910=1 AND 3540=1"]
[49,"2C","I>4 AR","Indexed String",null,"4x02344",null,"G102","G102",null,1,"Initiate Main AR","Setting",0,2,1,2,null,"*","*","*","*","0910=1 AND 3547=1"]
[49,"2D","IN1>1 AR","Indexed String",null,"4x02345",null,"G101","G101",null,1,"Initiate Main AR","Setting",0,1,1,2,null,"*","*","*","*","0913=1 AND 3825>=1"]
[49,"2E","IN1>2 AR","Indexed String",null,"4x02346",null,"G101","G101",null,1,"Initiate Main AR","Setting",0,1,1,2,null,"*","*","*","*","0913=1 AND 3836>=1"]
[49,"2F","IN1>3 AR","Indexed String",null,"4x02347",null,"G102","G102",null,1,"Initiate Main AR","Setting",0,2,1,2,null,"*","*","*","*","0913=1 AND 3846=1"]
[49,30,"IN1>4 AR","Indexed String",null,"4x02348",null,"G102","G102",null,1,"Initiate Main AR","Setting",0,2,1,2,null,"*","*","*","*","0913=1 AND 384D=1"]
[49,31,"IN2>1 AR","Indexed String",null,"4x02349",null,"G101","G101",null,1,"No Action","Setting",0,1,1,2,null,"*","*","*","*","0914=1 AND 3925>=1"]
[49,32,"IN2>2 AR","Indexed String",null,"4x02350",null,"G101","G101",null,1,"No Action","Setting",0,1,1,2,null,"*","*","*","*","0914=1 AND 3936>=1"]
[49,33,"IN2>3 AR","Indexed String",null,"4x02351",null,"G102","G102",null,1,"No Action","Setting",0,2,1,2,null,"*","*","*","*","0914=1 AND 3946=1"]
[49,34,"IN2>4 AR","Indexed String",null,"4x02352",null,"G102","G102",null,1,"No Action","Setting",0,2,1,2,null,"*","*","*","*","0914=1 AND 394D=1"]
[49,35,"ISEF>1 AR","Indexed String",null,"4x02353",null,"G103","G103",null,1,"No Action","Setting",0,3,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6) AND 3A2A>=1"]
[49,36,"ISEF>2 AR","Indexed String",null,"4x02354",null,"G103","G103",null,1,"No Action","Setting",0,3,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6) AND 3A3A>=1"]
[49,37,"ISEF>3 AR","Indexed String",null,"4x02355",null,"G103","G103",null,1,"No Action","Setting",0,3,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6) AND 3A49=1"]
[49,38,"ISEF>4 AR","Indexed String",null,"4x02356",null,"G103","G103",null,1,"No Action","Setting",0,3,1,2,null,"*","*","*","*","0915=1 AND (3A01<=3 OR 3A01>=6) AND 3A50=1"]
[49,39,"YN> AR","Indexed String",null,"4x02357",null,"G101","G101",null,1,"No Action","Setting",0,1,1,2,null,"*","*","*","*","091B=1 AND 4005=1"]
[49,"3A","GN> AR","Indexed String",null,"4x02358",null,"G101","G101",null,1,"No Action","Setting",0,1,1,2,null,"*","*","*","*","091B=1 AND 400B=1"]
[49,"3B","BN> AR","Indexed String",null,"4x02359",null,"G101","G101",null,1,"No Action","Setting",0,1,1,2,null,"*","*","*","*","091B=1 AND 4012=1"]
[49,"3C","Ext Prot","Indexed String",null,"4x02360",null,"G101","G101",null,1,"No Action","Setting",0,1,1,2,null,"*","*","*","*"]
[49,40,"SYSTEM CHECKS","(Sub Heading)",{"$nulls":14},"*","*","*","*"]
[49,41,"AR with ChkSyn","Indexed String",null,"4x02361",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,null,null,"*",null,"*"]
[49,42,"AR with SysSyn","Indexed String",null,"4x02362",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,null,null,"*",null,"*"]
[49,43,"Live/Dead Ccts","Indexed String",null,"4x02363",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,null,"*","*","*","*"]
[49,44,"No System Checks","Indexed String",null,"4x02364",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,null,"*","*","*","*"]
[49,45,"SysChk on Shot 1","Indexed String",null,"4x02365",null,"G37","G37",null,1,"Enabled","Setting",0,1,1,2,null,"*","*","*","*",{"$nulls":6},"System Check on First Shot"]
["4A",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0925 = 1",{"$nulls":6},"*"]
[null,null,"INPUT LABELS"]
["4A",1,"Opto Input 1","ASCII Text (16 chars)",null,"4x02400","4x02407",null,"G3",null,8,"Input L1","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4A",2,"Opto Input 2","ASCII Text (16 chars)",null,"4x02408","4x02415",null,"G3",null,8,"Input L2","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4A",3,"Opto Input 3","ASCII Text (16 chars)",null,"4x02416","4x02423",null,"G3",null,8,"Input L3","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4A",4,"Opto Input 4","ASCII Text (16 chars)",null,"4x02424","4x02431",null,"G3",null,8,"Input L4","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4A",5,"Opto Input 5","ASCII Text (16 chars)",null,"4x02432","4x02439",null,"G3",null,8,"Input L5","Setting",32,234,1,2,"*","*",null,"*",{"$nulls":8},"*"]
[{"$nulls":19},"*",null,"*"]
["4A",6,"Opto Input 6","ASCII Text (16 chars)",null,"4x02440","4x02447",null,"G3",null,8,"Input L6","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4A",7,"Opto Input 7","ASCII Text (16 chars)",null,"4x02448","4x02455",null,"G3",null,8,"Input L7","Setting",32,234,1,2,"*",null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*"]
["4A",8,"Opto Input 8","ASCII Text (16 chars)",null,"4x02456","4x02463",null,"G3",null,8,"Input L8","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4A",9,"Opto Input 9","ASCII Text (16 chars)",null,"4x02464","4x02471",null,"G3",null,8,"Input L9","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxC only"]
["4A","0A","Opto Input 10","ASCII Text (16 chars)",null,"4x02472","4x02479",null,"G3",null,8,"Input L10","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxC only"]
["4A","0B","Opto Input 11","ASCII Text (16 chars)",null,"4x02480","4x02487",null,"G3",null,8,"Input L11","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxC only"]
["4A","0C","Opto Input 12","ASCII Text (16 chars)",null,"4x02488","4x02495",null,"G3",null,8,"Input L12","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxC only"]
["4A","0D","Opto Input 13","ASCII Text (16 chars)",null,"4x02496","4x02503",null,"G3",null,8,"Input L13","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxC only"]
["4A","0E","Opto Input 14","ASCII Text (16 chars)",null,"4x02504","4x02511",null,"G3",null,8,"Input L14","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxC only"]
["4A","0F","Opto Input 15","ASCII Text (16 chars)",null,"4x02512","4x02519",null,"G3",null,8,"Input L15","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxC only"]
["4A",10,"Opto Input 16","ASCII Text (16 chars)",null,"4x02520","4x02527",null,"G3",null,8,"Input L16","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxC only"]
["4A",11,"Opto Input 17","ASCII Text (16 chars)",null,"4x02528","4x02535",null,"G3",null,8,"Input L17","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",12,"Opto Input 18","ASCII Text (16 chars)",null,"4x02536","4x02543",null,"G3",null,8,"Input L18","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",13,"Opto Input 19","ASCII Text (16 chars)",null,"4x02544","4x02551",null,"G3",null,8,"Input L19","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",14,"Opto Input 20","ASCII Text (16 chars)",null,"4x02552","4x02559",null,"G3",null,8,"Input L20","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",15,"Opto Input 21","ASCII Text (16 chars)",null,"4x02560","4x02567",null,"G3",null,8,"Input L21","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",16,"Opto Input 22","ASCII Text (16 chars)",null,"4x02568","4x02575",null,"G3",null,8,"Input L22","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",17,"Opto Input 23","ASCII Text (16 chars)",null,"4x02576","4x02583",null,"G3",null,8,"Input L23","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",18,"Opto Input 24","ASCII Text (16 chars)",null,"4x02584","4x02591",null,"G3",null,8,"Input L24","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxC, P143xxxE, P143xxxF only","*"]
["4A",19,"Opto Input 25","ASCII Text (16 chars)",null,"4x02592","4x02599",null,"G3",null,8,"Input L25","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4A","1A","Opto Input 26","ASCII Text (16 chars)",null,"4x02600","4x02607",null,"G3",null,8,"Input L26","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4A","1B","Opto Input 27","ASCII Text (16 chars)",null,"4x02608","4x02615",null,"G3",null,8,"Input L27","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4A","1C","Opto Input 28","ASCII Text (16 chars)",null,"4x02616","4x02623",null,"G3",null,8,"Input L28","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4A","1D","Opto Input 29","ASCII Text (16 chars)",null,"4x02624","4x02631",null,"G3",null,8,"Input L29","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4A","1E","Opto Input 30","ASCII Text (16 chars)",null,"4x02632","4x02639",null,"G3",null,8,"Input L30","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4A","1F","Opto Input 31","ASCII Text (16 chars)",null,"4x02640","4x02647",null,"G3",null,8,"Input L31","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4A",20,"Opto Input 32","ASCII Text (16 chars)",null,"4x02648","4x02655",null,"G3",null,8,"Input L32","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxF only","*"]
["4B",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0926 = 1",{"$nulls":6},"*"]
[null,null,"OUTPUT LABELS"]
["4B",1,"Relay 1","ASCII Text (16 chars)",null,"4x02700","4x02707",null,"G3",null,8,"Output R1","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4B",2,"Relay 2","ASCII Text (16 chars)",null,"4x02708","4x02715",null,"G3",null,8,"Output R2","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4B",3,"Relay 3","ASCII Text (16 chars)",null,"4x02716","4x02723",null,"G3",null,8,"Output R3","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4B",4,"Relay 4","ASCII Text (16 chars)",null,"4x02724","4x02731",null,"G3",null,8,"Output R4","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4B",5,"Relay 5","ASCII Text (16 chars)",null,"4x02732","4x02739",null,"G3",null,8,"Output R5","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4B",6,"Relay 6","ASCII Text (16 chars)",null,"4x02740","4x02747",null,"G3",null,8,"Output R6","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4B",7,"Relay 7","ASCII Text (16 chars)",null,"4x02748","4x02755",null,"G3",null,8,"Output R7","Setting",32,234,1,2,"*","*","*","*","*",{"$nulls":7},"*"]
["4B",8,"Relay 8","ASCII Text (16 chars)",null,"4x02756","4x02763",null,"G3",null,8,"Output R8","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxD only"]
["4B",9,"Relay 9","ASCII Text (16 chars)",null,"4x02764","4x02771",null,"G3",null,8,"Output R9","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxD only"]
["4B","0A","Relay 10","ASCII Text (16 chars)",null,"4x02772","4x02779",null,"G3",null,8,"Output R10","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxD only"]
["4B","0B","Relay 11","ASCII Text (16 chars)",null,"4x02780","4x02787",null,"G3",null,8,"Output R11","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxB, P142xxxD only"]
["4B","0C","Relay 12","ASCII Text (16 chars)",null,"4x02788","4x02795",null,"G3",null,8,"Output R12","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxD only"]
["4B","0D","Relay 13","ASCII Text (16 chars)",null,"4x02796","4x02803",null,"G3",null,8,"Output R13","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxD only"]
["4B","0E","Relay 14","ASCII Text (16 chars)",null,"4x02804","4x02811",null,"G3",null,8,"Output R14","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":7},"*"]
[{"$nulls":18},"*",null,"*",{"$nulls":7},"P142xxxD only"]
["4B","0F","Relay 15","ASCII Text (16 chars)",null,"4x02812","4x02819",null,"G3",null,8,"Output R15","Setting",32,234,1,2,null,"*","*","*","*",{"$nulls":6},"P142xxxD only","*"]
[{"$nulls":28},"P143xxxD, P143xxxE, P143xxxG only"]
["4B",10,"Relay 16","ASCII Text (16 chars)",null,"4x02820","4x02827",null,"G3",null,8,"Output R16","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxD, P143xxxE, P143xxxG only","*"]
["4B",11,"Relay 17","ASCII Text (16 chars)",null,"4x02828","4x02835",null,"G3",null,8,"Output R17","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxD, P143xxxE, P143xxxG only","*"]
["4B",12,"Relay 18","ASCII Text (16 chars)",null,"4x02836","4x02843",null,"G3",null,8,"Output R18","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxD, P143xxxE, P143xxxG only","*"]
["4B",13,"Relay 19","ASCII Text (16 chars)",null,"4x02844","4x02851",null,"G3",null,8,"Output R19","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxD, P143xxxE, P143xxxG only","*"]
["4B",14,"Relay 20","ASCII Text (16 chars)",null,"4x02852","4x02859",null,"G3",null,8,"Output R20","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxD, P143xxxE, P143xxxG only","*"]
["4B",15,"Relay 21","ASCII Text (16 chars)",null,"4x02860","4x02867",null,"G3",null,8,"Output R21","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxD, P143xxxE, P143xxxG only","*"]
["4B",16,"Relay 22","ASCII Text (16 chars)",null,"4x02868","4x02875",null,"G3",null,8,"Output R22","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxD, P143xxxE, P143xxxG only","*"]
["4B",17,"Relay 23","ASCII Text (16 chars)",null,"4x02876","4x02883",null,"G3",null,8,"Output R23","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B",18,"Relay 24","ASCII Text (16 chars)",null,"4x02884","4x02891",null,"G3",null,8,"Output R24","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B",19,"Relay 25","ASCII Text (16 chars)",null,"4x02892","4x02899",null,"G3",null,8,"Output R25","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B","1A","Relay 26","ASCII Text (16 chars)",null,"4x02900","4x02907",null,"G3",null,8,"Output R26","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B","1B","Relay 27","ASCII Text (16 chars)",null,"4x02908","4x02915",null,"G3",null,8,"Output R27","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B","1C","Relay 28","ASCII Text (16 chars)",null,"4x02916","4x02923",null,"G3",null,8,"Output R28","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B","1D","Relay 29","ASCII Text (16 chars)",null,"4x02924","4x02931",null,"G3",null,8,"Output R29","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B","1E","Relay 30","ASCII Text (16 chars)",null,"4x02932","4x02939",null,"G3",null,8,"Output R30","Setting",32,234,1,2,null,null,"*",null,"*",{"$nulls":6},"P143xxxG only","*"]
["4B","1F","Relay 31","ASCII Text (16 chars)",null,"4x02940","4x02947",null,"G3",null,8,"Output R31","Setting",32,234,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
["4B",20,"Relay 32","ASCII Text (16 chars)",null,"4x02948","4x02955",null,"G3",null,8,"Output R32","Setting",32,234,1,2,{"$nulls":4},"*",{"$nulls":7},"*"]
["4D",0,"GROUP 1",{"$nulls":14},"*","*","*","*","*","0927 = 1"]
[null,null,"Adv. Freq Prot'n"]
["4D","01","Freq Avg.Cycles","Unsigned Integer (16 bits)",null,"4x13000",null,null,"G1",48,1,5,"Setting",0,48,1,2,"*","*","*","*","*"]
["4D","02","df/dt Avg.Cycles","Unsigned Integer (16 bits)",null,"4x13001",null,null,"G1",48,1,5,"Setting",0,48,1,2,"*","*","*","*","*"]
["4D","03","V<B Status","Indexed String",null,"4x13002",null,"G37","G37",1,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D","04","V<B Voltage Set","Courier Number (Voltage)",null,"4x13003",null,null,"G2",110,1,"25*V1","Setting","10*V1","120*V1","1*V1",2,"*","*","*","*","*","4D03 = 1",{"$nulls":4},"M1","Range covers Ph-N & Ph-Ph"]
["4D","05","V<B Measur Mode","Indexed String",null,"4x13004",null,"G47","G1",null,1,"Phase-Phase","Setting",0,1,1,2,"*","*","*","*","*","4D03 = 1"]
["4D","06","V<B Operate Mode","Indexed String",null,"4x13005",null,"G48","G1",null,1,"Three Phase","Setting",0,1,1,2,"*","*","*","*","*","4D03 = 1"]
["4D","07","Stage 1","Indexed String",null,"4x13006",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D","08","Stg 1 f+t Status","Indexed String",null,"4x13007",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D07 = 1"]
["4D","09","Stg 1 f+t Freq","Courier Number (Frequency)",null,"4x13008",null,null,"G2",2980,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D08 <> 0"]
["4D","0A","Stg 1 f+t Time","Courier Number (Time)",null,"4x13009",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D08 <> 0"]
["4D","0B","df/dt+t 1 Status","Indexed String",null,"4x13010",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D07 = 1"]
["4D","0C","df/dt+t 1 Set","Courier Number (Hz/sec)",null,"4x13011",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D0B <> 0"]
["4D","0D","df/dt+t 1 Time","Courier Number (Time)",null,"4x13012",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D0B <> 0"]
["4D","0E","f+df/dt 1 Status","Indexed String",null,"4x13013",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D07 = 1"]
["4D","0F","f+df/dt 1 freq","Courier Number (Frequency)",null,"4x13014",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D0E <> 0"]
["4D",10,"f+df/dt 1 df/dt","Courier Number (Hz/s)",null,"4x13015",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D0E <> 0"]
["4D",11,"f+Df/Dt 1 Status","Indexed String",null,"4x13016",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D07 = 1"]
["4D",12,"f+Df/Dt 1 freq","Courier Number (Frequency)",null,"4x13017",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D11 <> 0"]
["4D",13,"f+Df/Dt 1 Dfreq","Courier Number (Frequency)",null,"4x13018",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D11 <> 0"]
["4D",14,"f+Df/Dt 1 Dtime","Courier Number (Time)",null,"4x13019",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D11 <> 0"]
["4D",15,"Restore1 Status","Indexed String",null,"4x13020",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D07 = 1"]
["4D",16,"Restore1 Freq","Courier Number (Frequency)",null,"4x13021",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D15 = 1"]
["4D",17,"Restore1 Time","Courier Number (Time)",null,"4x13022",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D15 = 1"]
["4D",18,"Holding Timer 1","Courier Number (Time)",null,"4x13023",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D15 = 1"]
["4D",19,"Stg 1 UV Block","Indexex string",null,"4x13024",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D07 = 1"]
["4D","1A","Stage 2","Indexed String",null,"4x13025",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D","1B","Stg 2 f+t Status","Indexed String",null,"4x13026",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D1A = 1"]
["4D","1C","Stg 2 f+t Freq","Courier Number (Frequency)",null,"4x13027",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D1B <> 0"]
["4D","1D","Stg 2 f+t Time","Courier Number (Time)",null,"4x13028",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D1B <> 0"]
["4D","1E","df/dt+t 2 Status","Indexed String",null,"4x13029",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D1A = 1"]
["4D","1F","df/dt+t 2 Set","Courier Number (Hz/sec)",null,"4x13030",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D1E <> 0"]
["4D",20,"df/dt+t 2 Time","Courier Number (Time)",null,"4x13031",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D1E <> 0"]
["4D",21,"f+df/dt 2 Status","Indexed String",null,"4x13032",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D1A = 1"]
["4D",22,"f+df/dt 2 freq","Courier Number (Frequency)",null,"4x13033",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D21 <> 0"]
["4D",23,"f+df/dt 2 df/dt","Courier Number (Hz/s)",null,"4x13034",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D21 <> 0"]
["4D",24,"f+Df/Dt 2 Status","Indexed String",null,"4x13035",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D1A = 1"]
["4D",25,"f+Df/Dt 2 freq","Courier Number (Frequency)",null,"4x13036",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D24 <> 0"]
["4D",26,"f+Df/Dt 2 Dfreq","Courier Number (Frequency)",null,"4x13037",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D24 <> 0"]
["4D",27,"f+Df/Dt 2 Dtime","Courier Number (Time)",null,"4x13038",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D24 <> 0"]
["4D",28,"Restore2 Status","Indexed String",null,"4x13039",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D1A = 1"]
["4D",29,"Restore2 Freq","Courier Number (Frequency)",null,"4x13040",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D28 = 1"]
["4D","2A","Restore2 Time","Courier Number (Time)",null,"4x13041",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D28 = 1"]
["4D","2B","Holding Timer 2","Courier Number (Time)",null,"4x13042",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D28 = 1"]
["4D","2C","Stg 2 UV Block","Indexex string",null,"4x13043",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D1A = 1"]
["4D","2D","Stage 3","Indexed String",null,"4x13044",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D","2E","Stg 3 f+t Status","Indexed String",null,"4x13045",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D2D = 1"]
["4D","2F","Stg 3 f+t Freq","Courier Number (Frequency)",null,"4x13046",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D2E <> 0  "]
["4D",30,"Stg 3 f+t Time","Courier Number (Time)",null,"4x13047",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D2E <> 0  "]
["4D",31,"df/dt+t 3 Status","Indexed String",null,"4x13048",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D2D = 1"]
["4D",32,"df/dt+t 3 Set","Courier Number (Hz/sec)",null,"4x13049",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D31 <> 0"]
["4D",33,"df/dt+t 3 Time","Courier Number (Time)",null,"4x13050",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D31 <> 0"]
["4D",34,"f+df/dt 3 Status","Indexed String",null,"4x13051",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D2D = 1"]
["4D",35,"f+df/dt 3 freq","Courier Number (Frequency)",null,"4x13052",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D34 <> 0"]
["4D",36,"f+df/dt 3 df/dt","Courier Number (Hz/s)",null,"4x13053",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D34 <> 0"]
["4D",37,"f+Df/Dt 3 Status","Indexed String",null,"4x13054",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D2D = 1"]
["4D",38,"f+Df/Dt 3 freq","Courier Number (Frequency)",null,"4x13055",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D37 <> 0"]
["4D",39,"f+Df/Dt 3 Dfreq","Courier Number (Frequency)",null,"4x13056",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D37 <> 0"]
["4D","3A","f+Df/Dt 3 Dtime","Courier Number (Time)",null,"4x13057",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D37 <> 0"]
["4D","3B","Restore3 Status","Indexed String",null,"4x13058",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D2D = 1"]
["4D","3C","Restore3 Freq","Courier Number (Frequency)",null,"4x13059",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D3B = 1"]
["4D","3D","Restore3 Time","Courier Number (Time)",null,"4x13060",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D3B = 1"]
["4D","3E","Holding Timer 3","Courier Number (Time)",null,"4x13061",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D3B = 1"]
["4D","3F","Stg 3 UV Block","Indexex string",null,"4x13062",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D2D = 1"]
["4D",40,"Stage 4","Indexed String",null,"4x13063",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D",41,"Stg 4 f+t Status","Indexed String",null,"4x13064",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D40 = 1"]
["4D",42,"Stg 4 f+t Freq","Courier Number (Frequency)",null,"4x13065",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D41 <> 0"]
["4D",43,"Stg 4 f+t Time","Courier Number (Time)",null,"4x13066",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D41 <> 0"]
["4D",44,"df/dt+t 4 Status","Indexed String",null,"4x13067",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D40 = 1"]
["4D",45,"df/dt+t 4 Set","Courier Number (Hz/sec)",null,"4x13068",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D44 <> 0"]
["4D",46,"df/dt+t 4 Time","Courier Number (Time)",null,"4x13069",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D44 <> 0"]
["4D",47,"f+df/dt 4 Status","Indexed String",null,"4x13070",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D40 = 1"]
["4D",48,"f+df/dt 4 freq","Courier Number (Frequency)",null,"4x13071",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D47 <> 0"]
["4D",49,"f+df/dt 4 df/dt","Courier Number (Hz/s)",null,"4x13072",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D47 <> 0"]
["4D","4A","f+Df/Dt 4 Status","Indexed String",null,"4x13073",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D40 = 1"]
["4D","4B","f+Df/Dt 4 freq","Courier Number (Frequency)",null,"4x13074",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D4A <> 0  "]
["4D","4C","f+Df/Dt 4 Dfreq","Courier Number (Frequency)",null,"4x13075",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D4A <> 0"]
["4D","4D","f+Df/Dt 4 Dtime","Courier Number (Time)",null,"4x13076",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D4A <> 0"]
["4D","4E","Restore4 Status","Indexed String",null,"4x13077",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D40 = 1"]
["4D","4F","Restore4 Freq","Courier Number (Frequency)",null,"4x13078",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D4E = 1"]
["4D",50,"Restore4 Time","Courier Number (Time)",null,"4x13079",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D4E = 1"]
["4D",51,"Holding Timer 4","Courier Number (Time)",null,"4x13080",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D4E = 1"]
["4D",52,"Stg 4 UV Block","Indexex string",null,"4x13081",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D40 = 1"]
["4D",53,"Stage 5","Indexed String",null,"4x13082",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D",54,"Stg 5 f+t Status","Indexed String",null,"4x13083",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D53 = 1"]
["4D",55,"Stg 5 f+t Freq","Courier Number (Frequency)",null,"4x13084",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D54 <> 0"]
["4D",56,"Stg 5 f+t Time","Courier Number (Time)",null,"4x13085",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D54 <> 0"]
["4D",57,"df/dt+t 5 Status","Indexed String",null,"4x13086",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D53 = 1"]
["4D",58,"df/dt+t 5 Set","Courier Number (Hz/sec)",null,"4x13087",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D57 <> 0"]
["4D",59,"df/dt+t 5 Time","Courier Number (Time)",null,"4x13088",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D57 <> 0"]
["4D","5A","f+df/dt 5 Status","Indexed String",null,"4x13089",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D53 = 1"]
["4D","5B","f+df/dt 5 freq","Courier Number (Frequency)",null,"4x13090",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D5A <> 0"]
["4D","5C","f+df/dt 5 df/dt","Courier Number (Hz/s)",null,"4x13091",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D5A <> 0"]
["4D","5D","f+Df/Dt 5 Status","Indexed String",null,"4x13092",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D53 = 1"]
["4D","5E","f+Df/Dt 5 freq","Courier Number (Frequency)",null,"4x13093",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D5D <> 0"]
["4D","5F","f+Df/Dt 5 Dfreq","Courier Number (Frequency)",null,"4x13094",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D5D <> 0"]
["4D",60,"f+Df/Dt 5 Dtime","Courier Number (Time)",null,"4x13095",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D5D <> 0"]
["4D",61,"Restore5 Status","Indexed String",null,"4x13096",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D53 = 1"]
["4D",62,"Restore5 Freq","Courier Number (Frequency)",null,"4x13097",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D61 = 1"]
["4D",63,"Restore5 Time","Courier Number (Time)",null,"4x13098",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D61 = 1"]
["4D",64,"Holding Timer 5","Courier Number (Time)",null,"4x13099",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D61 = 1"]
["4D",65,"Stg 5 UV Block","Indexex string",null,"4x13100",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D53 = 1"]
["4D",66,"Stage 6","Indexed String",null,"4x13101",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D",67,"Stg 6 f+t Status","Indexed String",null,"4x13102",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D66 = 1"]
["4D",68,"Stg 6 f+t Freq","Courier Number (Frequency)",null,"4x13103",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D67 <> 0"]
["4D",69,"Stg 6 f+t Time","Courier Number (Time)",null,"4x13104",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D67 <> 0"]
["4D","6A","df/dt+t 6 Status","Indexed String",null,"4x13105",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D66 = 1"]
["4D","6B","df/dt+t 6 Set","Courier Number (Hz/sec)",null,"4x13106",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D6A <> 0"]
["4D","6C","df/dt+t 6 Time","Courier Number (Time)",null,"4x13107",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D6A <> 0"]
["4D","6D","f+df/dt 6 Status","Indexed String",null,"4x13108",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D66 = 1"]
["4D","6E","f+df/dt 6 freq","Courier Number (Frequency)",null,"4x13109",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D6D <> 0"]
["4D","6F","f+df/dt 6 df/dt","Courier Number (Hz/s)",null,"4x13110",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D6D <> 0"]
["4D",70,"f+Df/Dt 6 Status","Indexed String",null,"4x13111",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D66 = 1"]
["4D",71,"f+Df/Dt 6 freq","Courier Number (Frequency)",null,"4x13112",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D70 <> 0  "]
["4D",72,"f+Df/Dt 6 Dfreq","Courier Number (Frequency)",null,"4x13113",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D70 <> 0"]
["4D",73,"f+Df/Dt 6 Dtime","Courier Number (Time)",null,"4x13114",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D70 <> 0"]
["4D",74,"Restore6 Status","Indexed String",null,"4x13115",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D66 = 1"]
["4D",75,"Restore6 Freq","Courier Number (Frequency)",null,"4x13116",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D74 = 1"]
["4D",76,"Restore6 Time","Courier Number (Time)",null,"4x13117",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D74 = 1"]
["4D",77,"Holding Timer 6","Courier Number (Time)",null,"4x13118",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D74 = 1"]
["4D",78,"Stg 6 UV Block","Indexex string",null,"4x13119",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D66 = 1"]
["4D",79,"Stage 7","Indexed String",null,"4x13120",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D","7A","Stg 7 f+t Status","Indexed String",null,"4x13121",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D79 = 1"]
["4D","7B","Stg 7 f+t Freq","Courier Number (Frequency)",null,"4x13122",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D7A <> 0"]
["4D","7C","Stg 7 f+t Time","Courier Number (Time)",null,"4x13123",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D7A <> 0"]
["4D","7D","df/dt+t 7 Status","Indexed String",null,"4x13124",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D79 = 1","=",1]
["4D","7E","df/dt+t 7 Set","Courier Number (Hz/sec)",null,"4x13125",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D7D <> 0"]
["4D","7F","df/dt+t 7 Time","Courier Number (Time)",null,"4x13126",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D7D <> 0"]
["4D",80,"f+df/dt 7 Status","Indexed String",null,"4x13127",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D79 = 1"]
["4D",81,"f+df/dt 7 freq","Courier Number (Frequency)",null,"4x13128",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D80 <> 0"]
["4D",82,"f+df/dt 7 df/dt","Courier Number (Hz/s)",null,"4x13129",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D80 <> 0"]
["4D",83,"f+Df/Dt 7 Status","Indexed String",null,"4x13130",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D79 = 1"]
["4D",84,"f+Df/Dt 7 freq","Courier Number (Frequency)",null,"4x13131",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D83 <> 0"]
["4D",85,"f+Df/Dt 7 Dfreq","Courier Number (Frequency)",null,"4x13132",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D83 <> 0"]
["4D",86,"f+Df/Dt 7 Dtime","Courier Number (Time)",null,"4x13133",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D83 <> 0"]
["4D",87,"Restore7 Status","Indexed String",null,"4x13134",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D79 = 1"]
["4D",88,"Restore7 Freq","Courier Number (Frequency)",null,"4x13135",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D87 = 1"]
["4D",89,"Restore7 Time","Courier Number (Time)",null,"4x13136",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D87 = 1"]
["4D","8A","Holding Timer 7","Courier Number (Time)",null,"4x13137",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D87 = 1"]
["4D","8B","Stg 7 UV Block","Indexex string",null,"4x13138",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D79 = 1"]
["4D","8C","Stage 8","Indexed String",null,"4x13139",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D","8D","Stg 8 f+t Status","Indexed String",null,"4x13140",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D8C = 1"]
["4D","8E","Stg 8 f+t Freq","Courier Number (Frequency)",null,"4x13141",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D8D <> 0"]
["4D","8F","Stg 8 f+t Time","Courier Number (Time)",null,"4x13142",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4D8D <> 0"]
["4D",90,"df/dt+t 8 Status","Indexed String",null,"4x13143",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D8C = 1"]
["4D",91,"df/dt+t 8 Set","Courier Number (Hz/sec)",null,"4x13144",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D90 <> 0"]
["4D",92,"df/dt+t 8 Time","Courier Number (Time)",null,"4x13145",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4D90 <> 0"]
["4D",93,"f+df/dt 8 Status","Indexed String",null,"4x13146",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D8C = 1"]
["4D",94,"f+df/dt 8 freq","Courier Number (Frequency)",null,"4x13147",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D93 <> 0"]
["4D",95,"f+df/dt 8 df/dt","Courier Number (Hz/s)",null,"4x13148",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4D93 <> 0"]
["4D",96,"f+Df/Dt 8 Status","Indexed String",null,"4x13149",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D8C = 1"]
["4D",97,"f+Df/Dt 8 freq","Courier Number (Frequency)",null,"4x13150",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D96 <> 0"]
["4D",98,"f+Df/Dt 8 Dfreq","Courier Number (Frequency)",null,"4x13151",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4D96 <> 0"]
["4D",99,"f+Df/Dt 8 Dtime","Courier Number (Time)",null,"4x13152",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4D96 <> 0"]
["4D","9A","Restore8 Status","Indexed String",null,"4x13153",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D8C = 1"]
["4D","9B","Restore8 Freq","Courier Number (Frequency)",null,"4x13154",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4D9A = 1"]
["4D","9C","Restore8 Time","Courier Number (Time)",null,"4x13155",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4D9A = 1"]
["4D","9D","Holding Timer 8","Courier Number (Time)",null,"4x13156",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4D9A = 1"]
["4D","9E","Stg 8 UV Block","Indexex string",null,"4x13157",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D8C = 1"]
["4D","9F","Stage 9","Indexed String",null,"4x13158",null,"G37","G37",null,1,"Disabled","Setting",0,1,1,2,"*","*","*","*","*"]
["4D","A0","Stg 9 f+t Status","Indexed String",null,"4x13159",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D9F","=",1]
["4D","A1","Stg 9 f+t Freq","Courier Number (Frequency)",null,"4x13160",null,null,"G2",2000,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4DA0 <> 0"]
["4D","A2","Stg 9 f+t Time","Courier Number (Time)",null,"4x13161",null,null,"G2",10000,1,2,"Setting",0,100,0.01,2,"*","*","*","*","*","4DA0 <> 0"]
["4D","A3","df/dt+t 9 Status","Indexed String",null,"4x13162",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D9F = 1"]
["4D","A4","df/dt+t 9 Set","Courier Number (Hz/sec)",null,"4x13163",null,null,"G2",999,1,2,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4DA3 <> 0"]
["4D","A5","df/dt+t 9 Time","Courier Number (Time)",null,"4x13164",null,null,"G2",10000,1,0.5,"Setting",0,100,0.01,2,"*","*","*","*","*","4DA3 <> 0"]
["4D","A6","f+df/dt 9 Status","Indexed String",null,"4x13165",null,"G160","G160",null,null,"Disabled","Setting",0,3,1,2,"*","*","*","*","*","4D9F = 1"]
["4D","A7","f+df/dt 9 freq","Courier Number (Frequency)",null,"4x13166",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4DA6 <> 0","<>",0]
["4D","A8","f+df/dt 9 df/dt","Courier Number (Hz/s)",null,"4x13167",null,null,"G2",999,1,1,"Setting",0.01,10,0.01,2,"*","*","*","*","*","4DA6 <> 0"]
["4D","A9","f+Df/Dt 9 Status","Indexed String",null,"4x13168",null,"G159","G159",null,null,"Disabled","Setting",0,2,1,2,"*","*","*","*","*","4D9F = 1"]
["4D","AA","f+Df/Dt 9 freq","Courier Number (Frequency)",null,"4x13169",null,null,"G2",2980.0000000000005,1,49,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4DA9 <> 0","<>",0]
["4D","AB","f+Df/Dt 9 Dfreq","Courier Number (Frequency)",null,"4x13170",null,null,"G2",990,1,1,"Setting",0.1,10,0.01,2,"*","*","*","*","*","4DA9 <> 0","<>",0]
["4D","AC","f+Df/Dt 9 Dtime","Courier Number (Time)",null,"4x13171",null,null,"G2",9998,1,0.5,"Setting",0.02,100,0.01,2,"*","*","*","*","*","4DA9 <> 0","<>",0]
["4D","AD","Restore9 Status","Indexed String",null,"4x13172",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D9F = 1"]
["4D","AE","Restore9 Freq","Courier Number (Frequency)",null,"4x13173",null,null,"G2",2980.0000000000005,1,49.5,"Setting",40.1,69.9,0.01,2,"*","*","*","*","*","4DAD = 1"]
["4D","AF","Restore9 Time","Courier Number (Time)",null,"4x13174",null,null,"G2",28800,1,240,"Setting",0,7200,0.25,2,"*","*","*","*","*","4DAD = 1"]
["4D","B0","Holding Timer 9","Courier Number (Time)",null,"4x13175",null,null,"G2",7199,1,5,"Setting",1,7200,1,2,"*","*","*","*","*","4DAD = 1"]
["4D","B1","Stg 9 UV Block","Indexex string",null,"4x13176",null,"G37","G37",null,null,"Disabled","Setting",0,1,1,2,"*","*","*","*","*","4D9F = 1"]
[50,0,"GROUP 2 PROTECTION SETTINGS",{"$nulls":14},"*","*","*","*","*"]
[null,null,"Repeat of Group 1 columns/rows",null,null,"*x43000","4x04999",{"$nulls":10},"*","*","*","*","*","0908=1"]
[70,0,"GROUP 3 PROTECTION SETTINGS",{"$nulls":14},"*","*","*","*","*"]
[null,null,"Repeat of Group 1 columns/rows",null,null,"*x45000","4x06999",{"$nulls":10},"*","*","*","*","*","0909=1"]
[90,0,"GROUP 4 PROTECTION SETTINGS",{"$nulls":14},"*","*","*","*","*"]
[null,null,"Repeat of Group 1 columns/rows",null,null,"*x47000","4x08999",{"$nulls":10},"*","*","*","*","*","090A=1"]
["B0",0,"(No Header)","Auto extraction Event Record Column","N/A",{"$nulls":12},"*","*","*","*","*"]
["B0",1,"Select Record","Unsigned Integer (16 bits)",{"$nulls":8},"Setting",0,65535,1,null,"*","*","*","*","*",{"$nulls":6},"Unique cyclical fault number(from event)"]
["B0",2,"Faulted Phase","Binary Flag (8 bits) Indexed String",null,null,null,"G16","G16",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Specific Bit Flags Targetting"]
["B0",3,"Start Elements 1","Binary Flag (32 bits) Indexed String",null,null,null,"G84","G84",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Specific Bit Flags Targetting"]
["B0",4,"Start Elements 2","Binary Flag (32 bits) Indexed String",null,null,null,"G107","G107",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Specific Bit Flags Targetting"]
["B0",5,"Start Elements 3","Binary Flag (32 bits) Indexed String",null,null,null,"G161","G161",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",6,"Unused"]
["B0",7,"Trip Elements 1","Binary Flag (32 bits) Indexed String",null,null,null,"G85","G85",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Specific Bit Flags Targetting"]
["B0",8,"Trip Elements 2","Binary Flag (32 bits) Indexed String",null,null,null,"G86","G86",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Specific Bit Flags Targetting"]
["B0",9,"Trip Elements 3","Binary Flag (32 bits) Indexed String",null,null,null,"G162","G162","G162","G162",null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0","0A","Trip Elements 4","Binary Flag (32 bits) Indexed String",null,null,null,"G164","G164",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0","0B","Fault Alarms","Binary Flag (32 bits) Indexed String",null,null,null,"G87","G87",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Product Specific Bit Flags Targetting"]
["B0","0C","Fault Time","IEC870 Date & Time",{"$nulls":4},"G12",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0","0D","Active Group","Unsigned Integer (16 bits)",{"$nulls":4},"G1",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0","0E","System Frequency","Courier Number (frequency)",{"$nulls":4},"G30",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0","0F","Fault Duration","Courier Number (time)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",10,"CB Operate Time","Courier Number (time)",{"$nulls":4},"G25",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",11,"Relay Trip Time","Courier Number (time)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",12,"Fault Location","Courier Number (metres)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",13,"Fault Location","Courier Number (miles)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",14,"Fault Location","Courier Number (impedance)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",15,"Fault Location","Courier Number (percentage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B0",16,"IA","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
["B0",17,"IB","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
["B0",18,"IC","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
["B0",19,"VAB","Courier Number (voltage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
["B0","1A","VBC","Courier Number (voltage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
["B0","1B","VCA","Courier Number (voltage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
["B0","1C","IN Measured","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M5"]
["B0","1D","IN Derived","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
["B0","1E","IN Sensitive","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M6"]
["B0","1F","IREF Diff","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
["B0",20,"IREF Bias","Courier Number (current)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M4"]
["B0",21,"VAN","Courier Number (voltage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
["B0",22,"VBN","Courier Number (voltage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
["B0",23,"VCN","Courier Number (voltage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
["B0",24,"VN Derived","Courier Number (voltage)",{"$nulls":4},"G24",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M1"]
["B0",25,"Admittance","Courier Number (inverse ohms)",{"$nulls":4},"G125",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M6/M1","(091B=1) && (4002=0)"]
["B0",26,"Conductance","Courier Number (inverse ohms)",{"$nulls":4},"G125",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M6/M1","(091B=1) && (4002=0)"]
["B0",27,"Susceptance","Courier Number (inverse ohms)",{"$nulls":4},"G125",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M6/M1","(091B=1) && (4002=0)"]
["B0",28,"Admittance","Courier Number (inverse ohms)",{"$nulls":4},"G125",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M5/M1","(091B=1) && (4002=1)"]
["B0",29,"Conductance","Courier Number (inverse ohms)",{"$nulls":4},"G125",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M5/M1","(091B=1) && (4002=1)"]
["B0","2A","Susceptance","Courier Number (inverse ohms)",{"$nulls":4},"G125",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":5},"M5/M1","(091B=1) && (4002=1)"]
["B1",0,"No Header",null,"N/A",{"$nulls":12},"*","*","*","*","*"]
["B1",1,"Select Record","Unsigned Integer (16 bits)",{"$nulls":8},"Setting",0,65535,1,null,"*","*","*","*","*"]
["B1",2,"Time and Date","IEC870 Date & Time",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*"]
["B1",3,"Record Text","ASCII Text (32 chars)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*"]
["B1",4,"Record Type","Unsigned Integer (32 bits)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*"]
["B1",5,"Record Data","Unsigned Integer (32 bits)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*"]
["B2",0,"DATA TRANSFER                       (No Header)",null,"N/A",{"$nulls":12},"*","*","*","*","*"]
["B2",4,"Domain","Indexed String",null,null,null,"G57","G57",null,null,"PSL Settings","Setting",0,1,1,2,"*","*","*","*","*"]
["B2",8,"Sub-Domain","Indexed String",null,null,null,"G90","G90",null,null,"Group 1","Setting",0,3,1,2,"*","*","*","*","*"]
["B2","0C","Version","Unsigned Integer (16 bits)",{"$nulls":7},256,"Setting",0,65535,1,2,"*","*","*","*","*"]
["B2",10,"Start","Not Used",{"$nulls":13},"*","*","*","*","*"]
["B2",14,"Length","Not Used",{"$nulls":13},"*","*","*","*","*"]
["B2",18,"Reference","Not Used",{"$nulls":13},"*","*","*","*","*"]
["B2","1C","Transfer Mode","Indexed String ",null,null,null,"G76","G76",null,null,6,"Setting",0,7,1,2,"*","*","*","*","*"]
["B2",20,"Data Transfer","Repeated groups of Unsigned Integers",{"$nulls":8},"Setting",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Only settable if Domain = PSL Settings"]
["B3",0,"RECORDER CONTROL             (No Header)",null,"N/A",{"$nulls":12},"*","*","*","*","*"]
["B3",1,"UNUSED",{"$nulls":14},"*","*","*","*","*"]
["B3",2,"Recorder Source","Indexed String",null,null,null,0,0,null,null,"Samples","Data",{"$nulls":4},"*","*","*","*","*"]
["B3","03-1F","Reserved for future use",{"$nulls":14},"*","*","*","*","*"]
["B4",0,"RECORDER EXTRACTION COLUMN (No Header)",null,"N/A",{"$nulls":12},"*","*","*","*","*"]
["B4",1,"Select Record Number - n","Unsigned Integer",{"$nulls":7},0,"Setting",-199,199,1,0,"*","*","*","*","*",null,null,"Data if BF03=1"]
["B4",2,"Trigger Time","IEC870 Date & Time",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*"]
["B4",3,"Active Channels","Binary Flag",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",4,"Channel Types","Binary Flag",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",5,"Channel Offsets","Courier Number (decimal)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",6,"Channel Scaling","Courier Number (decimal)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",7,"Channel SkewVal","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",8,"Channel MinVal","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",9,"Channel MaxVal","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4","0A","Compression Format","Unsigned Integer (16 bits)",{"$nulls":7},1,"Data",{"$nulls":4},"*","*","*","*","*"]
["B4","0B","Upload Compression Record","Unsigned Integer (16 bits)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*"]
["B4","0C-0F","UNUSED",{"$nulls":14},"*","*","*","*","*"]
["B4",10,"No. Of Samples","Unsigned Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",11,"Trig Position","Unsigned Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",12,"Time Base","Courier Number (time)",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",13,"UNUSED",{"$nulls":14},"*","*","*","*","*"]
["B4",14,"Sample Timer","Unsigned Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4","15-1F","UNUSED",{"$nulls":14},"*","*","*","*","*"]
["B4",20,"Dist. Channel 1","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",21,"Dist. Channel 2","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",22,"Dist. Channel 3","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",23,"Dist. Channel 4","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",24,"Dist. Channel 5","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",25,"Dist. Channel 6","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",26,"Dist. Channel 7","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",27,"Dist. Channel 8","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",28,"Dist. Channel 9","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4",29,"Dist. Channel 10","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4","2A","Dist. Channel 11","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4","2B","Dist. Channel 12","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4","2C","Dist. Channel 13","Integer",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4","2D~3D","UNUSED"]
["B4","3E","Dist. Channel 31","Binary Flag",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
["B4","3F","Dist. Channel 32","Binary Flag",{"$nulls":8},"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"Build=IEC60870-5-103"]
[{"$nulls":5},"3x00800",null,null,"G1",null,1,null,"Data",{"$nulls":15},"Number of Disturbance Records (0 to 200)"]
[{"$nulls":5},"3x00801",null,null,"G1",null,1,null,"Data",{"$nulls":15},"Oldest Stored Disturbance Record (1 to 65535)"]
[{"$nulls":5},"3x00802",null,null,"G1",null,1,null,"Data",{"$nulls":15},"Number of Registers in Current Page"]
[{"$nulls":5},"3x00803","3x00929",null,"G1",null,125,null,"Data",{"$nulls":15},"Disturbance Recorder Page (0 to 65535)"]
[{"$nulls":5},"4x00250",null,null,"G1",65534,1,null,"Setting",1,65535,1,2,{"$nulls":11},"Select Disturbance Record"]
[{"$nulls":5},"4x00251",null,null,"G1",null,1,null,"Setting",0,0,1,2,{"$nulls":11},"Select Disturbance Record file format (Presently BINARY format only)"]
[{"$nulls":5},"3x00930","3x00933",null,"G12",null,4,null,"Data",{"$nulls":15},"Timestamp of selected record"]
[{"$nulls":5},"3x00934",null,null,"G1",null,1,null,"Data",{"$nulls":15},"Disturbance recorder status."]
["B5",null,"Calibration Coefficients",null,"N/A",{"$nulls":12},"*","*","*","*","*"]
["B5",1,"Cal Software Version","ASCII Text (16 chars)",{"$nulls":13},"*","*","*","*","*"]
["B5",2,"Cal Date and Time","IEC870 Date & Time",{"$nulls":13},"*","*","*","*","*"]
["B5",3,"Channel Types","Repeated Group 16 * Binary Flag 8 bits",{"$nulls":13},"*","*","*","*","*"]
["B5",4,"Cal Coeffs","Block transfer Repeated Group of UINT32 (4 coeffs voltage channel, 8 coeffs current channel)",{"$nulls":13},"*","*","*","*","*"]
["B6",0,"Comms Diagnostics (Hidden)","Note: No text in column text ","N/A",{"$nulls":12},"*","*","*","*","*"]
["B6",1,"Bus Comms Err Count Front","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6",2,"Bus Message Count Front","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6",3,"Protocol Err Count Front","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6",4,"Busy Count Front","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6",5,"Reset front count","(Reset Menu Cell cmd only)",{"$nulls":13},"*","*","*","*","*"]
["B6",6,"Bus Comms Err Count Rear","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6",7,"Bus Message Count Rear","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6",8,"Protocol Err Count Rear","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6",9,"Busy Count Rear","Unsigned Integer (32 bits)",{"$nulls":13},"*","*","*","*","*"]
["B6","0A","Reset rear count","(Reset Menu Cell cmd only)",{"$nulls":13},"*","*","*","*","*"]
["B7",0,"PSL DATA",{"$nulls":14},"*","*","*","*","*"]
["B7",1,"Grp1 PSL Ref","ASCII Text (32 chars)",null,"3x01000","3x01015",null,"G3",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"\"Model Number\" Default PSL"]
["B7",2,"Date/Time","IEC870 Date & Time",null,"3x01016","3x01019",null,"G12",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B7",3,"Grp1 PSL ID","Unsigned Integer (32 bits)",null,"3x01020","3x01021",null,"G27",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B7",11,"Grp2 PSL Ref","ASCII Text (32 chars)",null,"3x01022","3x01037",null,"G3",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"\"Model Number\" Default PSL"]
["B7",12,"Date/Time","IEC870 Date & Time",null,"3x01038","3x01041",null,"G12",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B7",13,"Grp2 PSL ID","Unsigned Integer (32 bits)",null,"3x01042","3x01043",null,"G27",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B7",21,"Grp3 PSL Ref","ASCII Text (32 chars)",null,"3x01044","3x01059",null,"G3",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"\"Model Number\" Default PSL"]
["B7",22,"Date/Time","IEC870 Date & Time",null,"3x01060","3x01063",null,"G12",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B7",23,"Grp3 PSL ID","Unsigned Integer (32 bits)",null,"3x01064","3x01065",null,"G27",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B7",31,"Grp4 PSL Ref","ASCII Text (32 chars)",null,"3x01066","3x01081",null,"G3",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*",{"$nulls":6},"\"Model Number\" Default PSL"]
["B7",32,"Date/Time","IEC870 Date & Time",null,"3x01082","3x01085",null,"G12",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["B7",33,"Grp4 PSL ID","Unsigned Integer (32 bits)",null,"3x01086","3x01087",null,"G27",null,null,null,"Data",{"$nulls":4},"*","*","*","*","*"]
["BF",0,"COMMS SYS DATA",null,"N/A",{"$nulls":12},"*","*","*","*","*"]
["BF",1,"Dist Record Cntrl Ref","Menu Cell(2)",{"$nulls":7},"B300","Data",{"$nulls":4},"*","*","*","*","*"]
["BF",2,"Dist Record Extract Ref","Menu Cell(2)",{"$nulls":7},"B400","Data",{"$nulls":4},"*","*","*","*","*"]
["BF",3,"Setting Transfer","Unsigned Integer (16 bits)",{"$nulls":8},"Setting",{"$nulls":4},"*","*","*","*","*"]
["BF",4,"Reset Demand Timers","None (Reset Menu Cell)",{"$nulls":8},"Data(but supports Reset Menu cell)",{"$nulls":4},"*","*","*","*","*"]
["BF",5,"UNUSED",{"$nulls":14},"*","*","*","*","*"]
["BF",6,"Block Transfer Ref","Menu Cell(2)",{"$nulls":7},"B200","Data",{"$nulls":4},"*","*","*","*","*"]
["F0",0,"ETHERNET STATUS",null,"N/A",{"$nulls":12},"*","*","*","*","*","DNP3oe"]
["F0",1,"Status Selector",{"$nulls":14},"*","*","*","*","*","DNP3oe"]
["F0",2,"Status Value",{"$nulls":14},"*","*","*","*","*","DNP3oe"]
["F0",3,"Error Value",{"$nulls":14},"*","*","*","*","*","DNP3oe"]
["FE",0,"IEC61850 Only Data Cells",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"Build=UCA2"]
["FE",1,"Poc stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"Build=IEC61850 "]
[{"$nulls":28},"OcpPTOC1.ST.Beh.stVal [Protection]"]
["FE",2,"Poc stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"OcpPTOC2.ST.Beh.stVal [Protection]"]
["FE",2,"Poc stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"OcpPTOC3.ST.Beh.stVal [Protection]"]
["FE",4,"Poc stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"OcpPTOC4.ST.Beh.stVal [Protection]"]
["FE",5,"Chk Syn 1 beh",{"$nulls":16},"*",null,"*",{"$nulls":6},"AscRSYN1.ST.Beh.stVal [Control]"]
["FE",6,"Chk Syn 2 beh",{"$nulls":16},"*",null,"*",{"$nulls":6},"AscRSYN2.ST.Beh.stVal [Control]"]
["FE",7,"Cbf stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"CbfRBRF1.ST.Beh.stVal [Protection]"]
["FE",8,"Cbf stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"CbfRBRF2.ST.Beh.stVal [Protection]"]
["FE",9,"Dfp stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC1.ST.Beh.stVal [Protection]"]
["FE","0A","Dfp stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC2.ST.Beh.stVal [Protection]"]
["FE","0B","Dfp stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC3.ST.Beh.stVal [Protection]"]
["FE","0C","Dfp stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC4.ST.Beh.stVal [Protection]"]
["FE","0D","Efd stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfdPTOC1.ST.Beh.stVal [Protection]"]
["FE","0E","Efd stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfdPTOC2.ST.Beh.stVal [Protection]"]
["FE","0F","Efd stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfdPTOC3.ST.Beh.stVal [Protection]"]
["FE",10,"Efd stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfdPTOC4.ST.Beh.stVal [Protection]"]
["FE",11,"Efm stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfmPTOC1.ST.Beh.stVal [Protection]"]
["FE",12,"Efm stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfmPTOC2.ST.Beh.stVal [Protection]"]
["FE",13,"Efm stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfmPTOC3.ST.Beh.stVal [Protection]"]
["FE",14,"Efm stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"EfmPTOC4.ST.Beh.stVal [Protection]"]
["FE",15,"Ofp stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"FrqPTOF1.ST.Beh.stVal [Protection]"]
["FE",16,"Ofp stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"FrqPTOF2.ST.Beh.stVal [Protection]"]
["FE",17,"Ufp stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"FrqPTUF1.ST.Beh.stVal [Protection]"]
["FE",18,"Ufp stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"FrqPTUF2.ST.Beh.stVal [Protection]"]
["FE",19,"Ufp stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"FrqPTUF3.ST.Beh.stVal [Protection]"]
["FE","1A","Ufp stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"FrqPTUF4.ST.Beh.stVal [Protection]"]
["FE","1B","Noc stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"NgcPTOC1.ST.Beh.stVal [Protection]"]
["FE","1C","Noc stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"NgcPTOC2.ST.Beh.stVal [Protection]"]
["FE","1D","Noc stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"NgcPTOC3.ST.Beh.stVal [Protection]"]
["FE","1E","Noc stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"NgcPTOC4.ST.Beh.stVal [Protection]"]
["FE","1F","Nov stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"NgvPTOV1.ST.Beh.stVal [Protection]"]
["FE",20,"Nvd stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"VtpResPTOV1.ST.Beh.stVal [Protection]"]
["FE",21,"Nvd stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"VtpResPTOV2.ST.Beh.stVal [Protection]"]
["FE",22,"Ref Protn beh",{"$nulls":14},"*","*","*",null,"*",{"$nulls":6},"SenRefPDIF1.ST.Beh.stVal [Protection]"]
["FE",23,"Pov stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"VtpPhsPTOV1.ST.Beh.stVal [Protection]"]
["FE",24,"Pov stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"VtpPhsPTOV2.ST.Beh.stVal [Protection]"]
["FE",25,"Puv stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"VtpPhsPTUV1.ST.Beh.stVal [Protection]"]
["FE",26,"Puv stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"VtpPhsPTUV2.ST.Beh.stVal [Protection]"]
["FE",27,"Sef stg 1 mod",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC1.ST.Mod.stVal [Protection]"]
["FE",28,"Sef stg 2 mod",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC2.ST.Mod.stVal [Protection]"]
["FE",29,"Sef stg 3 mod",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC3.ST.Mod.stVal [Protection]"]
["FE","2A","Sef stg 4 mod",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC4.ST.Mod.stVal [Protection]"]
["FE","2B","Sef stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC1.ST.Beh.stVal [Protection]"]
["FE","2C","Sef stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC2.ST.Beh.stVal [Protection]"]
["FE","2D","Sef stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC3.ST.Beh.stVal [Protection]"]
["FE","2E","Sef stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"SenEftPTOC4.ST.Beh.stVal [Protection]"]
["FE","2F","Thm stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"ThmPTTR1.Beh.stVal [Protection]"]
["FE",30,"Dfp stg 1 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC1.ST.Beh.stVal [Protection]"]
["FE",31,"Dfp stg 2 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC2.ST.Beh.stVal [Protection]"]
["FE",32,"Dfp stg 3 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC3.ST.Beh.stVal [Protection]"]
["FE",33,"Dfp stg 4 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC4.ST.Beh.stVal [Protection]"]
["FE",34,"Dfp stg 5 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC5.ST.Beh.stVal [Protection]"]
["FE",35,"Dfp stg 6 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC6.ST.Beh.stVal [Protection]"]
["FE",36,"Dfp stg 7 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC7.ST.Beh.stVal [Protection]"]
["FE",37,"Dfp stg 8 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC8.ST.Beh.stVal [Protection]"]
["FE",38,"Dfp stg 9 beh",{"$nulls":14},"*","*","*","*","*",{"$nulls":6},"dfpPFRC9.ST.Beh.stVal [Protection]"]

{"sheet":"Data Types","index":2,"n_rows":1590,"n_cols":4,"rows_kept":1590,"cut":false,"hidden":false,"merged":[[1587,2,1587,3],[1588,2,1588,3],[1589,2,1589,3],[1583,2,1583,3],[1584,2,1584,3],[1585,2,1585,3],[1586,2,1586,3],[1579,2,1579,3],[1580,2,1580,3],[1581,2,1581,3],[1582,2,1582,3],[1575,2,1575,3],[1576,2,1576,3],[1577,2,1577,3],[1578,2,1578,3],[1571,2,1571,3],[1572,2,1572,3],[1573,2,1573,3],[1574,2,1574,3],[1567,2,1567,3],[1568,2,1568,3],[1569,2,1569,3],[1570,2,1570,3],[1563,2,1563,3],[1564,2,1564,3],[1565,2,1565,3],[1566,2,1566,3],[1559,2,1559,3],[1560,2,1560,3],[1561,2,1561,3],[1562,2,1562,3],[1555,2,1555,3],[1556,2,1556,3],[1557,2,1557,3],[1558,2,1558,3],[1551,2,1551,3],[1552,2,1552,3],[1553,2,1553,3],[1554,2,1554,3],[1547,2,1547,3],[1548,2,1548,3],[1549,2,1549,3],[1550,2,1550,3],[1543,2,1543,3],[1544,2,1544,3],[1545,2,1545,3],[1546,2,1546,3],[1539,2,1539,3],[1540,2,1540,3],[1541,2,1541,3],[1542,2,1542,3],[1535,2,1535,3],[1536,2,1536,3],[1537,2,1537,3],[1538,2,1538,3],[1531,2,1531,3],[1532,2,1532,3],[1533,2,1533,3],[1534,2,1534,3],[1527,2,1527,3],[1528,2,1528,3],[1529,2,1529,3],[1530,2,1530,3],[1523,2,1523,3],[1524,2,1524,3],[1525,2,1525,3],[1526,2,1526,3],[1519,2,1519,3],[1520,2,1520,3],[1521,2,1521,3],[1522,2,1522,3],[1515,2,1515,3],[1516,2,1516,3],[1517,2,1517,3],[1518,2,1518,3],[1511,2,1511,3],[1512,2,1512,3],[1513,2,1513,3],[1514,2,1514,3],[1507,2,1507,3],[1508,2,1508,3],[1509,2,1509,3],[1510,2,1510,3],[1503,2,1503,3],[1504,2,1504,3],[1505,2,1505,3],[1506,2,1506,3],[1499,2,1499,3],[1500,2,1500,3],[1501,2,1501,3],[1502,2,1502,3],[1495,2,1495,3],[1496,2,1496,3],[1497,2,1497,3],[1498,2,1498,3],[1491,2,1491,3],[1492,2,1492,3],[1493,2,1493,3],[1494,2,1494,3],[1487,2,1487,3],[1488,2,1488,3],[1489,2,1489,3],[1490,2,1490,3],[1483,2,1483,3],[1484,2,1484,3],[1485,2,1485,3],[1486,2,1486,3],[1479,2,1479,3],[1480,2,1480,3],[1481,2,1481,3],[1482,2,1482,3],[1478,2,1478,3],[1473,2,1473,3],[1476,2,1476,3],[1477,2,1477,3],[1472,2,1472,3],[1474,2,1474,3],[1475,2,1475,3],[1468,2,1468,3],[1469,2,1469,3],[1471,2,1471,3],[1461,2,1461,3],[1462,2,1462,3],[1463,2,1463,3],[1470,2,1470,3],[1464,2,1464,3],[1465,2,1465,3],[1466,2,1466,3],[1467,2,1467,3],[1457,2,1457,3],[1458,2,1458,3],[1459,2,1459,3],[1460,2,1460,3],[1453,2,1453,3],[1454,2,1454,3],[1455,2,1455,3],[1456,2,1456,3],[1449,2,1449,3],[1450,2,1450,3],[1451,2,1451,3],[1452,2,1452,3],[1445,2,1445,3],[1446,2,1446,3],[1447,2,1447,3],[1448,2,1448,3],[1441,2,1441,3],[1442,2,1442,3],[1443,2,1443,3],[1444,2,1444,3],[1437,2,1437,3],[1438,2,1438,3],[1439,2,1439,3],[1440,2,1440,3],[1433,2,1433,3],[1434,2,1434,3],[1435,2,1435,3],[1436,2,1436,3],[1429,2,1429,3],[1430,2,1430,3],[1431,2,1431,3],[1432,2,1432,3],[1425,2,1425,3],[1426,2,1426,3],[1427,2,1427,3],[1428,2,1428,3],[1421,2,1421,3],[1422,2,1422,3],[1423,2,1423,3],[1424,2,1424,3],[1417,2,1417,3],[1418,2,1418,3],[1419,2,1419,3],[1420,2,1420,3],[1413,2,1413,3],[1414,2,1414,3],[1415,2,1415,3],[1416,2,1416,3],[1409,2,1409,3],[1410,2,1410,3],[1411,2,1411,3],[1412,2,1412,3],[1405,2,1405,3],[1406,2,1406,3],[1407,2,1407,3],[1408,2,1408,3],[1401,2,1401,3],[1402,2,1402,3],[1403,2,1403,3],[1404,2,1404,3],[1397,2,1397,3],[1398,2,1398,3],[1399,2,1399,3],[1400,2,1400,3],[1393,2,1393,3],[1394,2,1394,3],[1395,2,1395,3],[1396,2,1396,3],[1389,2,1389,3],[1390,2,1390,3],[1391,2,1391,3],[1392,2,1392,3],[1385,2,1385,3],[1386,2,1386,3],[1387,2,1387,3],[1388,2,1388,3],[1381,2,1381,3],[1382,2,1382,3],[1383,2,1383,3],[1384,2,1384,3],[1377,2,1377,3],[1378,2,1378,3],[1379,2,1379,3],[1380,2,1380,3],[1341,2,1341,3],[1342,2,1342,3],[1343,2,1343,3],[1376,2,1376,3],[1337,2,1337,3],[1338,2,1338,3],[1339,2,1339,3],[1340,2,1340,3],[1333,2,1333,3],[1334,2,1334,3],[1335,2,1335,3],[1336,2,1336,3],[1329,2,1329,3],[1330,2,1330,3],[1331,2,1331,3],[1332,2,1332,3],[1325,2,1325,3],[1326,2,1326,3],[1327,2,1327,3],[1328,2,1328,3],[1321,2,1321,3],[1322,2,1322,3],[1323,2,1323,3],[1324,2,1324,3],[1317,2,1317,3],[1318,2,1318,3],[1319,2,1319,3],[1320,2,1320,3],[1313,2,1313,3],[1314,2,1314,3],[1315,2,1315,3],[1316,2,1316,3],[1309,2,1309,3],[1310,2,1310,3],[1311,2,1311,3],[1312,2,1312,3],[1305,2,1305,3],[1306,2,1306,3],[1307,2,1307,3],[1308,2,1308,3],[1301,2,1301,3],[1302,2,1302,3],[1303,2,1303,3],[1304,2,1304,3],[1297,2,1297,3],[1298,2,1298,3],[1299,2,1299,3],[1300,2,1300,3],[1293,2,1293,3],[1294,2,1294,3],[1295,2,1295,3],[1296,2,1296,3],[1289,2,1289,3],[1290,2,1290,3],[1291,2,1291,3],[1292,2,1292,3],[1285,2,1285,3],[1286,2,1286,3],[1287,2,1287,3],[1288,2,1288,3],[1281,2,1281,3],[1282,2,1282,3],[1283,2,1283,3],[1284,2,1284,3],[1277,2,1277,3],[1278,2,1278,3],[1279,2,1279,3],[1280,2,1280,3],[1273,2,1273,3],[1274,2,1274,3],[1275,2,1275,3],[1276,2,1276,3],[1269,2,1269,3],[1270,2,1270,3],[1271,2,1271,3],[1272,2,1272,3],[1265,2,1265,3],[1266,2,1266,3],[1267,2,1267,3],[1268,2,1268,3],[1261,2,1261,3],[1262,2,1262,3],[1263,2,1263,3],[1264,2,1264,3],[1257,2,1257,3],[1258,2,1258,3],[1259,2,1259,3],[1260,2,1260,3],[1253,2,1253,3],[1254,2,1254,3],[1255,2,1255,3],[1256,2,1256,3],[1249,2,1249,3],[1250,2,1250,3],[1251,2,1251,3],[1252,2,1252,3],[1245,2,1245,3],[1246,2,1246,3],[1247,2,1247,3],[1248,2,1248,3],[1241,2,1241,3],[1242,2,1242,3],[1243,2,1243,3],[1244,2,1244,3],[1237,2,1237,3],[1238,2,1238,3],[1239,2,1239,3],[1240,2,1240,3],[1233,2,1233,3],[1234,2,1234,3],[1235,2,1235,3],[1236,2,1236,3],[1229,2,1229,3],[1230,2,1230,3],[1231,2,1231,3],[1232,2,1232,3],[1225,2,1225,3],[1226,2,1226,3],[1227,2,1227,3],[1228,2,1228,3],[1221,2,1221,3],[1222,2,1222,3],[1223,2,1223,3],[1224,2,1224,3],[1217,2,1217,3],[1218,2,1218,3],[1219,2,1219,3],[1220,2,1220,3],[1213,2,1213,3],[1214,2,1214,3],[1215,2,1215,3],[1216,2,1216,3],[1209,2,1209,3],[1210,2,1210,3],[1211,2,1211,3],[1212,2,1212,3],[1205,2,1205,3],[1206,2,1206,3],[1207,2,1207,3],[1208,2,1208,3],[1201,2,1201,3],[1202,2,1202,3],[1203,2,1203,3],[1204,2,1204,3],[1197,2,1197,3],[1198,2,1198,3],[1199,2,1199,3],[1200,2,1200,3],[1193,2,1193,3],[1194,2,1194,3],[1195,2,1195,3],[1196,2,1196,3],[1189,2,1189,3],[1190,2,1190,3],[1191,2,1191,3],[1192,2,1192,3],[1185,2,1185,3],[1186,2,1186,3],[1187,2,1187,3],[1188,2,1188,3],[1181,2,1181,3],[1182,2,1182,3],[1183,2,1183,3],[1184,2,1184,3],[1177,2,1177,3],[1178,2,1178,3],[1179,2,1179,3],[1180,2,1180,3],[1173,2,1173,3],[1174,2,1174,3],[1175,2,1175,3],[1176,2,1176,3],[1169,2,1169,3],[1170,2,1170,3],[1171,2,1171,3],[1172,2,1172,3],[1155,2,1155,3],[1156,2,1156,3],[1167,2,1167,3],[1168,2,1168,3],[1151,2,1151,3],[1152,2,1152,3],[1153,2,1153,3],[1154,2,1154,3],[1147,2,1147,3],[1148,2,1148,3],[1149,2,1149,3],[1150,2,1150,3],[1143,2,1143,3],[1144,2,1144,3],[1145,2,1145,3],[1146,2,1146,3],[1139,2,1139,3],[1140,2,1140,3],[1141,2,1141,3],[1142,2,1142,3],[1135,2,1135,3],[1136,2,1136,3],[1137,2,1137,3],[1138,2,1138,3],[1131,2,1131,3],[1132,2,1132,3],[1133,2,1133,3],[1134,2,1134,3],[1127,2,1127,3],[1128,2,1128,3],[1129,2,1129,3],[1130,2,1130,3],[1123,2,1123,3],[1124,2,1124,3],[1125,2,1125,3],[1126,2,1126,3],[1119,2,1119,3],[1120,2,1120,3],[1121,2,1121,3],[1122,2,1122,3],[1116,2,1116,3],[1117,2,1117,3],[1118,2,1118,3],[1112,2,1112,3],[1113,2,1113,3],[1114,2,1114,3],[1115,2,1115,3],[1108,2,1108,3],[1109,2,1109,3],[1110,2,1110,3],[1111,2,1111,3],[1104,2,1104,3],[1105,2,1105,3],[1106,2,1106,3],[1107,2,1107,3],[1100,2,1100,3],[1101,2,1101,3],[1102,2,1102,3],[1103,2,1103,3],[1096,2,1096,3],[1097,2,1097,3],[1098,2,1098,3],[1099,2,1099,3],[1092,2,1092,3],[1093,2,1093,3],[1094,2,1094,3],[1095,2,1095,3],[1088,2,1088,3],[1089,2,1089,3],[1090,2,1090,3],[1091,2,1091,3],[1084,2,1084,3],[1085,2,1085,3],[1086,2,1086,3],[1087,2,1087,3],[1080,2,1080,3],[1081,2,1081,3],[1082,2,1082,3],[1083,2,1083,3],[1076,2,1076,3],[1077,2,1077,3],[1078,2,1078,3],[1079,2,1079,3],[1072,2,1072,3],[1073,2,1073,3],[1074,2,1074,3],[1075,2,1075,3],[1068,2,1068,3],[1069,2,1069,3],[1070,2,1070,3],[1071,2,1071,3],[1064,2,1064,3],[1065,2,1065,3],[1066,2,1066,3],[1067,2,1067,3],[1060,2,1060,3],[1061,2,1061,3],[1062,2,1062,3],[1063,2,1063,3],[1056,2,1056,3],[1057,2,1057,3],[1058,2,1058,3],[1059,2,1059,3],[1052,2,1052,3],[1053,2,1053,3],[1054,2,1054,3],[1055,2,1055,3],[1046,2,1046,3],[1051,2,1051,3],[1043,2,1043,3],[1044,2,1044,3],[1045,2,1045,3],[1047,2,1047,3],[1048,2,1048,3],[1049,2,1049,3],[1050,2,1050,3],[1039,2,1039,3],[1040,2,1040,3],[1041,2,1041,3],[1042,2,1042,3],[1035,2,1035,3],[1036,2,1036,3],[1037,2,1037,3],[1038,2,1038,3],[1031,2,1031,3],[1032,2,1032,3],[1033,2,1033,3],[1034,2,1034,3],[1029,2,1029,3],[1030,2,1030,3],[1023,2,1023,3],[980,2,980,3],[981,2,981,3],[995,2,995,3],[1009,2,1009,3],[976,2,976,3],[977,2,977,3],[978,2,978,3],[979,2,979,3],[972,2,972,3],[973,2,973,3],[974,2,974,3],[975,2,975,3],[969,2,969,3],[970,2,970,3],[971,2,971,3],[965,2,965,3],[966,2,966,3],[967,2,967,3],[968,2,968,3],[961,2,961,3],[962,2,962,3],[963,2,963,3],[964,2,964,3],[957,2,957,3],[958,2,958,3],[959,2,959,3],[960,2,960,3],[953,2,953,3],[954,2,954,3],[955,2,955,3],[956,2,956,3],[949,2,949,3],[950,2,950,3],[951,2,951,3],[952,2,952,3],[945,2,945,3],[946,2,946,3],[947,2,947,3],[948,2,948,3],[941,2,941,3],[942,2,942,3],[943,2,943,3],[944,2,944,3],[937,2,937,3],[938,2,938,3],[939,2,939,3],[940,2,940,3],[933,2,933,3],[934,2,934,3],[935,2,935,3],[936,2,936,3],[929,2,929,3],[930,2,930,3],[931,2,931,3],[932,2,932,3],[925,2,925,3],[926,2,926,3],[927,2,927,3],[928,2,928,3],[921,2,921,3],[922,2,922,3],[923,2,923,3],[924,2,924,3],[917,2,917,3],[918,2,918,3],[919,2,919,3],[920,2,920,3],[913,2,913,3],[914,2,914,3],[915,2,915,3],[916,2,916,3],[909,2,909,3],[910,2,910,3],[911,2,911,3],[912,2,912,3],[905,2,905,3],[906,2,906,3],[907,2,907,3],[908,2,908,3],[901,2,901,3],[902,2,902,3],[903,2,903,3],[904,2,904,3],[897,2,897,3],[898,2,898,3],[899,2,899,3],[900,2,900,3],[893,2,893,3],[894,2,894,3],[895,2,895,3],[896,2,896,3],[889,2,889,3],[890,2,890,3],[891,2,891,3],[892,2,892,3],[885,2,885,3],[886,2,886,3],[887,2,887,3],[888,2,888,3],[881,2,881,3],[882,2,882,3],[883,2,883,3],[884,2,884,3],[877,2,877,3],[878,2,878,3],[879,2,879,3],[880,2,880,3],[873,2,873,3],[874,2,874,3],[875,2,875,3],[876,2,876,3],[869,2,869,3],[870,2,870,3],[871,2,871,3],[872,2,872,3],[865,2,865,3],[866,2,866,3],[867,2,867,3],[868,2,868,3],[861,2,861,3],[862,2,862,3],[863,2,863,3],[864,2,864,3],[857,2,857,3],[858,2,858,3],[859,2,859,3],[860,2,860,3],[853,2,853,3],[854,2,854,3],[855,2,855,3],[856,2,856,3],[849,2,849,3],[850,2,850,3],[851,2,851,3],[852,2,852,3],[845,2,845,3],[846,2,846,3],[847,2,847,3],[848,2,848,3],[841,2,841,3],[842,2,842,3],[843,2,843,3],[844,2,844,3],[837,2,837,3],[838,2,838,3],[839,2,839,3],[840,2,840,3],[828,2,828,3],[834,2,834,3],[835,2,835,3],[836,2,836,3],[824,2,824,3],[825,2,825,3],[826,2,826,3],[827,2,827,3],[820,2,820,3],[821,2,821,3],[822,2,822,3],[823,2,823,3],[816,2,816,3],[817,2,817,3],[818,2,818,3],[819,2,819,3],[812,2,812,3],[813,2,813,3],[814,2,814,3],[815,2,815,3],[808,2,808,3],[809,2,809,3],[810,2,810,3],[811,2,811,3],[804,2,804,3],[805,2,805,3],[806,2,806,3],[807,2,807,3],[800,2,800,3],[801,2,801,3],[802,2,802,3],[803,2,803,3],[796,2,796,3],[797,2,797,3],[798,2,798,3],[799,2,799,3],[792,2,792,3],[793,2,793,3],[794,2,794,3],[795,2,795,3],[788,2,788,3],[789,2,789,3],[790,2,790,3],[791,2,791,3],[784,2,784,3],[785,2,785,3],[786,2,786,3],[787,2,787,3],[780,2,780,3],[781,2,781,3],[782,2,782,3],[783,2,783,3],[776,2,776,3],[777,2,777,3],[778,2,778,3],[779,2,779,3],[740,2,740,3],[741,2,741,3],[742,2,742,3],[743,2,743,3],[736,2,736,3],[737,2,737,3],[738,2,738,3],[739,2,739,3],[732,2,732,3],[733,2,733,3],[734,2,734,3],[735,2,735,3],[728,2,728,3],[729,2,729,3],[730,2,730,3],[731,2,731,3],[724,2,724,3],[725,2,725,3],[726,2,726,3],[727,2,727,3],[720,2,720,3],[721,2,721,3],[722,2,722,3],[723,2,723,3],[716,2,716,3],[717,2,717,3],[718,2,718,3],[719,2,719,3],[712,2,712,3],[713,2,713,3],[714,2,714,3],[715,2,715,3],[708,2,708,3],[709,2,709,3],[710,2,710,3],[711,2,711,3],[704,2,704,3],[705,2,705,3],[706,2,706,3],[707,2,707,3],[700,2,700,3],[701,2,701,3],[702,2,702,3],[703,2,703,3],[696,2,696,3],[697,2,697,3],[698,2,698,3],[699,2,699,3],[692,2,692,3],[693,2,693,3],[694,2,694,3],[695,2,695,3],[688,2,688,3],[689,2,689,3],[690,2,690,3],[691,2,691,3],[684,2,684,3],[685,2,685,3],[686,2,686,3],[687,2,687,3],[679,2,679,3],[680,2,680,3],[682,2,682,3],[683,2,683,3],[675,2,675,3],[676,2,676,3],[677,2,677,3],[678,2,678,3],[671,2,671,3],[672,2,672,3],[673,2,673,3],[674,2,674,3],[667,2,667,3],[668,2,668,3],[669,2,669,3],[670,2,670,3],[663,2,663,3],[664,2,664,3],[665,2,665,3],[666,2,666,3],[659,2,659,3],[660,2,660,3],[661,2,661,3],[662,2,662,3],[655,2,655,3],[656,2,656,3],[657,2,657,3],[658,2,658,3],[651,2,651,3],[652,2,652,3],[653,2,653,3],[654,2,654,3],[647,2,647,3],[648,2,648,3],[649,2,649,3],[650,2,650,3],[643,2,643,3],[644,2,644,3],[645,2,645,3],[646,2,646,3],[639,2,639,3],[640,2,640,3],[641,2,641,3],[642,2,642,3],[635,2,635,3],[636,2,636,3],[637,2,637,3],[638,2,638,3],[631,2,631,3],[632,2,632,3],[633,2,633,3],[634,2,634,3],[627,2,627,3],[628,2,628,3],[629,2,629,3],[630,2,630,3],[623,2,623,3],[624,2,624,3],[625,2,625,3],[626,2,626,3],[619,2,619,3],[620,2,620,3],[621,2,621,3],[622,2,622,3],[615,2,615,3],[616,2,616,3],[617,2,617,3],[618,2,618,3],[611,2,611,3],[612,2,612,3],[613,2,613,3],[614,2,614,3],[607,2,607,3],[608,2,608,3],[609,2,609,3],[610,2,610,3],[603,2,603,3],[604,2,604,3],[605,2,605,3],[606,2,606,3],[599,2,599,3],[600,2,600,3],[601,2,601,3],[602,2,602,3],[595,2,595,3],[596,2,596,3],[597,2,597,3],[598,2,598,3],[591,2,591,3],[592,2,592,3],[593,2,593,3],[594,2,594,3],[587,2,587,3],[588,2,588,3],[589,2,589,3],[590,2,590,3],[583,2,583,3],[584,2,584,3],[585,2,585,3],[586,2,586,3],[579,2,579,3],[580,2,580,3],[581,2,581,3],[582,2,582,3],[575,2,575,3],[576,2,576,3],[577,2,577,3],[578,2,578,3],[571,2,571,3],[572,2,572,3],[573,2,573,3],[574,2,574,3],[569,2,569,3],[570,2,570,3],[507,2,507,3],[508,2,508,3],[561,2,561,3],[503,2,503,3],[504,2,504,3],[505,2,505,3],[506,2,506,3],[499,2,499,3],[500,2,500,3],[501,2,501,3],[502,2,502,3],[491,2,491,3],[496,2,496,3],[497,2,497,3],[498,2,498,3],[487,2,487,3],[488,2,488,3],[489,2,489,3],[490,2,490,3],[483,2,483,3],[484,2,484,3],[485,2,485,3],[486,2,486,3],[479,2,479,3],[480,2,480,3],[481,2,481,3],[482,2,482,3],[475,2,475,3],[476,2,476,3],[477,2,477,3],[478,2,478,3],[471,2,471,3],[472,2,472,3],[473,2,473,3],[474,2,474,3],[467,2,467,3],[468,2,468,3],[469,2,469,3],[470,2,470,3],[463,2,463,3],[464,2,464,3],[465,2,465,3],[466,2,466,3],[459,2,459,3],[460,2,460,3],[461,2,461,3],[462,2,462,3],[455,2,455,3],[456,2,456,3],[457,2,457,3],[458,2,458,3],[451,2,451,3],[452,2,452,3],[453,2,453,3],[454,2,454,3],[447,2,447,3],[448,2,448,3],[449,2,449,3],[450,2,450,3],[443,2,443,3],[444,2,444,3],[445,2,445,3],[446,2,446,3],[439,2,439,3],[440,2,440,3],[441,2,441,3],[442,2,442,3],[435,2,435,3],[436,2,436,3],[437,2,437,3],[438,2,438,3],[431,2,431,3],[432,2,432,3],[433,2,433,3],[434,2,434,3],[427,2,427,3],[428,2,428,3],[429,2,429,3],[430,2,430,3],[423,2,423,3],[424,2,424,3],[425,2,425,3],[426,2,426,3],[419,2,419,3],[420,2,420,3],[421,2,421,3],[422,2,422,3],[415,2,415,3],[416,2,416,3],[417,2,417,3],[418,2,418,3],[411,2,411,3],[412,2,412,3],[413,2,413,3],[414,2,414,3],[407,2,407,3],[408,2,408,3],[409,2,409,3],[410,2,410,3],[403,2,403,3],[404,2,404,3],[405,2,405,3],[406,2,406,3]],"merged_total":1324,"flags":["formulas_cached_only","merged_cut"]}
["Data Types"]
["TYPE","VALUE/BIT MASK","DESCRIPTION"]
["G1",null,"UNSIGNED INTEGER"]
[null,null,"eg. 5678 stored as 5678"]
["G2",null,"NUMERIC SETTING"]
[null,null,"See 50300.3110.004"]
["G3",null,"ASCII TEXT CHARACTERS"]
[null,"0x00FF","Second character"]
[null,"0xFF00","First character"]
["G4",null,"PLANT STATUS (1 REGISTER)"]
[null,"0x0001","CB1 Open 1 (0 = Off, 1 = On)"]
[null,"0x0002","CB1 Closed 2 (0 = Off, 1 = On)"]
[null,"0x0004","Not Used 3 (0 = Off, 1 = On)"]
[null,"0x0008","Not Used 4 (0 = Off, 1 = On)"]
[null,"0x0010","Not Used 5 (0 = Off, 1 = On)"]
[null,"0x0020","Not Used 6 (0 = Off, 1 = On)"]
[null,"0x0040","Not Used 7 (0 = Off, 1 = On)"]
[null,"0x0080","Not Used 8 (0 = Off, 1 = On)"]
[null,"0x0100","Not Used 9 (0 = Off, 1 = On)"]
[null,"0x0200","Not Used 10 (0 = Off, 1 = On)"]
[null,"0x0400","Not Used 11 (0 = Off, 1 = On)"]
[null,"0x0800","Not Used 12 (0 = Off, 1 = On)"]
[null,"0x1000","Not Used 13 (0 = Off, 1 = On)"]
[null,"0x2000","Not Used 14 (0 = Off, 1 = On)"]
[null,"0x4000","Not Used 15 (0 = Off, 1 = On)"]
[null,"0x8000","Not Used 16 (0 = Off, 1 = On)"]
["G5",null,"CONTROL STATUS (1 REGISTER)"]
[null,"0x0001","Not Used 1 (0 = Off, 1 = On)"]
[null,"0x0002","Not Used 2 (0 = Off, 1 = On)"]
[null,"0x0004","Not Used 3 (0 = Off, 1 = On)"]
[null,"0x0008","Not Used 4 (0 = Off, 1 = On)"]
[null,"0x0010","Not Used 5 (0 = Off, 1 = On)"]
[null,"0x0020","Not Used 6 (0 = Off, 1 = On)"]
[null,"0x0040","Not Used 7 (0 = Off, 1 = On)"]
[null,"0x0080","Not Used 8 (0 = Off, 1 = On)"]
[null,"0x0100","Not Used 9 (0 = Off, 1 = On)"]
[null,"0x0200","Not Used 10 (0 = Off, 1 = On)"]
[null,"0x0400","Not Used 11 (0 = Off, 1 = On)"]
[null,"0x0800","Not Used 12 (0 = Off, 1 = On)"]
[null,"0x1000","Not Used 13 (0 = Off, 1 = On)"]
[null,"0x2000","Not Used 14 (0 = Off, 1 = On)"]
[null,"0x4000","Not Used 15 (0 = Off, 1 = On)"]
[null,"0x8000","Not Used 16 (0 = Off, 1 = On)"]
["G6",null,"Record Control Command Register"]
[null,0,"No Operation"]
[null,1,"Clear Event Records"]
[null,2,"Clear Fault Record"]
[null,3,"Clear Maintenance Records"]
[null,4,"Reset Indications"]
[null,5,"Clear Disturbance Records"]
["G7",null,"VTS Indicate/Block"]
[null,0,"Blocking"]
[null,1,"Indication"]
["G8",null,"LOGIC INPUT STATUS"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Opto 1 Input State (0=Of, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0002","Opto 2 Input State (0=Off, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0004","Opto 3 Input State (0=Off, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0008","Opto 4 Input State (0=Off, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0010","Opto 5 Input State (0=Off, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0020","Opto 6 Input State (0=Off, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0040","Opto 7 Input State (0=Off, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0080","Opto 8 Input State (0=Off, 1=Energised)            P141/P142/P143/P144"]
[null,"0x0000,0x0100","Opto 9 Input State (0=Off, 1=Energised)            P142xxxB, C/P143/P144xxxB, C"]
[null,"0x0000,0x0200","Opto 10 Input State (0=Off, 1=Energised)          P142xxxB, C/P143/P144xxxB, C"]
[null,"0x0000,0x0400","Opto 11 Input State (0=Off, 1=Energised)          P142xxxB, C/P143/P144xxxB, C"]
[null,"0x0000,0x0800","Opto 12 Input State (0=Off, 1=Energised)          P142xxxB, C/P143/P144xxxB, C"]
[null,"0x0000,0x1000","Opto 13 Input State (0=Off, 1=Energised)          P142xxxC/P143/P144xxxC"]
[null,"0x0000,0x2000","Opto 14 Input State (0=Off, 1=Energised)          P142xxxC/P143/P144xxxC"]
[null,"0x0000,0x4000","Opto 15 Input State (0=Off, 1=Energised)          P142xxxC/P143/P144xxxC"]
[null,"0x0000,0x8000","Opto 16 Input State (0=Off, 1=Energised)          P142xxxC/P143/P144xxxC"]
[null,"0x0001,0x0000","Opto 17 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0002,0x0000","Opto 18 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0004,0x0000","Opto 19 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0008,0x0000","Opto 20 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0010,0x0000","Opto 21 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0020,0x0000","Opto 22 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0040,0x0000","Opto 23 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0080,0x0000","Opto 24 Input State (0=Off, 1=Energised)          P143xxxC, E, F "]
[null,"0x0100,0x0000","Opto 25 Input State (0=Off, 1=Energised)          P143xxxF "]
[null,"0x0200,0x0000","Opto 26 Input State (0=Off, 1=Energised)          P143xxxF "]
[null,"0x0400,0x0000","Opto 27 Input State (0=Off, 1=Energised)          P143xxxF "]
[null,"0x0800,0x0000","Opto 28 Input State (0=Off, 1=Energised)          P143xxxF "]
[null,"0x1000,0x0000","Opto 29 Input State (0=Off, 1=Energised)          P143xxxF "]
[null,"0x2000,0x0000","Opto 30 Input State (0=Off, 1=Energised)          P143xxxF "]
[null,"0x4000,0x0000","Opto 31 Input State (0=Off, 1=Energised)          P143xxxF "]
[null,"0x8000,0x0000","Opto 32 Input State (0=Off, 1=Energised)          P143xxxF "]
["G9",null,"RELAY OUTPUT STATUS"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Relay 1 (0=Not Operated, 1=Operated)            P141/P142/P143/P144"]
[null,"0x0000,0x0002","Relay 2 (0=Not Operated, 1=Operated)            P141/P142/P143/P144"]
[null,"0x0000,0x0004","Relay 3 (0=Not Operated, 1=Operated)            P141/P142/P143/P144"]
[null,"0x0000,0x0008","Relay 4 (0=Not Operated, 1=Operated)            P141/P142/P143/P144"]
[null,"0x0000,0x0010","Relay 5 (0=Not Operated, 1=Operated)            P141/P142/P143/P144"]
[null,"0x0000,0x0020","Relay 6 (0=Not Operated, 1=Operated)            P141/P142/P143/P144"]
[null,"0x0000,0x0040","Relay 7 (0=Not Operated, 1=Operated)            P141/P142/P143/P144"]
[null,"0x0000,0x0080","Relay 8 (0=Not Operated, 1=Operated)            P142xxxB, D/P143/P144xxxB, D"]
[null,"0x0000,0x0100","Relay 9 (0=Not Operated, 1=Operated)            P142xxxB, D/P143/P144xxxB, D"]
[null,"0x0000,0x0200","Relay 10 (0=Not Operated, 1=Operated)          P142xxxB, D/P143/P144xxxB, D"]
[null,"0x0000,0x0400","Relay 11 (0=Not Operated, 1=Operated)          P142xxxB, D/P143/P144xxxB, D"]
[null,"0x0000,0x0800","Relay 12 (0=Not Operated, 1=Operated)          P142xxxD/P143/P144xxxD"]
[null,"0x0000,0x1000","Relay 13 (0=Not Operated, 1=Operated)          P142xxxD/P143/P144xxxD"]
[null,"0x0000,0x2000","Relay 14 (0=Not Operated, 1=Operated)          P142xxxD/P143/P144xxxD"]
[null,"0x0000,0x4000","Relay 15 (0=Not Operated, 1=Operated)          P142xxxD/P143xxxD, E, G/P144xxxD"]
[null,"0x0000,0x8000","Relay 16 (0=Not Operated, 1=Operated)          P143xxxD, E, G"]
[null,"0x0001,0x0000","Relay 17 (0=Not Operated, 1=Operated)          P143xxxD, E, G"]
[null,"0x0002,0x0000","Relay 18 (0=Not Operated, 1=Operated)          P143xxxD, E, G"]
[null,"0x0004,0x0000","Relay 19 (0=Not Operated, 1=Operated)          P143xxxD, E, G"]
[null,"0x0008,0x0000","Relay 20 (0=Not Operated, 1=Operated)          P143xxxD, E, G"]
[null,"0x0010,0x0000","Relay 21 (0=Not Operated, 1=Operated)          P143xxxD, E, G"]
[null,"0x0020,0x0000","Relay 22 (0=Not Operated, 1=Operated)          P143xxxD, E, G"]
[null,"0x0040,0x0000","Relay 23 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x0080,0x0000","Relay 24 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x0100,0x0000","Relay 25 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x0200,0x0000","Relay 26 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x0400,0x0000","Relay 27 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x0800,0x0000","Relay 28 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x1000,0x0000","Relay 29 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x2000,0x0000","Relay 30 (0=Not Operated, 1=Operated)          P143xxxG"]
[null,"0x4000,0x0000","Relay 31 (0=Not Operated, 1=Operated)          Not Used"]
[null,"0x8000,0x0000","Relay 32 (0=Not Operated, 1=Operated)          Not Used"]
["G10",null,"SIGNED FIXED POINT NUMBER - 1 decimal place"]
[null,null,"-3276.8 to 3276.7 e.g. display of temperature"]
["G11",null,"YES/NO"]
[null,0,"No"]
[null,1,"Yes"]
["G12a",null,"TIME AND DATE (4 REGISTERS)  -  Standard IEC format (See G238 definition)"]
[null,null,"Note: Register masks given in terms of Upper byte then Lower byte"]
[null,"0xFFFF","First Register -  Millisec MSB (Mask: 0xFF)","- Combined Mask: 0x0F"]
[null,null,"Millisec LSB (Mask: 0xFF)","- Combined Mask: 0xFF"]
[null,"0x9FBF","Second Register - Summertime (Mask: 0x80) and hours  ","(Mask: 0x1F) - Combined Mask: 0x9F"]
[null,null,"Validity (Mask: 0x80) and minutes ","(Mask: 0x3F) - Combined Mask: 0xBF"]
[null,"0x0FFF","Third Register - Months (Mask: 0x0F)  ","- Combined Mask: 0x0F"]
[null,null,"Day of Week (Mask: 0xE0) and Day of Month (Mask: 0x1F)","- Combined Mask: 0xFF"]
[null,"0x007F","Fourth Register - Dummy byte (Mask: 0x00)","- Combined Mask: 0x00"]
[null,null,"Years (Mask: 0x7F)","- Combined Mask: 0x7F"]
["G12b",null,"TIME AND DATE (4 REGISTERS)  -  Reverse IEC format (See G238 definition)"]
[null,null,"Note: Register masks given in terms of Upper byte then Lower byte"]
[null,"0x007F","First Register - Dummy byte (Mask: 0x00)","- Combined Mask: 0x00"]
[null,null,"Years (Mask: 0x7F)","- Combined Mask: 0x7F"]
[null,"0x0FFF","Second Register - Months (Mask: 0x0F)","- Combined Mask: 0x0F"]
[null,null,"Day of Week (Mask: 0xE0) and Day of Month (Mask: 0x1F)","- Combined Mask: 0x0F"]
[null,"0x9FBF","Third Register - Summertime (Mask: 0x80) and hours","(Mask: 0x1F) - Combined Mask: 0x9F"]
[null,null,"Validity (Mask: 0x80) and minutes","(Mask: 0x3F) - Combined Mask: 0xBF"]
[null,"0xFFFF","Fourth Register - Millisec MSB (Mask: 0xFF)                                            ","- Combined Mask: 0xFF"]
[null,null,"Millisec LSB (Mask: 0xFF)","- Combined Mask: 0xFF"]
["G13",null,"EVENT RECORD TYPE"]
[null,0,"Latched alarm active"]
[null,1,"Latched alarm inactive"]
[null,2,"Self reset alarm active"]
[null,3,"Self reset alarm inactive"]
[null,4,"Relay event"]
[null,5,"Opto event"]
[null,6,"Protection event"]
[null,7,"Platform event"]
[null,8,"Fault logged event"]
[null,9,"Maintenance record logged event"]
["G14",null,"I> Function Link","(P142/P143/P144/P145 only)"]
[null,"Bit 0","VTS Blocks I>1  ","(P142/P143/P144/P145 only)"]
[null,"Bit 1","VTS Blocks I>2   ","(P142/P143/P144/P145 only)"]
[null,"Bit 2","VTS Blocks I>3","(P142/P143/P144/P145 only)"]
[null,"Bit 3","VTS Blocks I>4","(P142/P143/P144/P145 only)"]
[null,"Bit 4","AR Blocks I>3","(P142/P143/P144/P145 only)"]
[null,"Bit 5","AR Blocks I>4","(P142/P143/P144/P145 only)"]
[null,"Bit 6","2H Blocks I>1","(P142/P143/P144/P145 only)"]
[null,"Bit 7","2H Blocks I>2  ","(P142/P143/P144/P145 only)"]
[null,"Bit 8","2H Blocks I>3  ","(P142/P143/P144/P145 only)"]
[null,"Bit 9","2H Blocks I>4","(P142/P143/P144/P145 only)"]
[null,"Bit 10","2H 1PH Block","(P142/P143/P144/P145 only)"]
[null,"Bit 11","Not Used"]
["G14","(P141 only)","I> Function Link","(P141 only)"]
[null,"Bit 0","VTS Blocks I>1    ","(P141 only)"]
[null,"Bit 1","VTS Blocks I>2","(P141 only)"]
[null,"Bit 2","VTS Blocks I>3","(P141 only)"]
[null,"Bit 3","VTS Blocks I>4","(P141 only)"]
[null,"Bit 4","2H Blocks I>1","(P141 only)"]
[null,"Bit 5","2H Blocks I>2","(P141 only)"]
[null,"Bit 6","2H Blocks I>3   ","(P141 only)"]
[null,"Bit 7","2H Blocks I>4","(P141 only)"]
[null,"Bit 8","2H 1PH Block","(P141 only)"]
[null,"Bit 9","Not Used","(P141 only)"]
[null,"Bit 10","Not Used","(P141 only)"]
[null,"Bit 11","Not Used"]
["G15",null,"DISTURBANCE RECORD INDEX STATUS"]
[null,0,"No Record"]
[null,1,"Un-extracted"]
[null,2,"Extracted"]
["G16",null,"FAULTED PHASE"]
[null,"0x0001","Start A"]
[null,"0x0002","Start B"]
[null,"0x0004","Start C"]
[null,"0x0008","Start N"]
[null,"0x0010","Trip A"]
[null,"0x0020","Trip B"]
[null,"0x0040","Trip C"]
[null,"0x0080","Trip N"]
["G17",null,"IRIG-B STATUS"]
[null,0,"Card not fitted"]
[null,1,"Card failed"]
[null,2,"Signal Healthy"]
[null,3,"No Signal"]
["G18",null,"Record Selection Command Register"]
[null,"0x0000","No Operation"]
[null,"0x0001","Select Next Event"]
[null,"0x0002","Accept Event"]
[null,"0x0004","Select Next Disturbance Record"]
[null,"0x0008","Accept Disturbance Record"]
[null,"0x0010","Select Next Disturbance Record Page"]
["G19",null,"LANGUAGE - UK/FR/DE/ES"]
[null,0,"English"]
[null,1,"Francais"]
[null,2,"Deutsch"]
[null,3,"Espanol"]
["G19",null,"LANGUAGE - UK/FR/DE/RU"]
[null,0,"English"]
[null,1,"Francais"]
[null,2,"Deutsch"]
[null,3,"Russian"]
["G19",null,"LANGUAGE - UK/FR/CN"]
[null,0,"English"]
[null,1,"Francais"]
[null,2,"Chinese - via HMI only - not front or rear port"]
["G20","(Second reg, First Reg)","PASSWORD (2 REGISTERS)"]
[null,"0x0000, 0x00FF","First password character"]
[null,"0x0000, 0xFF00","Second password character"]
[null,"0x00FF, 0x0000","Third password character"]
[null,"0xFF00, 0x0000","Fourth password character"]
[null,null,"NOTE THAT WHEN REGISTERS OF THIS TYPE ARE READ THE SLAVE WILL "]
[null,null,"ALWAYS INDICATE AN \"*\" IN EACH CHARACTER POSITION TO PRESERVE "]
[null,null,"THE PASSWORD SECURITY."]
["G21",null,"IEC870 Interface"]
[null,0,"RS485"]
[null,1,"Fibre Optic"]
["G22",null,"PASSWORD CONTROL ACCESS LEVEL"]
[null,0,"Level 0 - Passwords required for levels 1 & 2"]
[null,1,"Level 1 - Password required for level 2"]
[null,2,"Level 2 - No passwords required"]
["G23",null,"Voltage Curve selection"]
[null,0,"Disabled"]
[null,1,"DT"]
[null,2,"IDMT"]
["G24","2 REGISTERS","UNSIGNED LONG VALUE, 3 DECIMAL PLACES"]
[null,null,"High order word of long stored in 1st register"]
[null,null,"Low order word of long stored in 2nd register"]
[null,null,"Example 123456.789 stored as 123456789"]
["G25","1 REGISTER","UNSIGNED VALUE, 3 DECIMAL PLACES"]
[null,null,"Example 50.050 stored as 50050"]
["G26",null,"MODBUS Status Register"]
[null,"VALUE/BIT MASK","RELAY STATUS"]
[null,"0x0001","In Service Status (1 = In Service/0= Out Of Service)"]
[null,"0x0002","Minor Self Test Failure (1 = Failure/0 = No failure)"]
[null,"0x0004","New autoextraction event available (1 = Available/0 = Not Available)"]
[null,"0x0008","Time Synchronisation (=1 after MODBUS time synch.  Resets to 0 after 5 minutes \nunless it is time synched again.  Other time sources do not affect this bit). "]
[null,"0x0010","New auto extraction disturbance record available (1 = Available/0 = Not available)"]
[null,"0x0020","Fault (Not used - always 0)."]
[null,"0x0040","Trip LED status (1 = LED on, 0 = LED off)."]
[null,"0x0080","Alarm status summary (logical OR of all alarm status bits)."]
[null,"0x0100","Unused"]
[null,"0x0200","Unused"]
[null,"0x0400","Unused"]
[null,"0x0800","Unused"]
[null,"0x1000","Unused"]
[null,"0x2000","Unused"]
[null,"0x4000","Unused"]
[null,"0x8000","Unused"]
["G27","2 REGISTERS","UNSIGNED LONG VALUE"]
[null,null,"High order word of long stored in 1st register"]
[null,null,"Low order word of long stored in 2nd register"]
[null,null,"Example 123456 stored as 123456"]
["G28","1 REGISTER","SIGNED VALUE POWER & WATT-HOURS"]
[null,null,"Power = (Secondary power/CT secondary) * (110/VT secondary)"]
["G29","3 REGISTER","POWER MULTIPLER"]
[null,null,"All power measurments use a signed value of type G28 and a 2 register unsigned long multiplier of type G27 (G29 = G28 * G27) "]
[null,null,"Value = Real Value*110/(CTsecondary*VTsecondary)"]
[null,null,"For Primary Power Multipler = CTprimary * VTprimary/110"]
[null,null,"For Secondary Power Multipler = CTsecondary * VTsecondary/110"]
["G30","1 REGISTER","SIGNED VALUE, 2 DECIMAL PLACES"]
[null,null,"i.e. Divide the returned value by 100."]
["G31-1",null,"ANALOGUE CHANNEL ASSIGNMENT SELECTOR (P141 / P142)"]
[null,0,"VA"]
[null,1,"VB"]
[null,2,"VC"]
[null,3,"IA"]
[null,4,"IB"]
[null,5,"IC"]
[null,6,"IN"]
[null,7,"IN Sensitive"]
[null,8,"Frequency"]
[null,9,"Unused"]
["G31-2",null,"ANALOGUE CHANNEL ASSIGNMENT SELECTOR (P143)"]
[null,0,"VA"]
[null,1,"VB"]
[null,2,"VC"]
[null,3,"V Checksync"]
[null,4,"IA"]
[null,5,"IB"]
[null,6,"IC"]
[null,7,"IN"]
[null,8,"IN Sensitive"]
[null,9,"Frequency"]
[null,10,"Unused"]
["G31-3",null,"ANALOGUE CHANNEL ASSIGNMENT SELECTOR (P144)"]
[null,0,"VA"]
[null,1,"VB"]
[null,2,"VC"]
[null,3,"VN"]
[null,4,"IA"]
[null,5,"IB"]
[null,6,"IC"]
[null,7,"IN"]
[null,8,"IN Sensitive"]
[null,9,"Frequency"]
[null,10,"Unused"]
["G32",null,"DIGITAL CHANNEL ASSIGNMENT SELECTOR (see DDB)"]
[null,0,"Not used"]
[null,null,"Number of  Output Relays - depends on model"]
[null,null,"Number of Opto Inputs - depends on model"]
[null,null,"8 LEDs"]
[null,null,"PFSO (max is defined by the number of PFSO signals in each model)"]
["G33",null,"RECORDER TRIGGERING (2 REGISTERS, 32 BINARY FLAGS)"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Digital Channel 1 Bit 0  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0002","Digital Channel 1 Bit 1  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0004","Digital Channel 1 Bit 2  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0008","Digital Channel 1 Bit 3  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0010","Digital Channel 1 Bit 4  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0020","Digital Channel 1 Bit 5  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0040","Digital Channel 1 Bit 6  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0080","Digital Channel 1 Bit 7  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0100","Digital Channel 1 Bit 8  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0200","Digital Channel 1 Bit 9  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0400","Digital Channel 1 Bit 10  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x0800","Digital Channel 1 Bit 11  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x1000","Digital Channel 1 Bit 12  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x2000","Digital Channel 1 Bit 13  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x4000","Digital Channel 1 Bit 14  (0 = No Trigger, 1= Trigger)"]
[null,"0x0000,0x8000","Digital Channel 1 Bit 15  (0 = No Trigger, 1= Trigger)"]
[null,"0x0001,0x0000","Digital Channel 2 Bit 0  (0 = No Trigger, 1= Trigger)"]
[null,"0x0002,0x0000","Digital Channel 2 Bit 1  (0 = No Trigger, 1= Trigger)"]
[null,"0x0004,0x0000","Digital Channel 2 Bit 2  (0 = No Trigger, 1= Trigger)"]
[null,"0x0008,0x0000","Digital Channel 2 Bit 3  (0 = No Trigger, 1= Trigger)"]
[null,"0x0010,0x0000","Digital Channel 2 Bit 4  (0 = No Trigger, 1= Trigger)"]
[null,"0x0020,0x0000","Digital Channel 2 Bit 5  (0 = No Trigger, 1= Trigger)"]
[null,"0x0040,0x0000","Digital Channel 2 Bit 6  (0 = No Trigger, 1= Trigger)"]
[null,"0x0080,0x0000","Digital Channel 2 Bit 7  (0 = No Trigger, 1= Trigger)"]
[null,"0x0100,0x0000","Digital Channel 2 Bit 8  (0 = No Trigger, 1= Trigger)"]
[null,"0x0200,0x0000","Digital Channel 2 Bit 9  (0 = No Trigger, 1= Trigger)"]
[null,"0x0400,0x0000","Digital Channel 2 Bit 10  (0 = No Trigger, 1= Trigger)"]
[null,"0x0800,0x0000","Digital Channel 2 Bit 11  (0 = No Trigger, 1= Trigger)"]
[null,"0x1000,0x0000","Digital Channel 2 Bit 12  (0 = No Trigger, 1= Trigger)"]
[null,"0x2000,0x0000","Digital Channel 2 Bit 13  (0 = No Trigger, 1= Trigger)"]
[null,"0x4000,0x0000","Digital Channel 2 Bit 14  (0 = No Trigger, 1= Trigger)"]
[null,"0x8000,0x0000","Digital Channel 2 Bit 15  (0 = No Trigger, 1= Trigger)"]
[]
["G34",null,"TRIGGER MODE"]
[null,0,"Single"]
[null,1,"Extended"]
["G35",null,"Numeric Setting (as G2 but 2 registers)"]
[null,null,"Number of steps from minimum value expressed as 2 register 32 bit unsigned int"]
["G36",null,"AUTORECLOSE TEST"]
[null,0,"No Operation"]
[null,1,"3 Pole Test"]
["G37",null,"ENABLED/DISABLED"]
[null,0,"Disabled"]
[null,1,"Enabled"]
["G38c",null,"COMMUNICATION BAUD RATE (Courier - EIA485)"]
[null,0,"9600 bits/s"]
[null,1,"19200 bits/s"]
[null,2,"38400 bits/s"]
["G38m",null,"COMMUNICATION BAUD RATE (MODBUS)"]
[null,0,"9600 bits/s"]
[null,1,"19200 bits/s"]
[null,2,"38400 bits/s"]
["G38v",null,"COMMUNICATION BAUD RATE (IEC 60870)"]
[null,0,"9600 bits/s"]
[null,1,"19200 bits/s"]
["G38d",null,"COMMUNICATION BAUD RATE (DNP 3.0)"]
[null,0,"1200 bits/s"]
[null,1,"2400 bits/s"]
[null,2,"4800 bits/s"]
[null,3,"9600 bits/s"]
[null,4,"19200 bits/s"]
[null,5,"38400 bits/s"]
["G39",null,"COMMUNICATIONS PARITY"]
[null,0,"Odd"]
[null,1,"Even"]
[null,2,"None"]
["G40",null,"CHECK SYNC INPUT SELECTION - P143"]
[null,0,"A-N"]
[null,1,"B-N"]
[null,2,"C-N"]
[null,3,"A-B"]
[null,4,"B-C"]
[null,5,"C-A"]
["G41",null,"CHECK SYNC VOLTAGE BLOCKING - P143"]
[null,0,"None"]
[null,1,"V<"]
[null,2,"V>"]
[null,3,"Vdiff>"]
[null,4,"V< and V>"]
[null,5,"V< and Vdiff>"]
[null,6,"V> and Vdiff>"]
[null,7,"V< V> and Vdiff>"]
["G42",null,"CHECK SYNC SLIP CONTROL (STAGE 1) - P143"]
[null,0,"None"]
[null,1,"Timer"]
[null,2,"Frequency"]
[null,3,"Both"]
["G43",null,"IDMT CURVE TYPE"]
[null,0,"Disabled"]
[null,1,"DT"]
[null,2,"IEC S Inverse"]
[null,3,"IEC V Inverse"]
[null,4,"IEC E Inverse"]
[null,5,"UK LT Inverse"]
[null,6,"IEEE M Inverse"]
[null,7,"IEEE V Inverse"]
[null,8,"IEEE E Inverse"]
[null,9,"US Inverse"]
[null,10,"US ST Inverse"]
["G44",null,"DIRECTION"]
[null,0,"Non-Directional"]
[null,1,"Directional Fwd"]
[null,2,"Directional Rev"]
["G45",null,"VTS BLOCK"]
[null,0,"Block"]
[null,1,"Non-Directional"]
["G46",null,"POLARISATION"]
[null,0,"Zero Sequence"]
[null,1,"Neg Sequence"]
["G47",null,"MEASURING MODE"]
[null,0,"Phase-Phase"]
[null,1,"Phase-Neutral"]
["G48",null,"OPERATION MODE"]
[null,0,"Any Phase"]
[null,1,"Three Phase"]
["G49",null,"VN or IN INPUT"]
[null,0,"Measured"]
[null,1,"Derived"]
["G50",null,"RTD SELECT   Not used in P140"]
[null,"0x0001","RTD Input #1"]
[null,"0x0002","RTD Input #2"]
[null,"0x0004","RTD Input #3"]
[null,"0x0008","RTD Input #4"]
[null,"0x0010","RTD Input #5"]
[null,"0x0020","RTD Input #6"]
[null,"0x0040","RTD Input #7"]
[null,"0x0080","RTD Input #8"]
[null,"0x0100","RTD Input #9"]
[null,"0x0200","RTD Input #10"]
["G51",null,"FAULT LOCATION"]
[null,0,"Distance"]
[null,1,"Ohms"]
[null,2,"% of Line"]
["G52",null,"DEFAULT DISPLAY"]
[null,0,"3Ph + N Current"]
[null,1,"3Ph Voltage"]
[null,2,"Power"]
[null,3,"Date and Time"]
[null,4,"Description"]
[null,5,"Plant Reference"]
[null,6,"Frequency"]
[null,7,"Access Level"]
["G53",null,"SELECT FACTORY DEFAULTS"]
[null,0,"No Operation"]
[null,1,"All Settings"]
[null,2,"Setting Group 1"]
[null,3,"Setting Group 2"]
[null,4,"Setting Group 3"]
[null,5,"Setting Group 4"]
["G54",null,"SELECT PRIMARY SECONDARY MEASUREMENTS"]
[null,0,"Primary"]
[null,1,"Secondary"]
["G55",null,"CIRCUIT BREAKER CONTROL"]
[null,0,"No Operation"]
[null,1,"Trip"]
[null,2,"Close"]
["G56",null,"PHASE MEASUREMENT REFERENCE"]
[null,0,"VA"]
[null,1,"VB"]
[null,2,"VC"]
[null,3,"IA"]
[null,4,"IB"]
[null,5,"IC"]
["G57",null,"Data Transfer Domain"]
[null,0,"PSL Settings"]
[null,1,"PSL Configuration"]
["G58",null,"SEF/REF SELECTION"]
[null,0,"SEF"]
[null,1,"SEF cos(PHI)"]
[null,2,"SEF sin(PHI)"]
[null,3,"Wattmetric"]
[null,4,"Hi Z REF                                                                    (Not used in P144)","(Not used in P144)"]
[null,5,"Lo Z REF                                                                   (Not used in P144)","(Not used in P144)"]
[null,6,"Lo Z REF+SEF                                                           (Not used in P144)","(Not used in P144)"]
[null,7,"Lo Z REF+Wattmet                                                    (Not used in P144)","(Not used in P144)"]
["G59",null,"BATTERY STATUS"]
[null,0,"Dead"]
[null,1,"Healthy"]
["G60",null,"IDMT CURVE TYPE"]
[null,0,"DT"]
[null,1,"Inverse"]
["G61",null,"ACTIVE GROUP CONTROL"]
[null,0,"Select via Menu"]
[null,1,"Select via Opto"]
["G62",null,"SAVE AS"]
[null,0,"No Operation"]
[null,1,"Save"]
[null,2,"Abort"]
["G63","(P142/P143/P144/P145 only)","IN> Function Link","(P142/P143/P144/P145 only)"]
[null,"Bit 0","VTS Blocks IN>1","(P142/P143/P144/P145 only)"]
[null,"Bit 1","VTS Blocks IN>2","(P142/P143/P144/P145 only)"]
[null,"Bit 2","VTS Blocks IN>3","(P142/P143/P144/P145 only)"]
[null,"Bit 3","VTS Blocks IN>4","(P142/P143/P144/P145 only)"]
[null,"Bit 4","AR Blocks IN>3","(P142/P143/P144/P145 only)"]
[null,"Bit 5","AR Blocks IN>4","(P142/P143/P144/P145 only)"]
[null,"Bit 6","2H Blocks IN>1","(P142/P143/P144/P145 only)"]
[null,"Bit 7","2H Blocks IN>2","(P142/P143/P144/P145 only)"]
[null,"Bit 8","2H Blocks IN>3","(P142/P143/P144/P145 only)"]
[null,"Bit 9","2H Blocks IN>4","(P142/P143/P144/P145 only)"]
[null,"Bit 10","Not Used","(P142/P143/P144/P145 only)"]
[null,"Bit 11","Not Used","(P142/P143/P144/P145 only)"]
["G63","(P141 only)","IN> Function Link","(P141 only)"]
[null,"Bit 0","VTS Blocks IN>1","(P141 only)"]
[null,"Bit 1","VTS Blocks IN>2","(P141 only)"]
[null,"Bit 2","VTS Blocks IN>3","(P141 only)"]
[null,"Bit 3","VTS Blocks IN>4","(P141 only)"]
[null,"Bit 4","2H Blocks IN>1","(P141 only)"]
[null,"Bit 5","2H Blocks IN>2","(P141 only)"]
[null,"Bit 6","2H Blocks IN>3","(P141 only)"]
[null,"Bit 7","2H Blocks IN>4","(P141 only)"]
[null,"Bit 8","Not Used","(P141 only)"]
[null,"Bit 9","Not Used","(P141 only)"]
[null,"Bit 10","Not Used"]
[null,"Bit 11","Not Used"]
["G64","(P142/P143/P144/P145 only)","ISEF> Func Link","(P142/P143/P144/P145 only)"]
[null,"Bit 0","VTS Blks ISEF>1","(P142/P143/P144/P145 only)"]
[null,"Bit 1","VTS Blks ISEF>2","(P142/P143/P144/P145 only)"]
[null,"Bit 2","VTS Blks ISEF>3","(P142/P143/P144/P145 only)"]
[null,"Bit 3","VTS Blks ISEF>4","(P142/P143/P144/P145 only)"]
[null,"Bit 4","AR Blks ISEF>3","(P142/P143/P144/P145 only)"]
[null,"Bit 5","AR Blks ISEF>4","(P142/P143/P144/P145 only)"]
[null,"Bit 6","2H Blocks ISEF>1","(P142/P143/P144/P145 only)"]
[null,"Bit 7","2H Blocks ISEF>2","(P142/P143/P144/P145 only)"]
[null,"Bit 8","2H Blocks ISEF>3","(P142/P143/P144/P145 only)"]
[null,"Bit 9","2H Blocks ISEF>4","(P142/P143/P144/P145 only)"]
[null,"Bit 10","Not Used"]
[null,"Bit 11","Not Used"]
["G64","(P141 only)","ISEF> Func Link","(P141 only)"]
[null,"Bit 0","VTS Blks ISEF>1","(P141 only)"]
[null,"Bit 1","VTS Blks ISEF>2","(P141 only)"]
[null,"Bit 2","VTS Blks ISEF>3","(P141 only)"]
[null,"Bit 3","VTS Blks ISEF>4","(P141 only)"]
[null,"Bit 4","2H Blocks ISEF>1","(P141 only)"]
[null,"Bit 5","2H Blocks ISEF>2","(P141 only)"]
[null,"Bit 6","2H Blocks ISEF>3","(P141 only)"]
[null,"Bit 7","2H Blocks ISEF>4","(P141 only)"]
[null,"Bit 8","Not Used","(P141 only)"]
[null,"Bit 9","Not Used","(P141 only)"]
[null,"Bit 10","Not Used"]
[null,"Bit 11","Not Used"]
["G65",null,"F< Function Link"]
[null,"Bit 0","F<1 Poledead Blk"]
[null,"Bit 1","F<2 Poledead Blk"]
[null,"Bit 2","F<3 Poledead Blk"]
[null,"Bit 3","F<4 Poledead Blk"]
[null,"Bit 4","Not Used"]
[null,"Bit 5","Not Used"]
[null,"Bit 6","Not Used"]
[null,"Bit 7","Not Used"]
["G66",null,"MESSAGE FORMAT"]
[null,0,"No Trigger"]
[null,1,"Trigger L/H"]
[null,2,"Trigger H/L"]
["G67",null,"Thermal Overload Characteristic"]
[null,0,"Disabled"]
[null,1,"Single"]
[null,2,"Dual"]
["G68",null,"CB Fail Reset Options"]
[null,0,"I< Only"]
[null,1,"CB Open & I<"]
[null,2,"Prot Reset & I<"]
["G69",null,"VTS RESET MODE"]
[null,0,"Manual"]
[null,1,"Auto"]
["G70",null,"AUTORECLOSE MODE"]
[null,0,"Command Mode"]
[null,1,"Opto Set Mode"]
[null,2,"User Set Mode"]
[null,3,"Pulse Set Mode"]
["G71",null,"PROTOCOL"]
[null,0,"Courier"]
[null,1,"IEC60870-5-103"]
[null,2,"Modbus"]
[null,3,"DNP 3.0"]
["G72",null,"START DEAD TIME"]
[null,0,"Protection Reset"]
[null,1,"CB Trips"]
["G73",null,"Reclaim Time - tReclaim Extend"]
[null,0,"On Prot Start"]
[null,1,"No Operation"]
["G74",null,"RESET LOCKOUT"]
[null,0,"User Interface"]
[null,1,"Select NonAuto"]
["G75",null,"Auto-Reclose after Control Close"]
[null,0,"Enabled"]
[null,1,"Inhibited"]
["G76",null,"TRANSFER MODE"]
[null,0,"Prepare Rx"]
[null,1,"Complete Rx"]
[null,2,"Prepare Tx"]
[null,3,"Complete Tx"]
[null,4,"Rx Prepared"]
[null,5,"Tx Prepared"]
[null,6,"OK"]
[null,7,"Error"]
["G77",null,"Auto-Reclose"]
[null,0,"Out of Service"]
[null,1,"In Service"]
["G78",null,"AR Mode"]
[null,0,"No Operation"]
[null,1,"Auto"]
[null,2,"Non Auto"]
["G79",null,"Custom Settings"]
[null,0,"Disabled"]
[null,1,"Basic"]
[null,2,"Complete"]
["G80",null,"Visible/Invisible"]
[null,0,"Invisible"]
[null,1,"Visible"]
["G81",null,"Reset Lockout by"]
[null,0,"User Interface"]
[null,1,"CB Close"]
["G82",null,"A/R Protection blocking"]
[null,0,"No Block"]
[null,1,"Block Inst Prot"]
["G83",null,"A/R Status"]
[null,0,"Auto Mode"]
[null,1,"Non-auto Mode"]
[null,2,"Live Line"]
["G84","MODBUS value+bit pos","Started Elements(Product Specific)"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","General Start"]
[null,"0x0000,0x0002","Start I>1"]
[null,"0x0000,0x0004","Start I>2"]
[null,"0x0000,0x0008","Start I>3"]
[null,"0x0000,0x0010","Start I>4"]
[null,"0x0000,0x0020","Start BrokenLine"]
[null,"0x0000,0x0040","Start IN1>1"]
[null,"0x0000,0x0080","Start IN1>2"]
[null,"0x0000,0x0100","Start IN1>3"]
[null,"0x0000,0x0200","Start IN1>4"]
[null,"0x0000,0x0400","Start IN2>1"]
[null,"0x0000,0x0800","Start IN2>2"]
[null,"0x0000,0x1000","Start IN2>3"]
[null,"0x0000,0x2000","Start IN2>4"]
[null,"0x0000,0x4000","Start ISEF>1"]
[null,"0x0000,0x8000","Start ISEF>2"]
[null,"0x0001,0x0000","Start ISEF>3"]
[null,"0x0002,0x0000","Start ISEF>4"]
[null,"0x0004,0x0000","Start NVD VN>1"]
[null,"0x0008,0x0000","Start NVD VN>2"]
[null,"0x0010,0x0000","Thermal Alarm"]
[null,"0x0020,0x0000","Start V2>"]
[null,"0x0040,0x0000","Start V<1"]
[null,"0x0080,0x0000","Start V<2"]
[null,"0x0100,0x0000","Start V< A/AB"]
[null,"0x0200,0x0000","Start V< B/BC"]
[null,"0x0400,0x0000","Start V< C/CA"]
[null,"0x0800,0x0000","Start V>1"]
[null,"0x1000,0x0000","Start V>2"]
[null,"0x2000,0x0000","Start V> A/AB"]
[null,"0x4000,0x0000","Start V> B/BC"]
[null,"0x8000,0x0000","Start V> C/CA"]
["G85","MODBUS value+bit pos","Tripped Elements(1)(Product Specific)"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Any Trip"]
[null,"0x0000,0x0002","Trip I>1"]
[null,"0x0000,0x0004","Trip I>2"]
[null,"0x0000,0x0008","Trip I>3"]
[null,"0x0000,0x0010","Trip I>4"]
[null,"0x0000,0x0020","                                                                                                   (was Trip I2>)","(was Trip I2>)"]
[null,"0x0000,0x0040","Trip Broken Line"]
[null,"0x0000,0x0080","Trip IN1>1"]
[null,"0x0000,0x0100","Trip IN1>2"]
[null,"0x0000,0x0200","Trip IN1>3"]
[null,"0x0000,0x0400","Trip IN1>4"]
[null,"0x0000,0x0800","Trip IN2>1"]
[null,"0x0000,0x1000","Trip IN2>2"]
[null,"0x0000,0x2000","Trip IN2>3"]
[null,"0x0000,0x4000","Trip IN2>4"]
[null,"0x0000,0x8000","Trip ISEF>1"]
[null,"0x0001,0x0000","Trip ISEF>2"]
[null,"0x0002,0x0000","Trip ISEF>3"]
[null,"0x0004,0x0000","Trip ISEF>4"]
[null,"0x0008,0x0000","Trip IREF>"]
[null,"0x0010,0x0000","Trip NVD VN>1"]
[null,"0x0020,0x0000","Trip NVD VN>2"]
[null,"0x0040,0x0000","Trip Thermal"]
[null,"0x0080,0x0000","Trip V2>"]
[null,"0x0100,0x0000"]
[null,"0x0200,0x0000"]
[null,"0x0400,0x0000"]
[null,"0x0800,0x0000"]
[null,"0x1000,0x0000"]
[null,"0x2000,0x0000"]
[null,"0x4000,0x0000"]
[null,"0x8000,0x0000"]
["G86","Bit Description","Tripped Elements(2) (Product Specific)"]
[null,"(Second reg, First Reg)(Courier and IEC870 Bit Position)"]
[null,"0x0000,0x0001","Trip V<1 "]
[null,"0x0000,0x0002","Trip V<2"]
[null,"0x0000,0x0004","Trip V< A/AB "]
[null,"0x0000,0x0008","Trip V< B/BC"]
[null,"0x0000,0x0010","Trip V< C/CA"]
[null,"0x0000,0x0020","Trip V>1"]
[null,"0x0000,0x0040","Trip V>2"]
[null,"0x0000,0x0080","Trip V> A/AB "]
[null,"0x0000,0x0100","Trip V> B/BC"]
[null,"0x0000,0x0200","Trip V> C/CA"]
[null,"0x0000,0x0400","Trip F<1"]
[null,"0x0000,0x0800","Trip F<2"]
[null,"0x0000,0x1000","Trip F<3"]
[null,"0x0000,0x2000","Trip F<4"]
[null,"0x0000,0x4000","Trip F>1"]
[null,"0x0000,0x8000","Trip F>2"]
[null,"0x0001,0x0000","Trip YN>"]
[null,"0x0002,0x0000","Trip GN>"]
[null,"0x0004,0x0000","Trip BN>"]
[null,"0x0008,0x0000","Trip df/dt>1"]
[null,"0x0010,0x0000","Trip df/dt>2"]
[null,"0x0020,0x0000","Trip df/dt>3"]
[null,"0x0040,0x0000","Trip df/dt>4"]
[null,"0x0080,0x0000","Trip I2>1"]
[null,"0x0100,0x0000","Trip I2>2"]
[null,"0x0200,0x0000","Trip I2>3"]
[null,"0x0400,0x0000","Trip I2>4"]
[null,"0x0800,0x0000"]
[null,"0x1000,0x0000"]
[null,"0x2000,0x0000"]
[null,"0x4000,0x0000"]
[null,"0x8000,0x0000"]
["G87","Bit Description","Fault Alarms (Product Specific)"]
[null,"(Second reg, First Reg)(Courier and IEC870 Bit Position)"]
[null,"0x0000,0x0001","CB Fail 1"]
[null,"0x0000,0x0002","CB Fail 2"]
[null,"0x0000,0x0004","VTS"]
[null,"0x0000,0x0008","CTS"]
[null,"0x0000,0x0010","VCO"]
[null,"0x0000,0x0020","CLP"]
[null,"0x0000,0x0040","AR Trip 1","P142/P143/P144 only"]
[null,"0x0000,0x0080","AR Trip 2","P142/P143/P144 only"]
[null,"0x0000,0x0100","AR Trip 3","P142/P143/P144 only"]
[null,"0x0000,0x0200","AR Trip 4","P142/P143/P144 only"]
[null,"0x0000,0x0400","AR Trip 5","P142/P143/P144 only"]
[null,"0x0000,0x0800"]
[null,"0x0000,0x1000"]
[null,"0x0000,0x2000"]
[null,"0x0000,0x4000"]
[null,"0x0000,0x8000"]
[null,"0x0001,0x0000"]
[null,"0x0002,0x0000"]
[null,"0x0004,0x0000"]
[null,"0x0008,0x0000"]
[null,"0x0010,0x0000"]
[null,"0x0020,0x0000"]
[null,"0x0040,0x0000"]
[null,"0x0080,0x0000"]
[null,"0x0100,0x0000"]
[null,"0x0200,0x0000"]
[null,"0x0400,0x0000"]
[null,"0x0800,0x0000"]
[null,"0x1000,0x0000"]
[null,"0x2000,0x0000"]
[null,"0x4000,0x0000"]
[null,"0x8000,0x0000"]
["G88",null,"Alarms"]
[null,0,"Alarm Disabled"]
[null,1,"Alarm Enabled"]
["G89",null,"Main VT Location"]
[null,0,"Line"]
[null,1,"Bus"]
["G90",null,"Group Selection"]
[null,0,"Group 1"]
[null,1,"Group 2"]
[null,2,"Group 3"]
[null,3,"Group 4"]
["G91",null,"A/R Protection Blocking  - See also G82"]
[null,0,"No Block"]
[null,1,"Block Inst Prot"]
["G92",null,"Lockout"]
[null,0,"No Lockout"]
[null,1,"Lockout"]
["G93",null,"Commission Test - Contacts"]
[null,0,"No Operation"]
[null,1,"Apply Test"]
[null,2,"Remove Test"]
["G94",null,"Commission Test - LEDs"]
[null,0,"No Operation"]
[null,1,"Apply Test"]
["G95",null,"System Fn Links"]
[null,"Bit 0","Trip LED S/Reset (1 = enable self reset)"]
[null,"Bit 1","Not Used"]
[null,"Bit 2","Not Used"]
[null,"Bit 3","Not used"]
[null,"Bit 4","Not Used"]
[null,"Bit 5","Not Used"]
[null,"Bit 6","Not Used"]
[null,"Bit 7","Not Used"]
["G96-1","2nd register, 1st register","Product Alarm Status 1 (2 Registers)"]
["Bit 1","0x0000, 0x0001","Unused"]
["Bit 2","0x0000, 0x0002","Unused"]
["Bit 3","0x0000, 0x0004","SG-opto Invalid"]
["Bit 4","0x0000, 0x0008","Prot'n Disabled"]
["Bit 5","0x0000, 0x0010","F out of Range"]
["Bit 6","0x0000, 0x0020","VT Fail Alarm"]
["Bit 7","0x0000, 0x0040","CT Fail Alarm"]
["Bit 8","0x0000, 0x0080","CB Fail Alarm"]
["Bit 9","0x0000, 0x0100","I^ Maint Alarm"]
["Bit 10","0x0000, 0x0200","I^ Lockout Alarm"]
["Bit 11","0x0000, 0x0400","CB Ops Maint"]
["Bit 12","0x0000, 0x0800","CB Ops Lockout"]
["Bit 13","0x0000, 0x1000","CB Op Time Maint"]
["Bit 14","0x0000, 0x2000","CB Op Time Lock"]
["Bit 15","0x0000, 0x4000","Fault Freq Lock"]
["Bit 16","0x0000, 0x8000","CB Status Alarm"]
["Bit 17","0x0001, 0x0000","Man CB Trip Fail"]
["Bit 18","0x0002, 0x0000","Man CB Cls Fail"]
["Bit 19","0x0004, 0x0000","Man CB Unhealthy"]
["Bit 20","0x0008, 0x0000","Man No Checksync","(P143 only)"]
["Bit 21","0x0010, 0x0000","AR Lockout","(P142/P143/P144 only)"]
["Bit 22","0x0020, 0x0000","AR CB Unhealthy","(P142/P143/P144 only)"]
["Bit 23","0x0040, 0x0000","AR No Sys Check","(P143 only)"]
["Bit 24","0x0080, 0x0000","System Split","(P143 only)"]
["Bit 25","0x0100, 0x0000","SR User Alarm 1"]
["Bit 26","0x0200, 0x0000","SR User Alarm 2"]
["Bit 27","0x0400, 0x0000","SR User Alarm 3"]
["Bit 28","0x0800, 0x0000","SR User Alarm 4"]
["Bit 29","0x1000, 0x0000","SR User Alarm 5"]
["Bit 30","0x2000, 0x0000","SR User Alarm 6"]
["Bit 31","0x4000, 0x0000","SR User Alarm 7"]
["Bit 32","0x8000, 0x0000","SR User Alarm 8"]
["G96-2","2nd register, 1st register","Product Alarm Status 2 (2 Registers)"]
["Bit 1","0x0000, 0x0001","Unused"]
["Bit 2","0x0000, 0x0002","Unused"]
["Bit 3","0x0000, 0x0004","Unused"]
["Bit 4","0x0000, 0x0008","Unused"]
["Bit 5","0x0000, 0x0010","SR User Alarm 9"]
["Bit 6","0x0000, 0x0020","SR User Alarm 10"]
["Bit 7","0x0000, 0x0040","SR User Alarm 11"]
["Bit 8","0x0000, 0x0080","SR User Alarm 12"]
["Bit 9","0x0000, 0x0100","SR User Alarm 13"]
["Bit 10","0x0000, 0x0200","SR User Alarm 14"]
["Bit 11","0x0000, 0x0400","SR User Alarm 15"]
["Bit 12","0x0000, 0x0800","SR User Alarm 16"]
["Bit 13","0x0000, 0x1000","SR User Alarm 17"]
["Bit 14","0x0000, 0x2000","SR User Alarm 18"]
["Bit 15","0x0000, 0x4000","MR User Alarm 19"]
["Bit 16","0x0000, 0x8000","MR User Alarm 20"]
["Bit 17","0x0001, 0x0000","MR User Alarm 21"]
["Bit 18","0x0002, 0x0000","MR User Alarm 22"]
["Bit 19","0x0004, 0x0000","MR User Alarm 23"]
["Bit 20","0x0008, 0x0000","MR User Alarm 24"]
["Bit 21","0x0010, 0x0000","MR User Alarm 25"]
["Bit 22","0x0020, 0x0000","MR User Alarm 26"]
["Bit 23","0x0040, 0x0000","MR User Alarm 27"]
["Bit 24","0x0080, 0x0000","MR User Alarm 28"]
["Bit 25","0x0100, 0x0000","MR User Alarm 29"]
["Bit 26","0x0200, 0x0000","MR User Alarm 30"]
["Bit 27","0x0400, 0x0000","MR User Alarm 31"]
["Bit 28","0x0800, 0x0000","MR User Alarm 32"]
["Bit 29","0x1000, 0x0000","MR User Alarm 33"]
["Bit 30","0x2000, 0x0000","MR User Alarm 34"]
["Bit 31","0x4000, 0x0000","MR User Alarm 35"]
["Bit 32","0x8000, 0x0000","MR User Alarm 36"]
["G97",null,"Distance Unit"]
[null,0,"Kilometres"]
[null,1,"Miles"]
["G98",null,"Copy to"]
[null,0,"No Operation"]
[null,1,"Group 1"]
[null,2,"Group 2"]
[null,3,"Group 3"]
[null,4,"Group 4"]
["G99",null,"CB Control"]
[null,0,"Disabled"]
[null,1,"Local"]
[null,2,"Remote"]
[null,3,"Local+Remote"]
[null,4,"Opto"]
[null,5,"Opto+local"]
[null,6,"Opto+Remote"]
[null,7,"Opto+Rem+local"]
["G100",null,"VCO Options"]
[null,0,"Disabled"]
[null,1,"I>1"]
[null,2,"I>2"]
[null,3,"Both I>1 & I>2"]
["G101",null,"Prot-AR Interface I>/IN> Stages 1/2"]
[null,0,"No Action"]
[null,1,"Initiate Main AR"]
["G102",null,"Prot-AR Interface I>/IN> Stages 3/4  (Feeder Model 2 - SEF Stages 1/2/3/4)"]
[null,0,"No Action"]
[null,1,"Initiate Main AR"]
[null,2,"Block AR"]
["G103",null,"Prot-AR Interface ISEF> Stages 1/2 (& 3/4 Feeder Model 3)"]
[null,0,"No Action"]
[null,1,"Initiate Main AR"]
[null,2,"Initiate SEF AR"]
[null,3,"Block AR"]
["G104",null,"Prot-AR Interface ISEF> Stages 3/4"]
[null,0,"No Action"]
[null,1,"Block AR"]
["G106",null,"Cold Load Pickup"]
[null,0,"Block"]
[null,1,"Enable"]
["G107","MODBUS value+bit pos","Started Elements(Product Specific)"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Start F<1"]
[null,"0x0000,0x0002","Start F<2"]
[null,"0x0000,0x0004","Start F<3"]
[null,"0x0000,0x0008","Start F<4"]
[null,"0x0000,0x0010","Start F>1"]
[null,"0x0000,0x0020","Start F>2"]
[null,"0x0000,0x0040","Start YN>"]
[null,"0x0000,0x0080","Start GN>"]
[null,"0x0000,0x0100","Start BN>"]
[null,"0x0000,0x0200","Start df/dt>1"]
[null,"0x0000,0x0400","Start df/dt>2"]
[null,"0x0000,0x0800","Start df/dt>3"]
[null,"0x0000,0x1000","Start df/dt>4"]
[null,"0x0000,0x2000","Start I2>1"]
[null,"0x0000,0x4000","Start I2>2"]
[null,"0x0000,0x8000","Start I2>3"]
[null,"0x0001,0x0000","Start I2>4"]
[null,"0x0002,0x0000"]
[null,"0x0004,0x0000"]
[null,"0x0008,0x0000"]
[null,"0x0010,0x0000"]
[null,"0x0020,0x0000"]
[null,"0x0040,0x0000"]
[null,"0x0080,0x0000"]
[null,"0x0100,0x0000"]
[null,"0x0200,0x0000"]
[null,"0x0400,0x0000"]
[null,"0x0800,0x0000"]
[null,"0x1000,0x0000"]
[null,"0x2000,0x0000"]
[null,"0x4000,0x0000"]
[null,"0x8000,0x0000"]
["G118",null,"CB Control Logic Input Assignment"]
[null,0,"None"]
[null,1,"52A"]
[null,2,"52B"]
[null,3,"Both 52A and 52B"]
["G119",null,"TEST MODE"]
[null,0,"Disabled"]
[null,1,"Test Mode"]
[null,2,"Contacts Blocked"]
["G120",null,"CT input type"]
[null,0,"SEF CT"]
[null,1,"E/F CT"]
["G121",null,"DERIVED CT INPUT"]
[null,0,"IA"]
[null,1,"IB"]
[null,2,"IC"]
[null,3,"None"]
["G125","2 REGISTERS","IEEE FLOATING POINT FORMAT"]
[null,null,"Bit 31 = sign "]
[null,null,"Bits 30-23 = e7 - e0"]
[null,null,"Implicit 1."]
[null,null,"Bits 22-0 = f22 - f0"]
["G126",null,"AOP OPTIONS"]
[null,0,"Disabled"]
[null,1,"AOP1"]
[null,2,"AOP2"]
[null,3,"AOP3"]
["G128",null,"AOP3 MODE"]
[null,0,"Disabled"]
[null,1,"DTMode"]
[null,2,"ATMode"]
["G150",null,"POC CURVE TYPES"]
[null,0,"Disabled"]
[null,1,"DT","(DT)"]
[null,2,"IEC S Inverse","(TMS)"]
[null,3,"IEC V Inverse","(TMS)"]
[null,4,"IEC E Inverse","(TMS)"]
[null,5,"UK LT Inverse","(TMS)"]
[null,6,"UK Rectifier","(TMS)"]
[null,7,"RI","(K)"]
[null,8,"IEEE M Inverse","(TD)"]
[null,9,"IEEE V Inverse","(TD)"]
[null,10,"IEEE E Inverse","(TD)"]
[null,11,"US Inverse","(TD)"]
[null,12,"US ST Inverse","(TD)"]
["G151",null,"EF CURVE TYPES"]
[null,0,"Disabled"]
[null,1,"DT","(DT)"]
[null,2,"IEC S Inverse","(TMS)"]
[null,3,"IEC V Inverse","(TMS)"]
[null,4,"IEC E Inverse","(TMS)"]
[null,5,"UK LT Inverse","(TMS)"]
[null,6,"RI","(K)"]
[null,7,"IEEE M Inverse","(TD)"]
[null,8,"IEEE V Inverse","(TD)"]
[null,9,"IEEE E Inverse","(TD)"]
[null,10,"US Inverse","(TD)"]
[null,11,"US ST Inverse","(TD)"]
[null,12,"IDG"]
["G152",null,"SEF CURVE TYPES"]
[null,0,"Disabled"]
[null,1,"DT","(DT)"]
[null,2,"IEC S Inverse","(TMS)"]
[null,3,"IEC V Inverse","(TMS)"]
[null,4,"IEC E Inverse","(TMS)"]
[null,5,"UK LT Inverse","(TMS)"]
[null,6,"IEEE M Inverse","(TD)"]
[null,7,"IEEE V Inverse","(TD)"]
[null,8,"IEEE E Inverse","(TD)"]
[null,9,"US Inverse","(TD)"]
[null,10,"US ST Inverse","(TD)"]
[null,11,"IDG"]
[null,12,"EPATR B","(TMS)"]
["G156",null,"CHECK SYNC SLIP CONTROL (STAGE 2) - P143"]
[null,0,"None"]
[null,1,"Timer"]
[null,2,"Frequency"]
[null,3,"Timer + Freq","Timer & Frequency"]
[null,4,"Freq + CB Comp","Frequency with CB Close time compensation"]
["G157",null,"df/dt PROTECTION RAMP DIRECTION"]
[null,0,"Negative"]
[null,1,"Positive"]
[null,2,"Both"]
["G158",null,"I2> Function Link"]
[null,"Bit 0","VTS Blocks I2>1            "]
[null,"Bit 1","VTS Blocks I2>2            "]
[null,"Bit 2","VTS Blocks I2>3            "]
[null,"Bit 3","VTS Blocks I2>4          "]
[null,"Bit 4","2H Blocks I2>1"]
[null,"Bit 5","2H Blocks I2>2"]
[null,"Bit 6","2H Blocks I2>3"]
[null,"Bit 7","2H Blocks I2>4"]
["G159",null,"Advanced Frequency PROTECTION  DIRECTION"]
[null,0,"Disabled"]
[null,1,"Under"]
[null,2,"Over"]
["G160",null,"Advanced df/dt PROTECTION RAMP DIRECTION"]
[null,0,"Disabled"]
[null,1,"Negative"]
[null,2,"Positive"]
[null,3,"Both"]
["G161","MODBUS value+bit pos","Started Elements(Advanced frequney protection)"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Start F 1"]
[null,"0x0000,0x0002","Start F 2"]
[null,"0x0000,0x0004","Start F 3"]
[null,"0x0000,0x0008","Start F 4"]
[null,"0x0000,0x0010","Start F 5"]
[null,"0x0000,0x0020","Start F 6"]
[null,"0x0000,0x0040","Start F 7"]
[null,"0x0000,0x0080","Start F 8"]
[null,"0x0000,0x0100","Start F 9"]
[null,"0x0000,0x0200","Start df/dt+t 1"]
[null,"0x0000,0x0400","Start df/dt+t 2"]
[null,"0x0000,0x0800","Start df/dt+t 3"]
[null,"0x0000,0x1000","Start df/dt+t 4"]
[null,"0x0000,0x2000","Start df/dt+t 5"]
[null,"0x0000,0x4000","Start df/dt+t 6"]
[null,"0x0000,0x8000","Start df/dt+t 7"]
[null,"0x0001,0x0000","Start df/dt+t 8"]
[null,"0x0002,0x0000","Start df/dt+t 9"]
[null,"0x0004,0x0000","Sta DelF/DelT 1"]
[null,"0x0008,0x0000","Sta DelF/DelT 2"]
[null,"0x0010,0x0000","Sta DelF/DelT 3"]
[null,"0x0020,0x0000","Sta DelF/DelT 4"]
[null,"0x0040,0x0000","Sta DelF/DelT 5"]
[null,"0x0080,0x0000","Sta DelF/DelT 6"]
[null,"0x0100,0x0000","Sta DelF/DelT 7"]
[null,"0x0200,0x0000","Sta DelF/DelT 8"]
[null,"0x0400,0x0000","Sta DelF/DelT 9"]
[null,"0x0800,0x0000"]
[null,"0x1000,0x0000"]
[null,"0x2000,0x0000"]
[null,"0x4000,0x0000"]
[null,"0x8000,0x0000"]
["G162","MODBUS value+bit pos","Tripped Elements(Advanced frequney protection)"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Trip F 1"]
[null,"0x0000,0x0002","Trip F 2"]
[null,"0x0000,0x0004","Trip F 3"]
[null,"0x0000,0x0008","Trip F 4"]
[null,"0x0000,0x0010","Trip F 5"]
[null,"0x0000,0x0020","Trip F 6"]
[null,"0x0000,0x0040","Trip F 7"]
[null,"0x0000,0x0080","Trip F 8"]
[null,"0x0000,0x0100","Trip F 9"]
[null,"0x0000,0x0200","Trip df/dt+t 1"]
[null,"0x0000,0x0400","Trip df/dt+t 2"]
[null,"0x0000,0x0800","Trip df/dt+t 3"]
[null,"0x0000,0x1000","Trip df/dt+t 4"]
[null,"0x0000,0x2000","Trip df/dt+t 5"]
[null,"0x0000,0x4000","Trip df/dt+t 6"]
[null,"0x0000,0x8000","Trip df/dt+t 7"]
[null,"0x0001,0x0000","Trip df/dt+t 8"]
[null,"0x0002,0x0000","Trip df/dt+t 9"]
[null,"0x0004,0x0000","Trip DelF/DelT 1"]
[null,"0x0008,0x0000","Trip DelF/DelT 2"]
[null,"0x0010,0x0000","Trip DelF/DelT 3"]
[null,"0x0020,0x0000","Trip DelF/DelT 4"]
[null,"0x0040,0x0000","Trip DelF/DelT 5"]
[null,"0x0080,0x0000","Trip DelF/DelT 6"]
[null,"0x0100,0x0000","Trip DelF/DelT 7"]
[null,"0x0200,0x0000","Trip DelF/DelT 8"]
[null,"0x0400,0x0000","Trip DelF/DelT 9"]
[null,"0x0800,0x0000"]
[null,"0x1000,0x0000"]
[null,"0x2000,0x0000"]
[null,"0x4000,0x0000"]
[null,"0x8000,0x0000"]
["G163",null,"PHASE ROTATION"]
[null,0,"Standard ABC"]
[null,1,"Reverse ACB"]
["G164","MODBUS value+bit pos","Tripped Elements(Advanced frequney protection)"]
[null,"(Second reg, First Reg)"]
[null,"0x0000,0x0001","Trip f+df/dt  1"]
[null,"0x0000,0x0002","Trip f+df/dt  2"]
[null,"0x0000,0x0004","Trip f+df/dt  3"]
[null,"0x0000,0x0008","Trip f+df/dt  4"]
[null,"0x0000,0x0010","Trip f+df/dt  5"]
[null,"0x0000,0x0020","Trip f+df/dt  6"]
[null,"0x0000,0x0040","Trip f+df/dt  7"]
[null,"0x0000,0x0080","Trip f+df/dt  8"]
[null,"0x0000,0x0100","Trip f+df/dt  9"]
[null,"0x0000,0x0200"]
[null,"0x0000,0x0400"]
[null,"0x0000,0x0800"]
[null,"0x0000,0x1000"]
[null,"0x0000,0x2000"]
[null,"0x0000,0x4000"]
[null,"0x0000,0x8000"]
[null,"0x0001,0x0000"]
[null,"0x0002,0x0000"]
[null,"0x0004,0x0000"]
[null,"0x0008,0x0000"]
[null,"0x0010,0x0000"]
[null,"0x0020,0x0000"]
[null,"0x0040,0x0000"]
[null,"0x0080,0x0000"]
[null,"0x0100,0x0000"]
[null,"0x0200,0x0000"]
[null,"0x0400,0x0000"]
[null,"0x0800,0x0000"]
[null,"0x1000,0x0000"]
[null,"0x2000,0x0000"]
[null,"0x4000,0x0000"]
[null,"0x8000,0x0000"]
["G166",null,"NPSOC CURVE TYPES"]
[null,0,"DT","(DT)"]
[null,1,"IEC S Inverse","(TMS)"]
[null,2,"IEC V Inverse","(TMS)"]
[null,3,"IEC E Inverse","(TMS)"]
[null,4,"UK LT Inverse","(TMS)"]
[null,5,"IEEE M Inverse","(TD)"]
[null,6,"IEEE V Inverse","(TD)"]
[null,7,"IEEE E Inverse","(TD)"]
[null,8,"US Inverse","(TD)"]
[null,9,"US ST Inverse","(TD)"]
["G200",null,"OPTO INPUT CONFIGURATION - GLOBAL"]
[null,0,"24/27V"]
[null,1,"30/34V"]
[null,2,"48/54V"]
[null,3,"110/125V"]
[null,4,"220/250V"]
[null,5,"Custom"]
["G201",null,"OPTO INPUT CONFIGURATION - INDIVIDUAL"]
[null,0,"24/27V"]
[null,1,"30/34V"]
[null,2,"48/54V"]
[null,3,"110/125V"]
[null,4,"220/250V"]
["G202","2 REGISTERS","CONTROL INPUT STATUS"]
[null,"(2nd Reg, 1st Reg)"]
[null,"0x0000,0x0001","Control Input 1  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0002","Control Input 2  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0004","Control Input 3  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0008","Control Input 4  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0010","Control Input 5  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0020","Control Input 6  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0040","Control Input 7  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0080","Control Input 8  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0100","Control Input 9  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0200","Control Input 10  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0400","Control Input 11  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x0800","Control Input 12  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x1000","Control Input 13  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x2000","Control Input 14  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x4000","Control Input 15  (0 = Reset, 1 = Set)"]
[null,"0x0000,0x8000","Control Input 16  (0 = Reset, 1 = Set)"]
[null,"0x0001,0x0000","Control Input 17  (0 = Reset, 1 = Set)"]
[null,"0x0002,0x0000","Control Input 18  (0 = Reset, 1 = Set)"]
[null,"0x0004,0x0000","Control Input 19  (0 = Reset, 1 = Set)"]
[null,"0x0008,0x0000","Control Input 20  (0 = Reset, 1 = Set)"]
[null,"0x0010,0x0000","Control Input 21  (0 = Reset, 1 = Set)"]
[null,"0x0020,0x0000","Control Input 22  (0 = Reset, 1 = Set)"]
[null,"0x0040,0x0000","Control Input 23  (0 = Reset, 1 = Set)"]
[null,"0x0080,0x0000","Control Input 24  (0 = Reset, 1 = Set)"]
[null,"0x0100,0x0000","Control Input 25  (0 = Reset, 1 = Set)"]
[null,"0x0200,0x0000","Control Input 26  (0 = Reset, 1 = Set)"]
[null,"0x0400,0x0000","Control Input 27  (0 = Reset, 1 = Set)"]
[null,"0x0800,0x0000","Control Input 28  (0 = Reset, 1 = Set)"]
[null,"0x1000,0x0000","Control Input 29  (0 = Reset, 1 = Set)"]
[null,"0x2000,0x0000","Control Input 30  (0 = Reset, 1 = Set)"]
[null,"0x4000,0x0000","Control Input 31  (0 = Reset, 1 = Set)"]
[null,"0x8000,0x0000","Control Input 32  (0 = Reset, 1 = Set)"]
["G203",null,"CONTROL INPUT COMMAND"]
[null,0,"No Operation"]
[null,1,"Set"]
[null,2,"Reset"]
["G204",null,"REAR COMMS CARD STATUS"]
[null,0,"Unsupported"]
[null,1,"Card Not Fitted"]
[null,2,"EIA232 OK"]
[null,3,"EIA485 OK"]
[null,4,"K-Bus OK"]
["G205",null,"PORT CONFIG (RCUR2)"]
[null,0,"EIA232 (RS232)"]
[null,1,"EIA485 (RS485)"]
[null,2,"K Bus"]
["G206",null,"COMMS MODE (IEC60870-5-2)"]
[null,0,"IEC60870 FT1.2"]
[null,1,"10-Bit No Parity"]
["G207",null,"PORT CONFIG (First Rear Port)"]
[null,0,"K-Bus"]
[null,1,"EIA485 (RS485)"]
["G208",null,"FIRST REAR PORT STATUS"]
[null,0,"K-Bus OK"]
[null,1,"EIA485 OK"]
[null,2,"Fibre Optic OK"]
["G210",null,"CS103 BLOCKING MODE"]
[null,0,"Disabled"]
[null,1,"Monitor Blocking"]
[null,2,"Command Blocking"]
["G211",null,"INTERMICOM BLOCKING Reserved)"]
[null,0,"Disabled"]
[null,1,"Direct"]
[null,2,"Blocking"]
["G212",null,"INTERMICOM TRIP (Reserved)"]
[null,0,"Disabled"]
[null,1,"Permissive"]
[null,2,"Direct"]
["G213",null,"INTERMICOM DATA RATE"]
[null,0,600]
[null,1,1200]
[null,2,2400]
[null,3,4800]
[null,4,9600]
[null,5,19200]
["G214",null,"INTERMICOM LOOPBACK MODE"]
[null,0,"Disabled"]
[null,1,"Internal"]
[null,2,"External"]
["G215",null,"INTERMICOM SIGNAL STATE"]
[null,0,"Default"]
[null,1,"Latched"]
["G216",null,"INTERMICOM HW STATUS"]
[null,0,"OK"]
[null,1,"Fail"]
[null,2,"Card Not Fitted"]
[null,3,"Read Error"]
[null,4,"HW Version Error"]
[null,5,"Write Error"]
["G217",null,"INTERMICOM STATUS"]
[null,0,"OK"]
[null,1,"Fail"]
[null,2,"Card Not Fitted"]
[null,5,"Unavailable"]
["G218",null,"INTERMICOM REMOTE DEVICE (Reserved)"]
[null,0,"Px40"]
[null,1,"Px30"]
["G219",null,"INTERMICOM BLOCKING"]
[null,0,"Disabled"]
[null,1,"Direct"]
[null,2,"Permissive"]
[null,3,"Blocking"]
["G220",null,"ETHERNET CARD MEDIA SELECTOR (Reserved)"]
[null,0,"Copper"]
[null,1,"Fibre"]
["G221",null,"GOOSE STARTUP MODE (Reserved)"]
[null,0,"Promiscuous"]
[null,1,"Broadcast"]
["G222",null,"AE QUALIFIER SELECTOR (Reserved)"]
[null,0,"Not Used"]
[null,1,"Used"]
["G223",null,"IED STATISTICS RESET (Reserved)"]
[null,0,"None"]
[null,1,"Local IED"]
[null,2,"Viewed IED"]
[null,2,"All Enrolled"]
[null,3,"All Enrolled + Local"]
["G224",null,"ETHERNET LOOPBACK MODE (Reserved)"]
[null,0,"Loopback Off"]
[null,1,"Internal Loop"]
[null,2,"External Loop"]
["G225",null,"SOFTWARE RELOAD MODE (Reserved)"]
[null,0,"No Action"]
[null,1,"Reload Software"]
["G226",null,"LINK STATUS REPORT MODE (Reserved)"]
[null,0,"Alarm"]
[null,1,"Event"]
[null,2,"None"]
["G227",null,"GOOSE VIP STATUS"]
[null,0,"GOOSE VIP 1"]
[null,1,"GOOSE VIP 2"]
[null,2,"GOOSE VIP 3"]
[null,3,"GOOSE VIP 4"]
[null,4,"GOOSE VIP 5"]
[null,5,"GOOSE VIP 6"]
[null,6,"GOOSE VIP 7"]
[null,7,"GOOSE VIP 8"]
[null,8,"GOOSE VIP 9"]
[null,9,"GOOSE VIP 10"]
[null,10,"GOOSE VIP 11"]
[null,11,"GOOSE VIP 12"]
[null,12,"GOOSE VIP 13"]
[null,13,"GOOSE VIP 14"]
[null,14,"GOOSE VIP 15"]
[null,15,"GOOSE VIP 16"]
[null,16,"GOOSE VIP 17"]
[null,17,"GOOSE VIP 18"]
[null,18,"GOOSE VIP 19"]
[null,19,"GOOSE VIP 20"]
[null,20,"GOOSE VIP 21"]
[null,21,"GOOSE VIP 22"]
[null,22,"GOOSE VIP 23"]
[null,23,"GOOSE VIP 24"]
[null,24,"GOOSE VIP 25"]
[null,25,"GOOSE VIP 26"]
[null,26,"GOOSE VIP 27"]
[null,27,"GOOSE VIP 28"]
[null,28,"GOOSE VIP 29"]
[null,29,"GOOSE VIP 30"]
[null,30,"GOOSE VIP 31"]
[null,31,"GOOSE VIP 32"]
["G228",null,"PLATFORM ALARMS"]
[null,"0x00000001","Battery Fail"]
[null,"0x00000002","Field Volt Fail"]
[null,"0x00000004","Comm2 H/W FAIL"]
[null,"0x00000008","GOOSE IED Absent","UCA2.0"]
[null,"0x00000010","NIC Not Fitted","UCA2.0"]
[null,"0x00000020","NIC No Response","UCA2.0"]
[null,"0x00000040","NIC Fatal Error","UCA2.0"]
[null,"0x00000080","NIC Soft. Reload","UCA2.0"]
[null,"0x00000100","Bad TCP/IP Config.","UCA2.0"]
[null,"0x00000200","Bad OSI Config.","UCA2.0"]
[null,"0x00000400","NIC Link Fail","UCA2.0"]
[null,"0x00000800","NIC SW Mis-Match","UCA2.0"]
[null,"0x00001000","IP Addr Conflict","UCA2.0"]
[null,"0x00002000","Unused","Reserved for IM Loopback"]
[null,"0x00004000","Unused","Reserved for IM Message Fail"]
[null,"0x00008000","Unused","Reserved for IM Data CD Fail"]
[null,"0x00010000","Unused","Reserved for IM Channel Fail"]
[null,"0x00020000","Backup Setting"]
[null,"0x00040000","Bad DNP Setting","DNP3.0 "]
[null,"0x00080000","Unused"]
[null,"0x00100000","Unused"]
[null,"0x00200000","Unused"]
[null,"0x00400000","Unused"]
[null,"0x00800000","Unused"]
[null,"0x01000000","Unused"]
[null,"0x02000000","Unused"]
[null,"0x04000000","Unused"]
[null,"0x08000000","Unused"]
[null,"0x10000000","Unused"]
[null,"0x20000000","Unused"]
[null,"0x40000000","Unused"]
[null,"0x80000000","Unused"]
["G229",null,"ENROLLED FLAGS"]
[null,0,"IED Status 1"]
[null,1,"IED Status 2"]
[null,2,"IED Status 3"]
[null,3,"IED Status 4"]
[null,4,"IED Status 5"]
[null,5,"IED Status 6"]
[null,6,"IED Status 7"]
[null,7,"IED Status 8"]
[null,8,"IED Status 9"]
[null,9,"IED Status 10"]
[null,10,"IED Status 11"]
[null,11,"IED Status 12"]
[null,12,"IED Status 13"]
[null,13,"IED Status 14"]
[null,14,"IED Status 15"]
[null,15,"IED Status 16"]
[null,16,"IED Status 17"]
[null,17,"IED Status 18"]
[null,18,"IED Status 19"]
[null,19,"IED Status 20"]
[null,20,"IED Status 21"]
[null,21,"IED Status 22"]
[null,22,"IED Status 23"]
[null,23,"IED Status 24"]
[null,24,"IED Status 25"]
[null,25,"IED Status 26"]
[null,26,"IED Status 27"]
[null,27,"IED Status 28"]
[null,28,"IED Status 29"]
[null,29,"IED Status 30"]
[null,30,"IED Status 31"]
[null,31,"IED Status 32"]
["G230",null,"GOOSE TYPE"]
[null,0,"UCA2.0"]
[null,1,"IEC61850"]
["G231",null,"DIRECT ACCESS KEYS"]
[null,0,"Disabled"]
[null,1,"Enabled"]
[null,2,"Hotkey Only"]
[null,3,"CB Ctrl Only"]
["G232",null,"CONTROL INPUT COMMAND TEXT"]
[null,0,"ON/OFF"]
[null,1,"SET/RESET"]
[null,2,"IN/OUT"]
[null,3,"ENABLED/DISABLED"]
["G233",null,"HOTKEY ENABLED CONTROL INPUTS"]
[null,"0x00000001","Control Input 1"]
[null,"0x00000002","Control Input 2"]
[null,"0x00000004","Control Input 3"]
[null,"0x00000008","Control Input 4"]
[null,"0x00000010","Control Input 5"]
[null,"0x00000020","Control Input 6"]
[null,"0x00000040","Control Input 7"]
[null,"0x00000080","Control Input 8"]
[null,"0x00000100","Control Input 9"]
[null,"0x00000200","Control Input 10"]
[null,"0x00000400","Control Input 11"]
[null,"0x00000800","Control Input 12"]
[null,"0x00001000","Control Input 13"]
[null,"0x00002000","Control Input 14"]
[null,"0x00004000","Control Input 15"]
[null,"0x00008000","Control Input 16"]
[null,"0x00010000","Control Input 17"]
[null,"0x00020000","Control Input 18"]
[null,"0x00040000","Control Input 19"]
[null,"0x00080000","Control Input 20"]
[null,"0x00100000","Control Input 21"]
[null,"0x00200000","Control Input 22"]
[null,"0x00400000","Control Input 23"]
[null,"0x00800000","Control Input 24"]
[null,"0x01000000","Control Input 25"]
[null,"0x02000000","Control Input 26"]
[null,"0x04000000","Control Input 27"]
[null,"0x08000000","Control Input 28"]
[null,"0x10000000","Control Input 29"]
[null,"0x20000000","Control Input 30"]
[null,"0x40000000","Control Input 31"]
[null,"0x80000000","Control Input 32"]
["G234",null,"CONTROL INPUT SIGNAL TYPE"]
[null,0,"Latched"]
[null,1,"Pulsed"]
["G235",null,"ETHERNET PROTOCOL"]
[null,0,"UCA2.0"]
[null,1,"UCA2.0 GOOSE"]
[null,2,"IEC61850"]
[null,3,"DNP3"]
["G236",null,"MODBUS DISTURBANCE RECORDER EXTRACTION"]
[null,0,"Idle"]
[null,1,"Busy"]
[null,2,"Page Ready"]
[null,3,"Configuration Complete"]
[null,4,"Record Complete"]
[null,5,"Extraction Failed"]
["G237",null,"DUAL CHARACTERISTIC OPTO CONFIGURATION"]
[null,0,"Standard 60% - 80%"]
[null,1,"50% - 70%"]
["G238",null,"DATE & TIME FORMAT (MODBUS only)"]
[null,0,"Standard IEC  (Existing format)"]
[null,1,"Reverse IEC   (Company agreed format)"]
["G239",null,"NOT USED"]
["G240",null,"LOGICAL NODE ARRANGEMENT (NCIT)"]
[null,0,"VL, IL, IN"]
[null,1,"VL, IL, IN2"]
[null,2,"VL, IL, IN, IN2"]
[null,3,"VL, 2xIL, 2xIN"]
[null,4,"VL, Sum (2xIL)"]
[null,5,"VL, IL, IN, VB"]
[null,6,"VL, IL, IN, 2xVB"]
[null,7,"VL, 2xIL, 2xIN, VB"]
[null,8,"VL, IL, IN2, VB"]
[null,9,"VL, IL, IN2, 2xVB"]
[null,10,"VL, 2x (IL, IN, VB)"]
[null,11,"VL, IL, IN2, IN, VB"]
[null,12,"VL, 2xIL, 3xIN, VB"]
[null,13,"VL, IL, IN, IN2, VB"]
["G241",null,"CHECK SYNCH SELECTION (OLD NCIT ONLY)"]
[null,0,"A-N"]
[null,1,"B-N"]
[null,2,"C-N"]
[null,3,"A-B"]
[null,4,"B-C"]
[null,5,"C-A"]
["G242",null,"FUNCTION KEY STATUS (Extended CPU2 only)"]
[null,0,"Disabled"]
[null,1,"Unlocked (Enabled)"]
[null,2,"Locked"]
["G243",null,"FUNCTION KEY MODE (Extended CPU2 only)"]
[null,0,"Normal"]
[null,1,"Toggled"]
["G244",null,"NOT USED"]
["G245",null,"IEC61850 DATA TYPES"]
[null,0,"NONE"]
[null,1,"BSTR2"]
[null,2,"BOOL"]
[null,3,"INT8"]
[null,4,"INT16"]
[null,5,"INT32"]
[null,6,"UINT8"]
[null,7,"UINT16"]
[null,8,"UINT32"]
[null,9,"SPS"]
[null,10,"DPS"]
[null,11,"INS"]
["G246",null,"IEC61850 TEST MODE"]
[null,0,"Disabled"]
[null,1,"Pass Through"]
[null,2,"Forced"]
["G247",null,"SNTP Status"]
[null,0,"Disabled"]
[null,1,"Trying Server 1"]
[null,2,"Trying Server 2"]
[null,3,"Server 1 OK"]
[null,4,"Server 2 OK"]
[null,5,"No Response"]
[null,6,"No Valid Clock"]
["G248",null,"IEC61850 Setting Banks"]
[null,0,"No Action"]
[null,1,"Switch Banks"]
["G249",null,"DNP3.0 Measurment Scaling"]
[null,0,"Normalised"]
[null,1,"Primary"]
[null,2,"Secondary"]
["G250",null,"Days Of The Week"]
[null,0,"Sunday"]
[null,1,"Monday"]
[null,2,"Tuesday"]
[null,3,"Wednesday"]
[null,4,"Thursday"]
[null,5,"Friday"]
[null,6,"Saturday"]
["G251",null,"Months Of The Year"]
[null,0,"January"]
[null,1,"February"]
[null,2,"March"]
[null,3,"April"]
[null,4,"May"]
[null,5,"June"]
[null,6,"July"]
[null,7,"August"]
[null,8,"September"]
[null,9,"October"]
[null,10,"November"]
[null,11,"December"]
["G252",null,"Week Number"]
[null,0,"First"]
[null,1,"Second"]
[null,2,"Third"]
[null,3,"Fourth"]
[null,4,"Last"]
["G253",null,"Time Zone"]
[null,0,"UTC"]
[null,1,"Local"]
["G254",null,"Local Time"]
[null,0,"Disabled"]
[null,1,"Fixed"]
[null,2,"Flexible"]
["G256",null,"Restore MCL"]
[null,0,"No Action"]
[null,1,"Restore MCL"]
["G257",null,"Power Direction Select"]
[null,0,"Reverse"]
[null,1,"Forward"]
["G258",null,"Power Mode Select"]
[null,0,"Active"]
[null,1,"Reactive"]
["G259",null,"Power Blocking                                            "]
[null,"Bit 0","Poledead Blocks Power<1"]
[null,"Bit 1","Poledead Blocks Power<2"]
["G260",null,"Sensitive Power Select"]
[null,0,"Disabled"]
[null,1,"Reverse"]
[null,2,"Low Forward"]
[null,3,"Over"]

{"sheet":"DDBSignals","index":3,"n_rows":1538,"n_cols":40,"rows_kept":1538,"cut":false,"hidden":false,"merged":[[0,0,0,39]],"flags":["formulas_cached_only"]}
["Digital Data Bus"]
["Element Name","Ordinal","Source","Type","Response Fn","Description","English Text","1A","2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L","G32"]
["DDB_OUTPUT_RELAY_1",0,"SW","RELAY","event_RelayChange","see [4B 01]","See [4B 01]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_2",1,"SW","RELAY","event_RelayChange","see [4B 02]","See [4B 02]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_3",2,"SW","RELAY","event_RelayChange","see [4B 03]","See [4B 03]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_4",3,"SW","RELAY","event_RelayChange","see [4B 04]","See [4B 04]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_5",4,"SW","RELAY","event_RelayChange","see [4B 05]","See [4B 05]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_6",5,"SW","RELAY","event_RelayChange","see [4B 06]","See [4B 06]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_7",6,"SW","RELAY","event_RelayChange","see [4B 07]","See [4B 07]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_8",7,"SW","RELAY","event_RelayChange","see [4B 08]","See [4B 08]",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_9",8,"SW","RELAY","event_RelayChange","see [4B 09]","See [4B 09]",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_10",9,"SW","RELAY","event_RelayChange","see [4B 0A]","See [4B 0A]",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_11",10,"SW","RELAY","event_RelayChange","see [4B 0B]","See [4B 0B]",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_12",11,"SW","RELAY","event_RelayChange","see [4B 0C]","See [4B 0C]",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_13",12,"SW","RELAY","event_RelayChange","see [4B 0D]","See [4B 0D]",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_14",13,"SW","RELAY","event_RelayChange","see [4B 0E]","See [4B 0E]",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_15",14,"SW","RELAY","event_RelayChange","see [4B 0F]","See [4B 0F]",{"$nulls":4},"*",null,null,null,"*","*",null,"*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_16",15,"SW","RELAY","event_RelayChange","see [4B 10]","See [4B 10]",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":5},"*",null,"*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_17",16,"SW","RELAY","event_RelayChange","see [4B 11]","See [4B 11]",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_18",17,"SW","RELAY","event_RelayChange","see [4B 12]","See [4B 12]",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_19",18,"SW","RELAY","event_RelayChange","see [4B 13]","See [4B 13]",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_20",19,"SW","RELAY","event_RelayChange","see [4B 14]","See [4B 14]",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","*"]
["DDB_OUTPUT_RELAY_21",20,"SW","RELAY","event_RelayChange","see [4B 15]","See [4B 15]",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*","*"]
["DDB_OUTPUT_RELAY_22",21,"SW","RELAY","event_RelayChange","see [4B 16]","See [4B 16]",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*","*"]
["DDB_OUTPUT_RELAY_23",22,"SW","RELAY","event_RelayChange","see [4B 17]","See [4B 17]",{"$nulls":11},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*","*"]
["DDB_OUTPUT_RELAY_24",23,"SW","RELAY","event_RelayChange","see [4B 18]","See [4B 18]",{"$nulls":11},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*","*"]
["DDB_OUTPUT_RELAY_25",24,"SW","RELAY","event_RelayChange","see [4B 19]","See [4B 19]",{"$nulls":11},"*",null,null,"*",{"$nulls":12},"*",null,null,"*",null,"*"]
["DDB_OUTPUT_RELAY_26",25,"SW","RELAY","event_RelayChange","see [4B 1A]","See [4B 1A]",{"$nulls":11},"*",null,null,"*",{"$nulls":12},"*",null,null,"*",null,"*"]
["DDB_OUTPUT_RELAY_27",26,"SW","RELAY","event_RelayChange","see [4B 1B]","See [4B 1B]",{"$nulls":11},"*",{"$nulls":15},"*",null,null,"*",null,"*"]
["DDB_OUTPUT_RELAY_28",27,"SW","RELAY","event_RelayChange","see [4B 1C]","See [4B 1C]",{"$nulls":11},"*",{"$nulls":15},"*",null,null,"*",null,"*"]
["DDB_OUTPUT_RELAY_29",28,"SW","RELAY","event_RelayChange","see [4B 1D]","See [4B 1D]",{"$nulls":11},"*",{"$nulls":15},"*",{"$nulls":4},"*"]
["DDB_OUTPUT_RELAY_30",29,"SW","RELAY","event_RelayChange","see [4B 1E]","See [4B 1E]",{"$nulls":11},"*",{"$nulls":15},"*",{"$nulls":4},"*"]
["DDB_OUTPUT_RELAY_31",30,"SW","RELAY","event_RelayChange","see [4B 1F]","See [4B 1F]",{"$nulls":27},"*",{"$nulls":4},"*"]
["DDB_OUTPUT_RELAY_32",31,"SW","RELAY","event_RelayChange","see [4B 20]","See [4B 20]",{"$nulls":27},"*",{"$nulls":4},"*"]
["DDB_OPTO_ISOLATOR_1",32,"SW","OPTO","NO_RESPONSE","see [4A 01]","See [4A 01]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_2",33,"SW","OPTO","NO_RESPONSE","see [4A 02]","See [4A 02]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_3",34,"SW","OPTO","NO_RESPONSE","see [4A 03]","See [4A 03]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_4",35,"SW","OPTO","NO_RESPONSE","see [4A 04]","See [4A 04]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_5",36,"SW","OPTO","NO_RESPONSE","see [4A 05]","See [4A 05]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_6",37,"SW","OPTO","NO_RESPONSE","see [4A 06]","See [4A 06]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_7",38,"SW","OPTO","NO_RESPONSE","see [4A 07]","See [4A 07]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_8",39,"SW","OPTO","NO_RESPONSE","see [4A 08]","See [4A 08]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OPTO_ISOLATOR_9",40,"SW","OPTO","NO_RESPONSE","see [4A 09]","See [4A 09]",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_10",41,"SW","OPTO","NO_RESPONSE","see [4A 0A]","See [4A 0A]",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_11",42,"SW","OPTO","NO_RESPONSE","see [4A 0B]","See [4A 0B]",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_12",43,"SW","OPTO","NO_RESPONSE","see [4A 0C]","See [4A 0C]",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_13",44,"SW","OPTO","NO_RESPONSE","see [4A 0D]","See [4A 0D]",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_14",45,"SW","OPTO","NO_RESPONSE","see [4A 0E]","See [4A 0E]",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_15",46,"SW","OPTO","NO_RESPONSE","see [4A 0F]","See [4A 0F]",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_16",47,"SW","OPTO","NO_RESPONSE","see [4A 10]","See [4A 10]",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"*"]
["DDB_OPTO_ISOLATOR_17",48,"SW","OPTO","NO_RESPONSE","see [4A 11]","See [4A 11]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_18",49,"SW","OPTO","NO_RESPONSE","see [4A 12]","See [4A 12]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_19",50,"SW","OPTO","NO_RESPONSE","see [4A 13]","See [4A 13]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_20",51,"SW","OPTO","NO_RESPONSE","see [4A 14]","See [4A 14]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_21",52,"SW","OPTO","NO_RESPONSE","see [4A 15]","See [4A 15]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_22",53,"SW","OPTO","NO_RESPONSE","see [4A 16]","See [4A 16]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_23",54,"SW","OPTO","NO_RESPONSE","see [4A 17]","See [4A 17]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_24",55,"SW","OPTO","NO_RESPONSE","see [4A 18]","See [4A 18]",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_25",56,"SW","OPTO","NO_RESPONSE","see [4A 19]","See [4A 19]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_26",57,"SW","OPTO","NO_RESPONSE","see [4A 1A]","See [4A 1A]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_27",58,"SW","OPTO","NO_RESPONSE","see [4A 1B]","See [4A 1B]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_28",59,"SW","OPTO","NO_RESPONSE","see [4A 1C]","See [4A 1C]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_29",60,"SW","OPTO","NO_RESPONSE","see [4A 1D]","See [4A 1D]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_30",61,"SW","OPTO","NO_RESPONSE","see [4A 1E]","See [4A 1E]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_31",62,"SW","OPTO","NO_RESPONSE","see [4A 1F]","See [4A 1F]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OPTO_ISOLATOR_32",63,"SW","OPTO","NO_RESPONSE","see [4A 20]","See [4A 20]",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"*"]
["DDB_OUTPUT_LED_1",64,"SW","LED","NO_RESPONSE",null,"LED 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_LED_2",65,"SW","LED","NO_RESPONSE",null,"LED 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_LED_3",66,"SW","LED","NO_RESPONSE",null,"LED 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_LED_4",67,"SW","LED","NO_RESPONSE",null,"LED 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_LED_5",68,"SW","LED","NO_RESPONSE",null,"LED 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_LED_6",69,"SW","LED","NO_RESPONSE",null,"LED 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_LED_7",70,"SW","LED","NO_RESPONSE",null,"LED 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_LED_8",71,"SW","LED","NO_RESPONSE",null,"LED 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"*"]
["DDB_OUTPUT_CON_1",72,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_2",73,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_3",74,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_4",75,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_5",76,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_6",77,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_7",78,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_8",79,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 8",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_9",80,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 9",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_10",81,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 10",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_11",82,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 11",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_12",83,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 12",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_13",84,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 13",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_14",85,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 14",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_15",86,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 15",{"$nulls":4},"*",null,null,null,"*","*",null,"*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_16",87,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 16",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":5},"*",null,"*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_CON_17",88,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 17",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*"]
["DDB_OUTPUT_CON_18",89,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 18",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*"]
["DDB_OUTPUT_CON_19",90,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 19",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*"]
["DDB_OUTPUT_CON_20",91,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 20",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*"]
["DDB_OUTPUT_CON_21",92,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 21",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*"]
["DDB_OUTPUT_CON_22",93,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 22",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*"]
["DDB_OUTPUT_CON_23",94,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 23",{"$nulls":11},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*"]
["DDB_OUTPUT_CON_24",95,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 24",{"$nulls":11},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*"]
["DDB_OUTPUT_CON_25",96,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 25",{"$nulls":11},"*",null,null,"*",{"$nulls":12},"*",null,null,"*"]
["DDB_OUTPUT_CON_26",97,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 26",{"$nulls":11},"*",null,null,"*",{"$nulls":12},"*",null,null,"*"]
["DDB_OUTPUT_CON_27",98,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 27",{"$nulls":11},"*",{"$nulls":15},"*",null,null,"*"]
["DDB_OUTPUT_CON_28",99,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 28",{"$nulls":11},"*",{"$nulls":15},"*",null,null,"*"]
["DDB_OUTPUT_CON_29",100,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 29",{"$nulls":11},"*",{"$nulls":15},"*"]
["DDB_OUTPUT_CON_30",101,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 30",{"$nulls":11},"*",{"$nulls":15},"*"]
["DDB_OUTPUT_CON_31",102,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 31",{"$nulls":27},"*"]
["DDB_OUTPUT_CON_32",103,"PSL","OUTPUT_CON ","NO_RESPONSE",null,"Relay Cond 32",{"$nulls":27},"*"]
["DDB_LED_CON_1",104,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LED_CON_2",105,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LED_CON_3",106,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LED_CON_4",107,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LED_CON_5",108,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LED_CON_6",109,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LED_CON_7",110,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LED_CON_8",111,"PSL","LED_CON ","NO_RESPONSE",null,"LED Cond IN 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_1",112,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_2",113,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_3",114,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_4",115,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_5",116,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_6",117,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_7",118,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_8",119,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_9",120,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_10",121,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_11",122,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_12",123,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_13",124,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_14",125,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_15",126,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMERIN_16",127,"PSL","TIMERIN","NO_RESPONSE",null,"Timer in 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_1",128,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_2",129,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_3",130,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_4",131,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_5",132,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_6",133,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_7",134,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_8",135,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_9",136,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_10",137,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_11",138,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_12",139,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_13",140,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_14",141,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_15",142,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIMEROUT_16",143,"SW","TIMEROUT","NO_RESPONSE",null,"Timer out 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FAULT_RECORDER_START",144,"PSL","FRT","NO_RESPONSE",null,"Fault REC TRIG","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ILLEGAL_OPTO_SETTINGS_GROUP",145,"SW","PFSO","event_AlarmSelfReset","Setting Group via opto invalid","SG-opto Invalid","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OOS_ALARM",146,"SW","PFSO","event_AlarmSelfReset","Test Mode Enabled","Prot'n Disabled","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FREQ_ALARM",147,"FL","PFSO","event_AlarmSelfReset","Frequency out of range","F out of Range","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_INDICATION",148,"SW","PFSO","event_AlarmSelfReset","VTS Indication","VT Fail Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CTS_INDICATION",149,"SW","PFSO","event_AlarmSelfReset","CTS Indication","CT Fail Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BREAKER_FAIL_ALARM",150,"SW","PFSO","event_AlarmLatched","Breaker Fail Any Trip","CB Fail Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BROKEN_CURRENT_ALARM",151,"SW","PFSO","event_AlarmSelfReset","Broken Current Maintenance Alarm","I^ Maint Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BROKEN_CURRENT_LOCKOUT",152,"SW","PFSO","event_AlarmSelfReset","Broken Current Lockout Alarm","I^ Lockout Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_MAINTENANCE_ALARM",153,"SW","PFSO","event_AlarmSelfReset","No of CB Ops Maintenance Alarm","CB Ops Maint","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_MAINTENANCE_LOCKOUT",154,"SW","PFSO","event_AlarmSelfReset","No of CB Ops Maintenance Lockout","CB Ops Lockout","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXCESSIVE_OP_TIME_ALARM",155,"SW","PFSO","event_AlarmSelfReset","Excessive CB Op Time Maintenance Alarm","CB Op Time Maint","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXCESSIVE_OP_TIME_LOCKOUT",156,"SW","PFSO","event_AlarmSelfReset","Excessive CB Op Time Lockout Alarm","CB Op Time Lock","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EFF_LOCKOUT",157,"SW","PFSO","event_AlarmSelfReset","EFF Lockout Alarm","Fault Freq Lock","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_STATUS_ALARM",158,"SW","PFSO","event_AlarmLatched","CB Status Alarm","CB Status Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_FAILED_TO_TRIP",159,"SW","PFSO","event_AlarmLatched","CB Failed to Trip","Man CB Trip Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_FAILED_TO_CLOSE",160,"SW","PFSO","event_AlarmLatched","CB Failed to Close","Man CB Cls Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_CB_UNHEALTHY",161,"SW","PFSO","event_AlarmLatched","Control CB Unhealthy","Man CB Unhealthy","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_NO_CHECK_SYNC",162,"SW","PFSO","event_AlarmLatched","Control No Check Sync","Man No Checksync",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_LOCKOUT",163,"SW","PFSO","event_AlarmSelfReset","Autoclose Lockout/RLY BAR","AR Lockout",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_CB_UNHEALTHY",164,"SW","PFSO","event_AlarmLatched","AR CB Unhealthy","AR CB Unhealthy",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_NO_SYS_CHECK",165,"SW","PFSO","event_AlarmLatched","A/R No Sys Check","AR No Sys Check",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSTEM_SPLIT_ALARM",166,"SW","PFSO","event_AlarmSelfReset","System Split Alarm","System Split",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDERVOLTAGE_BLOCK",167,"SW","PFSO","event_AlarmLatched","Blocks advanced frequency load shedding","UV Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_1",168,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 1","SR User Alarm 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_2",169,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 2","SR User Alarm 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_3",170,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 3","SR User Alarm 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_4",171,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 4","SR User Alarm 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_5",172,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 5","SR User Alarm 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_6",173,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 6","SR User Alarm 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_7",174,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 7","SR User Alarm 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_8",175,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 8","SR User Alarm 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_9",176,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 9","SR User Alarm 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_10",177,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 10","SR User Alarm 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_11",178,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 11","SR User Alarm 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_12",179,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 12","SR User Alarm 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_13",180,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 13","SR User Alarm 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_14",181,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 14","SR User Alarm 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_15",182,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 15","SR User Alarm 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_16",183,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 16","SR User Alarm 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_17",184,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 17","SR User Alarm 17","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_18",185,"PSL","PFSI","event_AlarmSelfReset","User definable Self Reset Alarm 18","SR User Alarm 18","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_19",186,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 19","MR User Alarm 19","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_20",187,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 20","MR User Alarm 20","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_21",188,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 21","MR User Alarm 21","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_22",189,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 22","MR User Alarm 22","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_23",190,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 23","MR User Alarm 23","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_24",191,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 24","MR User Alarm 24","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_25",192,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 25","MR User Alarm 25","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_26",193,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 26","MR User Alarm 26","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_27",194,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 27","MR User Alarm 27","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_28",195,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 28","MR User Alarm 28","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_29",196,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 29","MR User Alarm 29","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_30",197,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 30","MR User Alarm 30","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_31",198,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 31","MR User Alarm 31","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_32",199,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 32","MR User Alarm 32","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_33",200,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 33","MR User Alarm 33","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_34",201,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 34","MR User Alarm 34","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_USER_ALARM_35",202,"PSL","PFSI","event_AlarmLatched","User definable Manual Reset Alarm 35","MR User Alarm 35","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_TIMER_BLOCK",203,"PSL","PFSI","NO_RESPONSE","Block Phase Overcurrent Stage 1 time delay","I>1 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_TIMER_BLOCK",204,"PSL","PFSI","NO_RESPONSE","Block Phase Overcurrent Stage 2 time delay","I>2 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_TIMER_BLOCK",205,"PSL","PFSI","NO_RESPONSE","Block Phase Overcurrent Stage 3 time delay","I>3 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_TIMER_BLOCK",206,"PSL","PFSI","NO_RESPONSE","Block Phase Overcurrent Stage 4 time delay","I>4 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_207",207,"SW","UNUSED","NO_RESPONSE"]
["DDB_EF1_1_TIMER_BLOCK",208,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #1 Stage 1 time delay","IN1>1 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_2_TIMER_BLOCK",209,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #1 Stage 2 time delay","IN1>2 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_3_TIMER_BLOCK",210,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #1 Stage 3 time delay","IN1>3 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_4_TIMER_BLOCK",211,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #1 Stage 4 time delay","IN1>4 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_1_TIMER_BLOCK",212,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #2 Stage 1 time delay","IN2>1 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_2_TIMER_BLOCK",213,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #2 Stage 2 time delay","IN2>2 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_3_TIMER_BLOCK",214,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #2 Stage 3 time delay","IN2>3 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_4_TIMER_BLOCK",215,"PSL","PFSI","NO_RESPONSE","Block Earth Fault #2 Stage 4 time delay","IN2>4 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_1_TIMER_BLOCK",216,"PSL","PFSI","NO_RESPONSE","Block SEF Stage 1 time delay","ISEF>1 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_2_TIMER_BLOCK",217,"PSL","PFSI","NO_RESPONSE","Block SEF Stage 2 time delay","ISEF>2 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_3_TIMER_BLOCK",218,"PSL","PFSI","NO_RESPONSE","Block SEF Stage 3 time delay","ISEF>3 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_4_TIMER_BLOCK",219,"PSL","PFSI","NO_RESPONSE","Block SEF Stage 4 time delay","ISEF>4 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESOV_1_TIMER_BLOCK",220,"PSL","PFSI","NO_RESPONSE","Block Residual Overvoltage Stage 1 time delay","VN>1 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESOV_2_TIMER_BLOCK",221,"PSL","PFSI","NO_RESPONSE","Block Residual Overvoltage Stage 2 time delay","VN>2 Timer Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_TIMER_BLOCK",222,"PSL","PFSI","NO_RESPONSE","Block Phase Undervoltage Stage 1 time delay","V<1 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_TIMER_BLOCK",223,"PSL","PFSI","NO_RESPONSE","Block Phase Undervoltage Stage 2 time delay","V<2 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_TIMER_BLOCK",224,"PSL","PFSI","NO_RESPONSE","Block Phase Overvoltage Stage 1 time delay","V>1 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_TIMER_BLOCK",225,"PSL","PFSI","NO_RESPONSE","Block Phase Overvoltage Stage 4 time delay","V>2 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CLP_INITIATE",226,"PSL","PFSI","NO_RESPONSE","CLP Initiate","CLP Initiate","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXTERNAL_TRIP_3PH",227,"PSL","PFSI","NO_RESPONSE","External Trip 3ph","Ext. Trip 3ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_THREE_PHASE_52A",228,"PSL","PFSI","NO_RESPONSE","52-A (3 phase)","CB Aux 3ph(52-A)","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_THREE_PHASE_52B",229,"PSL","PFSI","NO_RESPONSE","52-B (3 phase)","CB Aux 3ph(52-B)","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_HEALTHY",230,"PSL","PFSI","NO_RESPONSE","CB Healthy","CB Healthy","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_MCB_OPTO",231,"PSL","PFSI","NO_RESPONSE","MCB/VTS opto","MCB/VTS","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LOGIC_INPUT_TRIP",232,"PSL","PFSI","NO_RESPONSE","Logic Input Trip","Init Trip CB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LOGIC_INPUT_CLOSE",233,"PSL","PFSI","NO_RESPONSE","Logic Input Close","Init Close CB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESET_CB_CLOSE_DELAY",234,"PSL","PFSI","NO_RESPONSE","Reset Manual CB Close Time Delay","Reset Close Dly","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESET_RELAYS_LEDS",235,"PSL","PFSI","event_OptoResetInd","Reset Latched Relays & LED’s","Reset Relays/LED","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESET_THERMAL",236,"PSL","PFSI","NO_RESPONSE","Reset Thermal State","Reset Thermal","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESET_LOCKOUT",237,"PSL","PFSI","NO_RESPONSE","Reset Lockout Opto Input","Reset Lockout","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESET_ALL_VALUES",238,"PSL","PFSI","NO_RESPONSE","Reset CB Maintenance Values","Reset CB Data","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BLOCK_AR",239,"PSL","PFSI","NO_RESPONSE","Block Autoreclose / BAR","Block AR",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LIVE_LINE_MODE",240,"PSL","PFSI","NO_RESPONSE","Live Line Operation","Live Line Mode",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AUTO_MODE",241,"PSL","PFSI","NO_RESPONSE","Auto Mode Operation","Auto Mode",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TELECONTROL_MODE",242,"PSL","PFSI","NO_RESPONSE","Telecontrol Mode Operation","Telecontrol Mode",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_3PH_TRIP",243,"SW","PFSO","event_Protection","1st Stage O/C Trip 3ph","I>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_PH_A_TRIP",244,"SW","PFSO","event_Protection","1st Stage O/C Trip A ","I>1 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_PH_B_TRIP",245,"SW","PFSO","event_Protection","1st Stage O/C Trip B","I>1 Trip B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_PH_C_TRIP",246,"SW","PFSO","event_Protection","1st Stage O/C Trip C","I>1 Trip C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_3PH_TRIP",247,"SW","PFSO","event_Protection","2nd Stage O/C Trip 3ph","I>2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_PH_A_TRIP",248,"SW","PFSO","event_Protection","2nd Stage O/C Trip A ","I>2 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_PH_B_TRIP",249,"SW","PFSO","event_Protection","2nd Stage O/C Trip B ","I>2 Trip B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_PH_C_TRIP",250,"SW","PFSO","event_Protection","2nd Stage O/C Trip C","I>2 Trip C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_3PH_TRIP",251,"SW","PFSO","event_Protection","3rd Stage O/C Trip 3ph","I>3 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_PH_A_TRIP",252,"SW","PFSO","event_Protection","3rd Stage O/C Trip A ","I>3 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_PH_B_TRIP",253,"SW","PFSO","event_Protection","3rd Stage O/C Trip B","I>3 Trip B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_PH_C_TRIP",254,"SW","PFSO","event_Protection","3rd Stage O/C Trip C","I>3 Trip C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_3PH_TRIP",255,"SW","PFSO","event_Protection","4th Stage O/C Trip 3ph","I>4 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_PH_A_TRIP",256,"SW","PFSO","event_Protection","4th Stage O/C Trip A ","I>4 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_PH_B_TRIP",257,"SW","PFSO","event_Protection","4th Stage O/C Trip B ","I>4 Trip B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_PH_C_TRIP",258,"SW","PFSO","event_Protection","4th Stage O/C Trip C","I>4 Trip C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_259",259,"SW","UNUSED","NO_RESPONSE"]
["DDB_BROKEN_CONDUCTOR_TRIP",260,"SW","PFSO","event_Protection","Broken Conductor Trip","Broken Line Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_1_TRIP",261,"SW","PFSO","event_Protection","1st Stage EF#1 Trip","IN1>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_2_TRIP",262,"SW","PFSO","event_Protection","2nd Stage EF#1 Trip","IN1>2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_3_TRIP",263,"SW","PFSO","event_Protection","3rd Stage EF#1 Trip","IN1>3 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_4_TRIP",264,"SW","PFSO","event_Protection","4th Stage EF#1 Trip","IN1>4 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_1_TRIP",265,"SW","PFSO","event_Protection","1st Stage EF#2 Trip","IN2>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_2_TRIP",266,"SW","PFSO","event_Protection","2nd Stage EF#2 Trip","IN2>2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_3_TRIP",267,"SW","PFSO","event_Protection","3rd Stage EF#2 Trip","IN2>3 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_4_TRIP",268,"SW","PFSO","event_Protection","4th Stage EF#2 Trip","IN2>4 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_1_TRIP",269,"SW","PFSO","event_Protection","1st Stage SEF Trip","ISEF>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_2_TRIP",270,"SW","PFSO","event_Protection","2nd Stage SEF Trip","ISEF>2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_3_TRIP",271,"SW","PFSO","event_Protection","3rd Stage SEF Trip","ISEF>3 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_4_TRIP",272,"SW","PFSO","event_Protection","4th Stage SEF Trip","ISEF>4 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_REF_TRIP",273,"SW","PFSO","event_Protection","REF Trip","IREF> Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESOV_1_TRIP",274,"SW","PFSO","event_Protection","1st Stage Residual O/V Trip","VN>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESOV_2_TRIP",275,"SW","PFSO","event_Protection","2nd Stage Residual O/V Trip","VN>2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_THERMAL_TRIP",276,"SW","PFSO","event_Protection","Thermal Overload Trip","Thermal Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NEGSEQOV_TRIP",277,"SW","PFSO","event_Protection","Negative Sequence O/V Trip","V2> Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_3PH_TRIP",278,"SW","PFSO","event_Protection","1st Stage Phase U/V Trip 3ph","V<1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_PH_A_TRIP",279,"SW","PFSO","event_Protection","1st Stage Phase U/V Trip A/AB","V<1 Trip A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_PH_B_TRIP",280,"SW","PFSO","event_Protection","1st Stage Phase U/V Trip B/BC","V<1 Trip B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_PH_C_TRIP",281,"SW","PFSO","event_Protection","1st Stage Phase U/V Trip C/CA","V<1 Trip C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_3PH_TRIP",282,"SW","PFSO","event_Protection","2nd Stage Phase U/V Trip 3ph","V<2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_PH_A_TRIP",283,"SW","PFSO","event_Protection","2nd Stage Phase U/V Trip A/AB","V<2 Trip A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_PH_B_TRIP",284,"SW","PFSO","event_Protection","2nd Stage Phase U/V Trip B/BC","V<2 Trip B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_PH_C_TRIP",285,"SW","PFSO","event_Protection","2nd Stage Phase U/V Trip C/CA","V<2 Trip C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_3PH_TRIP",286,"SW","PFSO","event_Protection","1st Stage Phase O/V Trip 3ph","V>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_PH_A_TRIP",287,"SW","PFSO","event_Protection","1st Stage Phase O/V Trip A/AB","V>1 Trip A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_PH_B_TRIP",288,"SW","PFSO","event_Protection","1st Stage Phase O/V Trip B/BC","V>1 Trip B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_PH_C_TRIP",289,"SW","PFSO","event_Protection","1st Stage Phase O/V Trip C/CA","V>1 Trip C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_3PH_TRIP",290,"SW","PFSO","event_Protection","2nd Stage Phase O/V Trip 3ph","V>2 Trip ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_PH_A_TRIP",291,"SW","PFSO","event_Protection","2nd Stage Phase O/V Trip A/AB","V>2 Trip A/AB ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_PH_B_TRIP",292,"SW","PFSO","event_Protection","2nd Stage Phase O/V Trip B/BC","V>2 Trip B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_PH_C_TRIP",293,"SW","PFSO","event_Protection","2nd Stage Phase O/V Trip C/CA","V>2 Trip C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ANY_START",294,"FL","PFSO","event_FAN+event_Protection","Any Start","Any Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_3PH_START",295,"SW","PFSO","event_Protection","1st Stage O/C Start 3ph","I>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_PH_A_START",296,"SW","PFSO","event_Protection","1st Stage O/C Start A ","I>1 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_PH_B_START",297,"SW","PFSO","event_Protection","1st Stage O/C Start B ","I>1 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_1_PH_C_START",298,"SW","PFSO","event_Protection","1st Stage O/C Start C ","I>1 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_3PH_START",299,"SW","PFSO","event_Protection","2nd Stage O/C Start 3ph","I>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_PH_A_START",300,"SW","PFSO","event_Protection","2nd Stage O/C Start A ","I>2 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_PH_B_START",301,"SW","PFSO","event_Protection","2nd Stage O/C Start B ","I>2 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_2_PH_C_START",302,"SW","PFSO","event_Protection","2nd Stage O/C Start C ","I>2 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_3PH_START",303,"SW","PFSO","event_Protection","3rd Stage O/C Start 3ph","I>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_PH_A_START",304,"SW","PFSO","event_Protection","3rd Stage O/C Start A ","I>3 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_PH_B_START",305,"SW","PFSO","event_Protection","3rd Stage O/C Start B","I>3 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_3_PH_C_START",306,"SW","PFSO","event_Protection","3rd Stage O/C Start C","I>3 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_3PH_START",307,"SW","PFSO","event_Protection","4th Stage O/C Start 3ph","I>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_PH_A_START",308,"SW","PFSO","event_Protection","4th Stage O/C Start A ","I>4 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_PH_B_START",309,"SW","PFSO","event_Protection","4th Stage O/C Start B ","I>4 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POC_4_PH_C_START",310,"SW","PFSO","event_Protection","4th Stage O/C Start C","I>4 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VCO_PH_AB_START",311,"SW","PFSO","event_Protection","Voltage Controlled O/C Start AB","VCO Start AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VCO_PH_BC_START",312,"SW","PFSO","event_Protection","Voltage Controlled O/C Start BC","VCO Start BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VCO_PH_CA_START",313,"SW","PFSO","event_Protection","Voltage Controlled O/C Start CA","VCO Start CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_314",314,"SW","UNUSED","NO_RESPONSE"]
["DDB_EF1_1_START",315,"SW","PFSO","event_Protection","1st Stage EF#1 Start","IN1>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_2_START",316,"SW","PFSO","event_Protection","2nd Stage EF#1 Start","IN1>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_3_START",317,"SW","PFSO","event_Protection","3rd Stage EF#1 Start","IN1>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_4_START",318,"SW","PFSO","event_Protection","4th Stage EF#1 Start","IN1>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_1_START",319,"SW","PFSO","event_Protection","1st Stage EF#2 Start","IN2>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_2_START",320,"SW","PFSO","event_Protection","2nd Stage EF#2 Start","IN2>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_3_START",321,"SW","PFSO","event_Protection","3rd Stage EF#2 Start","IN2>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_4_START",322,"SW","PFSO","event_Protection","4th Stage EF#2 Start","IN2>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_1_START",323,"SW","PFSO","event_Protection","1st Stage SEF Start","ISEF>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_2_START",324,"SW","PFSO","event_Protection","2nd Stage SEF Start","ISEF>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_3_START",325,"SW","PFSO","event_Protection","3rd Stage SEF Start","ISEF>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_4_START",326,"SW","PFSO","event_Protection","4th Stage SEF Start","ISEF>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESOV_1_START",327,"SW","PFSO","event_Protection","1st Stage Residual O/V Start","VN>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESOV_2_START",328,"SW","PFSO","event_Protection","2nd Stage Residual O/V Start","VN>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_THERMAL_ALARM",329,"SW","PFSO","event_Protection","Thermal Overload Alarm","Thermal Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NEGSEQOV_START",330,"SW","PFSO","event_Protection","Negative Sequence O/V Start","V2> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_3PH_START",331,"SW","PFSO","event_Protection","1st Stage Phase U/V Start 3ph","V<1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_PH_A_START",332,"SW","PFSO","event_Protection","1st Stage Phase U/V Start A/AB","V<1 Start A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_PH_B_START",333,"SW","PFSO","event_Protection","1st Stage Phase U/V Start B/BC","V<1 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_1_PH_C_START",334,"SW","PFSO","event_Protection","1st Stage Phase U/V Start C/CA","V<1 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_3PH_START",335,"SW","PFSO","event_Protection","2nd Stage Phase U/V Start 3ph","V<2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_PH_A_START",336,"SW","PFSO","event_Protection","2nd Stage Phase U/V Start A/AB","V<2 Start A/AB ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_PH_B_START",337,"SW","PFSO","event_Protection","2nd Stage Phase U/V Start B/BC","V<2 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PUV_2_PH_C_START",338,"SW","PFSO","event_Protection","2nd Stage Phase U/V Start C/CA","V<2 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_3PH_START",339,"SW","PFSO","event_Protection","1st Stage Phase O/V Start 3ph","V>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_PH_A_START",340,"SW","PFSO","event_Protection","1st Stage Phase O/V Start A/AB","V>1 Start A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_PH_B_START",341,"SW","PFSO","event_Protection","1st Stage Phase O/V Start B/BC","V>1 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_1_PH_C_START",342,"SW","PFSO","event_Protection","1st Stage Phase O/V Start C/CA","V>1 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_3PH_START",343,"SW","PFSO","event_Protection","2nd Stage Phase O/V Start 3ph","V>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_PH_A_START",344,"SW","PFSO","event_Protection","2nd Stage Phase O/V Start A/AB","V>2 Start A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_PH_B_START",345,"SW","PFSO","event_Protection","2nd Stage Phase O/V Start B/BC","V>2 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_POV_2_PH_C_START",346,"SW","PFSO","event_Protection","2nd Stage Phase O/V Start C/CA","V>2 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CLP_OPERATION",347,"SW","PFSO","event_Protection","Cold Load Pickup Operation","CLP Operation","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PH_BLOCKED_OC_START",348,"SW","PFSO","event_Protection","I> Blocked O/C Start","I> BlockStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_N_BLOCKED_OC_START",349,"SW","PFSO","event_Protection","IN/ISEF> Blocked O/C Start","IN/SEF>Blk Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_FAST_BLOCK",350,"SW","PFSO","NO_RESPONSE","VTS Fast Block","VTS Fast Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_SLOW_BLOCK",351,"SW","PFSO","NO_RESPONSE","VTS Slow Block","VTS Slow Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CTS_BLOCK",352,"SW","PFSO","NO_RESPONSE","CTS Block","CTS Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CBF1_TRIP_3PH",353,"SW","PFSO","event_Protection","tBF1 Trip 3Ph","Bfail1 Trip 3ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CBF2_TRIP_3PH",354,"SW","PFSO","event_Protection","tBF2 Trip 3Ph","Bfail2 Trip 3ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_TRIP",355,"SW","PFSO","event_Protection","Control Trip","Control Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_CLOSE",356,"SW","PFSO","event_Protection","Control Close","Control Close","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_CLOSE_IN_PROGRESS",357,"SW","PFSO","event_Protection","Control Close in Progress","Close in Prog","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_BLOCK_MAIN_PROTECTION",358,"SW","PFSO","event_Protection","AR Block Main Protection","Block Main Prot",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_BLOCK_SEF_PROTECTION",359,"SW","PFSO","event_Protection","AR Block SEF Protection","Block SEF Prot",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_3_POLE_IN_PROGRESS",360,"SW","PFSO","event_Protection","Autoreclose In Progress","AR In Progress",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_IN_SERVICE",361,"SW","PFSO","event_Protection","Autoreclose In/Out of service","AR In Service",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEQ_COUNT_0",362,"SW","PFSO","NO_RESPONSE","Seq Counter = 0","Seq Counter = 0",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEQ_COUNT_1",363,"SW","PFSO","event_Protection","Seq Counter = 1","Seq Counter = 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEQ_COUNT_2",364,"SW","PFSO","event_Protection","Seq Counter = 2","Seq Counter = 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEQ_COUNT_3",365,"SW","PFSO","event_Protection","Seq Counter = 3","Seq Counter = 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEQ_COUNT_4",366,"SW","PFSO","event_Protection","Seq Counter = 4","Seq Counter = 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_SUCCESSFUL_RECLOSE",367,"SW","PFSO","event_Protection","Successful Reclosure","Successful Close",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_DEAD_TIME_IN_PROGRESS",368,"SW","PFSO","event_Protection","Dead Time in Progress","Dead T in Prog",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_PROTECTION_LOCKOUT",369,"SW","PFSO","event_Protection","Protection Lockout of AR","Protection Lockt",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_RESET_LOCKOUT_ALARM",370,"SW","PFSO","event_Protection","AR Reset Lockout Alarm","Reset Lckout Alm",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AUTO_CLOSE",371,"SW","PFSO","event_Protection","Auto Close/ AR Close","Auto Close",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_TRIP_TEST",372,"SW","PFSO","event_Protection","Autoreclose trip test","AR Trip Test",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PHASE_A_UNDERCURRENT",373,"SW","PFSO","NO_RESPONSE","IA< operate","IA< Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PHASE_B_UNDERCURRENT",374,"SW","PFSO","NO_RESPONSE","IB< operate","IB< Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PHASE_C_UNDERCURRENT",375,"SW","PFSO","NO_RESPONSE","IC< operate","IC< Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF_UNDERCURRENT",376,"SW","PFSO","NO_RESPONSE","IN< operate","IN< Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_UNDERCURRENT",377,"SW","PFSO","NO_RESPONSE","ISEF< operate","ISEF< Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_OPEN",378,"SW","PFSO","event_Protection","3 ph CB Open","CB Open 3 ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_CLOSED",379,"SW","PFSO","event_Protection","3 ph CB Closed","CB Closed 3 ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ALL_POLEDEAD",380,"SW","PFSO","NO_RESPONSE","All Poles Dead","All Poles Dead","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ANY_POLEDEAD",381,"SW","PFSO","NO_RESPONSE","Any Pole Dead","Any Pole Dead","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PHASE_A_POLEDEAD",382,"SW","PFSO","NO_RESPONSE","Phase A Pole Dead","Pole Dead A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PHASE_B_POLEDEAD",383,"SW","PFSO","NO_RESPONSE","Phase B Pole Dead","Pole Dead B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PHASE_C_POLEDEAD",384,"SW","PFSO","NO_RESPONSE","Phase C Pole Dead","Pole Dead C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_ACCELERATE_INPUT",385,"FL","HIDDEN","NO_RESPONSE","Accelerate Ind","VTS Acc Ind","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_ANY_VOLTAGE_DEP_FN",386,"FL","HIDDEN","NO_RESPONSE","Any Voltage Dependent","VTS Volt Dep","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_IA_OPERATED",387,"SW","HIDDEN","NO_RESPONSE","Ia over threshold  ","VTS IA>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_IB_OPERATED",388,"SW","HIDDEN","NO_RESPONSE","Ib over threshold  ","VTS IB>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_IC_OPERATED",389,"SW","HIDDEN","NO_RESPONSE","Ic over threshold  ","VTS IC>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_VA_OPERATED",390,"SW","HIDDEN","NO_RESPONSE","Va over threshold  ","VTS VA>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_VB_OPERATED",391,"SW","HIDDEN","NO_RESPONSE","Vb over threshold  ","VTS VB>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_VC_OPERATED",392,"SW","HIDDEN","NO_RESPONSE","Vc over threshold  ","VTS VC>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_I2_OPERATED",393,"SW","HIDDEN","NO_RESPONSE","I2 over threshold  ","VTS I2>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_V2_OPERATED",394,"SW","HIDDEN","NO_RESPONSE","V2 over threshold  ","VTS V2>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_DELTA_IA_OPERATED",395,"SW","HIDDEN","NO_RESPONSE","Superimposed Ia over threshold  ","VTS IA delta>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_DELTA_IB_OPERATED",396,"SW","HIDDEN","NO_RESPONSE","Superimposed Ib over threshold  ","VTS IB delta>","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_VTS_DELTA_IC_OPERATED",397,"SW","HIDDEN","NO_RESPONSE","Superimposed Ic over threshold  ","VTS IC delta> ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CURRENT_PROT_SEF_TRIP",398,"FL","HIDDEN","NO_RESPONSE","CBF Current Prot SEF Trip","CBF SEF Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CBF_NON_CURRENT_PROT_TRIP",399,"FL","HIDDEN","NO_RESPONSE","CBF Non Current Prot Trip ","CBF Non I Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CBF_SEF_STAGE_TRIP",400,"FL","HIDDEN","NO_RESPONSE","Fixed Logic CBF SEF Stage Trip","CBF SEF Trip-1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CBF_NON_CURRENT_STAGE_TRIP",401,"FL","HIDDEN","NO_RESPONSE","Fixed Logic CBF Non Current Protection Stage Trip","CBF Non I Trip-1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYNC_CTRL_SYS_CHECK_OK",402,"PSL","PFSI","NO_RESPONSE","Control System Checks OK","Man Check Synch",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYNC_AR_SYS_CHECK_OK",403,"PSL","PFSI","NO_RESPONSE","AR System Checks OK","AR Sys Checks OK",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_LOCKOUT_ALARM",404,"SW","PFSO","NO_RESPONSE","Composite Lockout Alarm","Lockout Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_PRE_LOCKOUT",405,"SW","HIDDEN","NO_RESPONSE","Pre-Lockout","Pre-Lockout",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FREQ_ABOVE_RANGE_LIMIT",406,"SW","HIDDEN","NO_RESPONSE","Freq High","Freq High","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FREQ_BELOW_RANGE_LIMIT",407,"SW","HIDDEN","NO_RESPONSE","Freq Low","Freq Low","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FREQ_STOP_TRACK",408,"FL","HIDDEN","event_Protection","Stop Freq Track","Stop Freq Track","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF_START",409,"FL","HIDDEN","event_Protection","Composite EF Start","Start N","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FIELD_VOLTS_FAIL",410,"SW","PFSO","NO_RESPONSE","Field Voltage Failure","Field volts fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FREQ_NOT_FOUND",411,"SW","HIDDEN","NO_RESPONSE","Freq Not Found","Freq Not Found","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_1_TIMER_BLOCK",412,"PSL","PFSI","NO_RESPONSE","Block Underfrequency Stage 1 Timer","F<1 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_2_TIMER_BLOCK",413,"PSL","PFSI","NO_RESPONSE","Block Underfrequency Stage 2 Timer","F<2 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_3_TIMER_BLOCK",414,"PSL","PFSI","NO_RESPONSE","Block Underfrequency Stage 3 Timer","F<3 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_4_TIMER_BLOCK",415,"PSL","PFSI","NO_RESPONSE","Block Underfrequency Stage 4 Timer","F<4 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OFREQ_1_TIMER_BLOCK",416,"PSL","PFSI","NO_RESPONSE","Block Overfrequency Stage 1 Timer","F>1 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OFREQ_2_TIMER_BLOCK",417,"PSL","PFSI","NO_RESPONSE","Block Overfrequency Stage 2 Timer","F>2 Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_1_START",418,"SW","PFSO","event_Protection","Under frequency Stage 1 START","F<1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_2_START",419,"SW","PFSO","event_Protection","Under frequency Stage 2 START","F<2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_3_START",420,"SW","PFSO","event_Protection","Under frequency Stage 3 START","F<3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_4_START",421,"SW","PFSO","event_Protection","Under frequency Stage 4 START","F<4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OFREQ_1_START",422,"SW","PFSO","event_Protection","Over frequency Stage 1 START","F>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OFREQ_2_START",423,"SW","PFSO","event_Protection","Over frequency Stage 2 START","F>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_1_TRIP",424,"SW","PFSO","event_Protection","Under frequency Stage 1 trip","F<1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_2_TRIP",425,"SW","PFSO","event_Protection","Under frequency Stage 2 trip","F<2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_3_TRIP",426,"SW","PFSO","event_Protection","Under frequency Stage 3 trip","F<3 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UFREQ_4_TRIP",427,"SW","PFSO","event_Protection","Under frequency Stage 4 trip","F<4 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OFREQ_1_TRIP",428,"SW","PFSO","event_Protection","Over frequency Stage 1 Trip","F>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OFREQ_2_TRIP",429,"SW","PFSO","event_Protection","Over frequency Stage 2 Trip","F>2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_YN_TIMER_BLOCK",430,"PSL","PFSI","NO_RESPONSE","Block Overadmittance Timer","YN> Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GN_TIMER_BLOCK",431,"PSL","PFSI","NO_RESPONSE","Block Overconductance Timer","GN> Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BN_TIMER_BLOCK",432,"PSL","PFSI","NO_RESPONSE","Block Oversusceptance Timer","BN> Timer Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_YN_START",433,"SW","PFSO","event_Protection","Overadmittance Start","YN> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GN_START",434,"SW","PFSO","event_Protection","Overconductance Start","GN> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BN_START",435,"SW","PFSO","event_Protection","Oversusceptance Start","BN> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_YN_TRIP",436,"SW","PFSO","event_Protection","Overadmittance Trip","YN> Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GN_TRIP",437,"SW","PFSO","event_Protection","Overconductance Trip","GN> Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BN_TRIP",438,"SW","PFSO","event_Protection","Oversusceptance Trip","BN> Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXT_AR_PROT_TRIP",439,"PSL","PFSI","NO_RESPONSE","External Initiate AR Protection Trip","Ext AR Prot Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXT_AR_PROT_START",440,"PSL","PFSI","NO_RESPONSE","External Initiate AR Protection Start","Ext AR Prot Strt",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TEST_MODE",441,"PSL","PFSI","NO_RESPONSE","Initiate Test Mode","Test Mode","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_INHIBIT",442,"PSL","PFSI","NO_RESPONSE","Inhibit SEF","Inhibit SEF","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_LINE_LIVE",443,"SW","PFSO","NO_RESPONSE","Live Line","Live Line",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_LINE_DEAD",444,"SW","PFSO","NO_RESPONSE","Dead Line","Dead Line",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_BUS_LIVE",445,"SW","PFSO","NO_RESPONSE","Live Line","Live Bus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_BUS_DEAD",446,"SW","PFSO","NO_RESPONSE","Dead Line","Dead Bus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CHECKSYNC_1_OK",447,"SW","PFSO","NO_RESPONSE","Check Sync 1 OK","Check Sync 1 OK",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CHECKSYNC_2_OK",448,"SW","PFSO","NO_RESPONSE","Check Sync 2 OK","Check Sync 2 OK",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_INACTIVE",449,"SW","PFSO","NO_RESPONSE","SysChks Inactive","SysChks Inactive",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CHECKSYNC_1_ENABLED",450,"PSL","PFSI","NO_RESPONSE","CS1 Enabled","CS1 Enabled",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CHECKSYNC_2_ENABLED",451,"PSL","PFSI","NO_RESPONSE","CS2 Enabled","CS2 Enabled",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSTEM_SPLIT_ENABLED",452,"PSL","PFSI","NO_RESPONSE","SysSplit Enabled","SysSplit Enabled",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_DAR_COMPLETE",453,"PSL","PFSI","NO_RESPONSE","DAR Complete","DAR Complete",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CB_IN_SERVICE",454,"PSL","PFSI","NO_RESPONSE","CB in Service","CB in Service",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_RESTART",455,"PSL","PFSI","NO_RESPONSE","AR Restart","AR Restart",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_IP_1",456,"SW","PFSO","NO_RESPONSE","AR In Progress 1","AR In Progress 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_DEADTIME_ENABLE",457,"PSL","PFSI","NO_RESPONSE","DeadTime Enabled","DeadTime Enabled",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_DEADTIME_OK_TO_START",458,"PSL","PFSI","NO_RESPONSE","DT OK To Start","DT OK To Start",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_DEADTIME_COMPLETE",459,"SW","PFSO","NO_RESPONSE","DT Complete","DT Complete",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ARCHECKS_IN_PROGRESS",460,"SW","PFSO","NO_RESPONSE","Reclose Checks In Progress","Reclose Checks",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_LIVEDEAD_CCTS_OK",461,"PSL","PFSI","NO_RESPONSE","Live/Dead Circuits OK","Circuits OK",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_SYNC_CHECK",462,"SW","PFSO","NO_RESPONSE","AR Sync Check","AR Sync Check",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_SYSTEMCHECKS_OK",463,"SW","PFSO","NO_RESPONSE","AR SysChecks OK","AR SysChecks OK",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INIT_AR_TRIP_TEST",464,"PSL","PFSI","NO_RESPONSE","AR Init TripTest","AR Init TripTest",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_MONITOR_BLOCKING ",465,"PSL","PFSI","ddbRF_103MonitorBlck","Monitor Block","103 MonitorBlock","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_COMMAND_BLOCKING",466,"PSL","PFSI","ddbRF_103CommandBlck","Command Block","103 CommandBlock","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_1_START_2",467,"SW","PFSO","event_Protection","1st Stage SEF Start 2","ISEF>1 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_2_START_2",468,"SW","PFSO","event_Protection","2nd Stage SEF Start 2","ISEF>2 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_3_START_2",469,"SW","PFSO","event_Protection","3rd Stage SEF Start 2","ISEF>3 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SEF_4_START_2",470,"SW","PFSO","event_Protection","4th Stage SEF Start 2","ISEF>4 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS1_SLIP_ABOVE_SETTING",471,"SW","PFSO","event_Protection","Check Synch 1 Slip > Setting","CS1 Slipfreq>",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS1_SLIP_BELOW_SETTING",472,"SW","PFSO","NO_RESPONSE","Check Synch 1 Slip < Setting","CS1 Slipfreq<",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS2_SLIP_ABOVE_SETTING",473,"SW","PFSO","event_Protection","Check Synch 2 Slip > Setting","CS2 Slipfreq>",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS2_SLIP_BELOW_SETTING",474,"SW","PFSO","NO_RESPONSE","Check Synch 2 Slip < Setting","CS2 Slipfreq<",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TIME_SYNCH",475,"PSL","PFSI","event_TimeSync","Perform basic time synchronisation","Time Synch","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_476",476,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_477",477,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_478",478,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_479",479,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_480",480,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_481",481,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_482",482,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_483",483,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_484",484,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_485",485,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_486",486,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_487",487,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_488",488,"SW","UNUSED","NO_RESPONSE"]
["DDB_SYSCHECKS_VLINE_UV",489,"SW","PFSO","NO_RESPONSE","Line volts less than CS undervoltage setting","CS Vline<",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_VBUS_UV",490,"SW","PFSO","NO_RESPONSE","Bus volts less than CS undervoltage setting","CS Vbus<",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_VLINE_OV",491,"SW","PFSO","NO_RESPONSE","Line volts greater than CS overvoltage setting","CS Vline>",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_VBUS_OV",492,"SW","PFSO","NO_RESPONSE","Bus volts greater than CS overvoltage setting","CS Vbus>",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_VLINE_DIFF_HIGH",493,"SW","PFSO","NO_RESPONSE","Line volts greater than (bus volts + CS diff voltage setting)","CS Vline>Vbus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_VBUS_DIFF_HIGH",494,"SW","PFSO","NO_RESPONSE","Bus volts greater than (line volts + CS diff voltage setting)","CS Vline<Vbus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS1_LINE_FREQ_GT_BUS_FREQ",495,"SW","PFSO","NO_RESPONSE","Line freq greater than (bus freq + CS1 slip freq setting)","CS1 Fline>Fbus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS1_LINE_FREQ_LT_BUS_FREQ",496,"SW","PFSO","NO_RESPONSE","Bus freq greater than (line freq + CS1 slip freq setting)","CS1 Fline<Fbus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS1_ANG_NOT_OK_POS",497,"SW","PFSO","NO_RESPONSE","Line angle in range (CS1 ang setting to +180 deg)","CS1 Ang Not OK +",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS1_ANG_NOT_OK_NEG",498,"SW","PFSO","NO_RESPONSE","Line angle in range (-CS1 ang setting to -180 deg)","CS1 Ang Not OK -",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXTERNAL_TRIP_A",499,"PSL","PFSI","NO_RESPONSE","External A Phase Trip initiates CB Fail","External Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXTERNAL_TRIP_B",500,"PSL","PFSI","NO_RESPONSE","External B Phase Trip initiates CB Fail","External Trip B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXTERNAL_TRIP_C",501,"PSL","PFSI","NO_RESPONSE","External C Phase Trip initiates CB Fail","External Trip C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXTERNAL_TRIP_EF",502,"PSL","PFSI","NO_RESPONSE","External EF Trip initiates CB Fail","External Trip EF","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EXTERNAL_TRIP_SEF",503,"PSL","PFSI","NO_RESPONSE","External SEF Trip initiates CB Fail","External TripSEF","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_INHIBIT",504,"PSL","PFSI","NO_RESPONSE","Inhibit I2> protection","I2> Inhibit","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_1_TIMER_BLOCK",505,"PSL","PFSI","NO_RESPONSE","Block I2> Stage 1 Timer","I2>1 Tmr Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_2_TIMER_BLOCK",506,"PSL","PFSI","NO_RESPONSE","Block I2> Stage 2 Timer","I2>2 Tmr Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_3_TIMER_BLOCK",507,"PSL","PFSI","NO_RESPONSE","Block I2> Stage 3 Timer","I2>3 Tmr Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_4_TIMER_BLOCK",508,"PSL","PFSI","NO_RESPONSE","Block I2> Stage 4 Timer","I2>4 Tmr Blk","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_1_START",509,"SW","PFSO","event_Protection","I2> Stage 1 Start","I2>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_2_START",510,"SW","PFSO","event_Protection","I2> Stage 2 Start","I2>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_3_START",511,"SW","PFSO","event_Protection","I2> Stage 3 Start","I2>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_4_START",512,"SW","PFSO","event_Protection","I2> Stage 4 Start","I2>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_1_TRIP",513,"SW","PFSO","event_Protection","I2> Stage 1 Trip","I2>1 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_2_TRIP",514,"SW","PFSO","event_Protection","I2> Stage 2 Trip","I2>2 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_3_TRIP",515,"SW","PFSO","event_Protection","I2> Stage 3 Trip","I2>3 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NPSOC_4_TRIP",516,"SW","PFSO","event_Protection","I2> Stage 4 Trip","I2>4 Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ACCELERATE_NPSOV",517,"PSL","PFSI","NO_RESPONSE","Accelerate V2>","V2> Accelerate","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRIP_LED_TRIGGER",518,"PSL","PFSI","NO_RESPONSE","Trip LED Trigger","Trip LED Trigger","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS2_LINE_FREQ_GT_BUS_FREQ",519,"SW","PFSO","NO_RESPONSE","Line freq greater than (bus freq + CS2 slip freq setting)","CS2 Fline>Fbus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS2_LINE_FREQ_LT_BUS_FREQ",520,"SW","PFSO","NO_RESPONSE","Bus freq greater than (line freq + CS2 slip freq setting)","CS2 Fline<Fbus",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS2_ANG_NOT_OK_POS",521,"SW","PFSO","NO_RESPONSE","Line angle in range (CS2 angle setting to +180 deg)","CS2 Ang Not OK +",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CS2_ANG_NOT_OK_NEG",522,"SW","PFSO","NO_RESPONSE","Line angle in range (-CS2 angle setting to -180 deg)","CS2 Ang Not OK -",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_ANG_ACW",523,"SW","PFSO","NO_RESPONSE","Line/Bus phase angle is rotating anti-clockwise","CS Ang Rot ACW",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SYSCHECKS_ANG_CW",524,"SW","PFSO","NO_RESPONSE","Line/Bus phase angle is rotating clockwise","CS Ang Rot CW",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BLOCK_REMOTE_CB_OPS",525,"PSL","PFSI","NO_RESPONSE","Blocks remote CB Trip/Close commands when asserted","Blk Rmt. CB Ops","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SG_SELECTOR_X1",526,"PSL","PFSI","NO_RESPONSE","Binary coded setting group selector 1","SG Select x1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SG_SELECTOR_1X",527,"PSL","PFSI","NO_RESPONSE","Binary coded setting group selector 2","SG Select 1x","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF1_INHIBIT",528,"PSL","PFSI","NO_RESPONSE","Inhibit IN1> (Earth Fault 1) protection","IN1> Inhibit","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_EF2_INHIBIT",529,"PSL","PFSI","NO_RESPONSE","Inhibit IN2> (Earth Fault 2) protection","IN2> Inhibit","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_SKIP_SHOT_1",530,"PSL","PFSI","NO_RESPONSE","Forces AR to skip shot 1 of a reclose sequence","AR Skip Shot 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_LOGIC_0",531,"SW","PFSO","NO_RESPONSE","Logic 0 for use in PSL (Never changes state!)","Logic 0 Ref.","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_INHIBIT_RECLAIM_TIME",532,"PSL","PFSI","NO_RESPONSE","Inhibit AR Reclaim Timer","Inh Reclaim Time",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_RECLAIM_IN_PROGRESS",533,"SW","PFSO","NO_RESPONSE","AR Reclaim Time In Progress","Reclaim In Prog",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_AR_RECLAIM_TIME_COMPLETE",534,"SW","PFSO","NO_RESPONSE","AR Reclaim Time Complete","Reclaim Complete",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BROKEN_CONDUCTOR_START",535,"SW","PFSO","event_Protection","Broken Conductor Start","BrokenLine Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ANY_TRIP",536,"PSL","PFSI","event_Protection","Trip Command initiated by DDB_TRIP_INITIATE","Trip Command In","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRIP_INITIATE",537,"FL","PFSO","NO_RESPONSE","Initiate Trip","Trip Command Out","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_2ND_HARMONIC_IA",538,"SW","PFSO","event_Protection","2nd Harmonic over threshold in IA","IA2H Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_2ND_HARMONIC_IB",539,"SW","PFSO","event_Protection","2nd Harmonic over threshold in IB","IB2H Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_2ND_HARMONIC_IC",540,"SW","PFSO","event_Protection","2nd Harmonic over threshold in IC","IC2H Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_2ND_HARMONIC",541,"SW","PFSO","event_Protection","2nd Harmonic over threshold in any of IA, IB or IC","I2H Any Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RP1_READ_ONLY",542,"PSL","PFSI","ddbRF_ReadOnly_RP1","Remote Read Only 1 DDB","RP1 Read Only","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RP2_READ_ONLY",543,"PSL","PFSI","ddbRF_ReadOnly_RP2","Remote Read Only 2 DDB","RP2 Read Only","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NIC_READ_ONLY",544,"PSL","PFSI","ddbRF_ReadOnly_NIC","Remote Read Only NIC DDB","NIC Read Only","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_545",545,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_546",546,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_547",547,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_548",548,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_549",549,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_550",550,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_551",551,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_552",552,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_553",553,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_554",554,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_555",555,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_556",556,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_557",557,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_558",558,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_559",559,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_560",560,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_561",561,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_562",562,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_563",563,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_564",564,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_565",565,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_566",566,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_567",567,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_568",568,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_569",569,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_570",570,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_571",571,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_572",572,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_573",573,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_574",574,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_575",575,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_576",576,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_577",577,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_578",578,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_579",579,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_580",580,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_581",581,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_582",582,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_583",583,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_584",584,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_585",585,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_586",586,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_587",587,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_588",588,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_589",589,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_590",590,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_591",591,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_592",592,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_593",593,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_594",594,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_595",595,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_596",596,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_597",597,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_598",598,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_599",599,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_600",600,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_601",601,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_602",602,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_603",603,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_604",604,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_605",605,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_606",606,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_607",607,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_608",608,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_609",609,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_610",610,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_611",611,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_612",612,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_613",613,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_614",614,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_615",615,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_616",616,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_617",617,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_618",618,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_619",619,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_620",620,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_621",621,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_622",622,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_623",623,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_624",624,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_625",625,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_626",626,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_627",627,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_628",628,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_629",629,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_630",630,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_631",631,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_632",632,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_633",633,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_634",634,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_635",635,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_636",636,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_637",637,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_638",638,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_639",639,"SW","UNUSED","NO_RESPONSE"]
["DDB_OUTPUT_TRI_LED_1_RED",640,"SW","TRI_LED","NO_RESPONSE",null,"LED1 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_1_GRN",641,"SW","TRI_LED","NO_RESPONSE",null,"LED1 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_2_RED",642,"SW","TRI_LED","NO_RESPONSE",null,"LED2 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_2_GRN",643,"SW","TRI_LED","NO_RESPONSE",null,"LED2 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_3_RED",644,"SW","TRI_LED","NO_RESPONSE",null,"LED3 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_3_GRN",645,"SW","TRI_LED","NO_RESPONSE",null,"LED3 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_4_RED",646,"SW","TRI_LED","NO_RESPONSE",null,"LED4 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_4_GRN",647,"SW","TRI_LED","NO_RESPONSE",null,"LED4 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_5_RED",648,"SW","TRI_LED","NO_RESPONSE",null,"LED5 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_5_GRN",649,"SW","TRI_LED","NO_RESPONSE",null,"LED5 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_6_RED",650,"SW","TRI_LED","NO_RESPONSE",null,"LED6 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_6_GRN",651,"SW","TRI_LED","NO_RESPONSE",null,"LED6 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_7_RED",652,"SW","TRI_LED","NO_RESPONSE",null,"LED7 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_7_GRN",653,"SW","TRI_LED","NO_RESPONSE",null,"LED7 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_8_RED",654,"SW","TRI_LED","NO_RESPONSE",null,"LED8 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_8_GRN",655,"SW","TRI_LED","NO_RESPONSE",null,"LED8 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_9_RED",656,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED1 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_9_GRN",657,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED1 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_10_RED",658,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED2 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_10_GRN",659,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED2 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_11_RED",660,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED3 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_11_GRN",661,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED3 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_12_RED",662,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED4 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_12_GRN",663,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED4 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_13_RED",664,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED5 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_13_GRN",665,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED5 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_14_RED",666,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED6 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_14_GRN",667,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED6 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_15_RED",668,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED7 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_15_GRN",669,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED7 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_16_RED",670,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED8 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_16_GRN",671,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED8 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_17_RED",672,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED9 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_17_GRN",673,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED9 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_18_RED",674,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED10 Red",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OUTPUT_TRI_LED_18_GRN",675,"SW","TRI_LED","NO_RESPONSE",null,"FnKey LED10 Grn",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_1",676,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED1 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_1",677,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED1 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_2",678,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED2 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_2",679,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED2 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_3",680,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED3 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_3",681,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED3 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_4",682,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED4 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_4",683,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED4 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_5",684,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED5 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_5",685,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED5 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_6",686,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED6 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_6",687,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED6 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_7",688,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED7 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_7",689,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED7 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_8",690,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED8 Con R",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_8",691,"PSL","TRI_LED_CON","NO_RESPONSE",null,"LED8 Con G",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_9",692,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED1 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_9",693,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED1 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_10",694,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED2 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_10",695,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED2 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_11",696,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED3 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_11",697,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED3 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_12",698,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED4 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_12",699,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED4 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_13",700,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED5 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_13",701,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED5 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_14",702,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED6 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_14",703,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED6 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_15",704,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED7 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_15",705,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED7 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_16",706,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED8 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_16",707,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED8 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_17",708,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED9 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_17",709,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED9 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_RED_CON_18",710,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED10 ConR",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_TRI_LED_GRN_CON_18",711,"PSL","TRI_LED_CON","NO_RESPONSE",null,"FnKey LED10 ConG",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_1",712,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 1",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_2",713,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 2",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_3",714,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 3",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_4",715,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 4",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_5",716,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 5",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_6",717,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 6",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_7",718,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 7",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_8",719,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 8",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_9",720,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 9",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_FN_KEY_10",721,"SW","FUNCTION_KEY","event_Protection",null,"Function Key 10",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_3PH_START",722,"SW","PFSO","event_Protection",null,"Power>1 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_A_PH_START",723,"SW","PFSO","event_Protection",null,"Power>1 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_B_PH_START",724,"SW","PFSO","event_Protection",null,"Power>1 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_C_PH_START",725,"SW","PFSO","event_Protection",null,"Power>1 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_3PH_START",726,"SW","PFSO","event_Protection",null,"Power>2 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_A_PH_START",727,"SW","PFSO","event_Protection",null,"Power>2 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_B_PH_START",728,"SW","PFSO","event_Protection",null,"Power>2 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_C_PH_START",729,"SW","PFSO","event_Protection",null,"Power>2 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_3PH_START",730,"SW","PFSO","event_Protection",null,"Power<1 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_A_PH_START",731,"SW","PFSO","event_Protection",null,"Power<1 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_B_PH_START",732,"SW","PFSO","event_Protection",null,"Power<1 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_C_PH_START",733,"SW","PFSO","event_Protection",null,"Power<1 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_3PH_START",734,"SW","PFSO","event_Protection",null,"Power<2 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_A_PH_START",735,"SW","PFSO","event_Protection",null,"Power<2 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_B_PH_START",736,"SW","PFSO","event_Protection",null,"Power<2 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_C_PH_START",737,"SW","PFSO","event_Protection",null,"Power<2 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_3PH_TRIP",738,"SW","PFSO","event_Protection",null,"Power>1 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_A_PH_TRIP",739,"SW","PFSO","event_Protection",null,"Power>1 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_B_PH_TRIP",740,"SW","PFSO","event_Protection",null,"Power>1 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_C_PH_TRIP",741,"SW","PFSO","event_Protection",null,"Power>1 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_3PH_TRIP",742,"SW","PFSO","event_Protection",null,"Power>2 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_A_PH_TRIP",743,"SW","PFSO","event_Protection",null,"Power>2 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_B_PH_TRIP",744,"SW","PFSO","event_Protection",null,"Power>2 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_C_PH_TRIP",745,"SW","PFSO","event_Protection",null,"Power>2 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_3PH_TRIP",746,"SW","PFSO","event_Protection",null,"Power<1 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_A_PH_TRIP",747,"SW","PFSO","event_Protection",null,"Power<1 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_B_PH_TRIP",748,"SW","PFSO","event_Protection",null,"Power<1 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_C_PH_TRIP",749,"SW","PFSO","event_Protection",null,"Power<1 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_3PH_TRIP",750,"SW","PFSO","event_Protection",null,"Power<2 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_A_PH_TRIP",751,"SW","PFSO","event_Protection",null,"Power<2 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_B_PH_TRIP",752,"SW","PFSO","event_Protection",null,"Power<2 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_C_PH_TRIP",753,"SW","PFSO","event_Protection",null,"Power<2 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_1_BLOCK",754,"PSL","PFSI","event_Protection",null,"Power>1 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_OVER_POWER_2_BLOCK",755,"PSL","PFSI","event_Protection",null,"Power>2 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_1_BLOCK",756,"PSL","PFSI","event_Protection",null,"Power<1 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNDER_POWER_2_BLOCK",757,"PSL","PFSI","event_Protection",null,"Power<2 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SPOWER_1_START",758,"SW","PFSO","event_Protection","Sensitive A Phase Power Stage 1 Start","SensP1 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SPOWER_2_START",759,"SW","PFSO","event_Protection","Sensitive A Phase Power Stage 2 Start","SensP2 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SPOWER_1_TRIP",760,"SW","PFSO","event_Protection","Sensitive A Phase Power Stage 1 Trip","SensP1 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SPOWER_2_TRIP",761,"SW","PFSO","event_Protection","Sensitive A Phase Power Stage 2 Trip","SensP2 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_762",762,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_763",763,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_764",764,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_765",765,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_766",766,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_767",767,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_768",768,"SW","UNUSED","NO_RESPONSE"]
["DDB_BATTERY_FAIL_ALARM",769,"SW","PFSO","NO_RESPONSE","Battery Failure Alarm","Battery Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_REAR_COMMS_FAIL",770,"SW","PFSO","NO_RESPONSE","Rear Comms Failed","Rear Comms Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSE_MISSING_IED_ALARM",771,"SW","PFSO","NO_RESPONSE","GOOSE IED Absent Alarm","GOOSE IED Absent","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_ECARD_NOT_FITTED_ALARM",772,"SW","PFSO","NO_RESPONSE","Ethernet card not fitted Alarm","NIC Not Fitted","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NIC_NOT_RESPONDING_ALARM",773,"SW","PFSO","NO_RESPONSE","Ethernet card not responding Alarm","NIC No Response","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NIC_FATAL_ERROR_ALARM",774,"SW","PFSO","NO_RESPONSE","Ethernet card fatal error Alarm","NIC Fatal Error","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NIC_SOFTWARE_RELOAD_ALARM",775,"SW","PFSO","NO_RESPONSE","Ethernet card software reload Alarm","NIC Soft. Reload","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INVALID_TCP_IP_CONFIG_ALARM",776,"SW","PFSO","NO_RESPONSE","Bad TCP/IP Configuration Alarm","Bad TCP/IP Cfg.","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INVALID_OSI_CONFIG_ALARM",777,"SW","PFSO","NO_RESPONSE","Bad OSI Configuration Alarm","Bad OSI Config.","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_NIC_LINK_FAIL_ALARM",778,"SW","PFSO","NO_RESPONSE","Ethernet card network link failure Alarm","NIC Link Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_SW_MISMATCH_ALARM",779,"SW","PFSO","NO_RESPONSE","Main card/Ethernet card software mismatch Alarm","NIC SW Mis-Match","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_IP_ADDRESS_CONFLICT_ALARM",780,"SW","PFSO","NO_RESPONSE","IP Address conflict Alarm","IP Addr Conflict","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERMICOM_LOOPBACK_ALARM",781,"SW","PFSO","NO_RESPONSE","InterMiCOM Loopback Fail","IM Loopback","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERMICOM_MESSAGE_ALARM",782,"SW","PFSO","NO_RESPONSE","InterMiCOM Message Fail","IM Msg Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERMICOM_DCD_ALARM",783,"SW","PFSO","NO_RESPONSE","InterMiCOM Data CD Fail","IM DCD Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERMICOM_CHANNEL_ALARM",784,"SW","PFSO","NO_RESPONSE","InterMiCOM Channel Fail","IM Chan Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_BACKUP_SETTINGS_ALARM",785,"SW","PFSO","NO_RESPONSE","Backup settings in use' Alarm","Backup Setting","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_786",786,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_787",787,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_788",788,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_789",789,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_790",790,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_791",791,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_792",792,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_793",793,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_794",794,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_795",795,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_796",796,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_797",797,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_798",798,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_799",799,"SW","UNUSED","NO_RESPONSE"]
["DDB_CONTROL_1",800,"SW","CONTROL","event_Protection","Control Input 1","See [29 01]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_2",801,"SW","CONTROL","event_Protection","Control Input 2","See [29 02]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_3",802,"SW","CONTROL","event_Protection","Control Input 3","See [29 03]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_4",803,"SW","CONTROL","event_Protection","Control Input 4","See [29 04]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_5",804,"SW","CONTROL","event_Protection","Control Input 5","See [29 05]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_6",805,"SW","CONTROL","event_Protection","Control Input 6","See [29 06]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_7",806,"SW","CONTROL","event_Protection","Control Input 7","See [29 07]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_8",807,"SW","CONTROL","event_Protection","Control Input 8","See [29 08]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_9",808,"SW","CONTROL","event_Protection","Control Input 9","See [29 09]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_10",809,"SW","CONTROL","event_Protection","Control Input 10","See [29 0A]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_11",810,"SW","CONTROL","event_Protection","Control Input 11","See [29 0B]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_12",811,"SW","CONTROL","event_Protection","Control Input 12","See [29 0C]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_13",812,"SW","CONTROL","event_Protection","Control Input 13","See [29 0D]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_14",813,"SW","CONTROL","event_Protection","Control Input 14","See [29 0E]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_15",814,"SW","CONTROL","event_Protection","Control Input 15","See [29 0F]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_16",815,"SW","CONTROL","event_Protection","Control Input 16","See [29 10]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_17",816,"SW","CONTROL","event_Protection","Control Input 17","See [29 11]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_18",817,"SW","CONTROL","event_Protection","Control Input 18","See [29 12]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_19",818,"SW","CONTROL","event_Protection","Control Input 19","See [29 13]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_20",819,"SW","CONTROL","event_Protection","Control Input 20","See [29 14]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_21",820,"SW","CONTROL","event_Protection","Control Input 21","See [29 15]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_22",821,"SW","CONTROL","event_Protection","Control Input 22","See [29 16]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_23",822,"SW","CONTROL","event_Protection","Control Input 23","See [29 17]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_24",823,"SW","CONTROL","event_Protection","Control Input 24","See [29 18]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_25",824,"SW","CONTROL","event_Protection","Control Input 25","See [29 19]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_26",825,"SW","CONTROL","event_Protection","Control Input 26","See [29 1A]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_27",826,"SW","CONTROL","event_Protection","Control Input 27","See [29 1B]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_28",827,"SW","CONTROL","event_Protection","Control Input 28","See [29 1C]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_29",828,"SW","CONTROL","event_Protection","Control Input 29","See [29 1D]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_30",829,"SW","CONTROL","event_Protection","Control Input 30","See [29 1E]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_31",830,"SW","CONTROL","event_Protection","Control Input 31","See [29 1F]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_CONTROL_32",831,"SW","CONTROL","event_Protection","Control Input 32","See [29 20]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_1",832,"SW","GOOSEIN","event_Protection",null,"Virtual Input 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_2",833,"SW","GOOSEIN","event_Protection",null,"Virtual Input 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_3",834,"SW","GOOSEIN","event_Protection",null,"Virtual Input 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_4",835,"SW","GOOSEIN","event_Protection",null,"Virtual Input 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_5",836,"SW","GOOSEIN","event_Protection",null,"Virtual Input 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_6",837,"SW","GOOSEIN","event_Protection",null,"Virtual Input 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_7",838,"SW","GOOSEIN","event_Protection",null,"Virtual Input 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_8",839,"SW","GOOSEIN","event_Protection",null,"Virtual Input 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_9",840,"SW","GOOSEIN","event_Protection",null,"Virtual Input 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_10",841,"SW","GOOSEIN","event_Protection",null,"Virtual Input 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_11",842,"SW","GOOSEIN","event_Protection",null,"Virtual Input 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_12",843,"SW","GOOSEIN","event_Protection",null,"Virtual Input 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_13",844,"SW","GOOSEIN","event_Protection",null,"Virtual Input 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_14",845,"SW","GOOSEIN","event_Protection",null,"Virtual Input 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_15",846,"SW","GOOSEIN","event_Protection",null,"Virtual Input 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_16",847,"SW","GOOSEIN","event_Protection",null,"Virtual Input 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_17",848,"SW","GOOSEIN","event_Protection",null,"Virtual Input 17","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_18",849,"SW","GOOSEIN","event_Protection",null,"Virtual Input 18","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_19",850,"SW","GOOSEIN","event_Protection",null,"Virtual Input 19","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_20",851,"SW","GOOSEIN","event_Protection",null,"Virtual Input 20","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_21",852,"SW","GOOSEIN","event_Protection",null,"Virtual Input 21","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_22",853,"SW","GOOSEIN","event_Protection",null,"Virtual Input 22","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_23",854,"SW","GOOSEIN","event_Protection",null,"Virtual Input 23","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_24",855,"SW","GOOSEIN","event_Protection",null,"Virtual Input 24","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_25",856,"SW","GOOSEIN","event_Protection",null,"Virtual Input 25","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_26",857,"SW","GOOSEIN","event_Protection",null,"Virtual Input 26","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_27",858,"SW","GOOSEIN","event_Protection",null,"Virtual Input 27","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_28",859,"SW","GOOSEIN","event_Protection",null,"Virtual Input 28","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_29",860,"SW","GOOSEIN","event_Protection",null,"Virtual Input 29","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_30",861,"SW","GOOSEIN","event_Protection",null,"Virtual Input 30","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_31",862,"SW","GOOSEIN","event_Protection",null,"Virtual Input 31","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_32",863,"SW","GOOSEIN","event_Protection",null,"Virtual Input 32","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_GOOSEIN_33",864,"SW","GOOSEIN","event_Protection",null,"Virtual Input 33",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_34",865,"SW","GOOSEIN","event_Protection",null,"Virtual Input 34",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_35",866,"SW","GOOSEIN","event_Protection",null,"Virtual Input 35",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_36",867,"SW","GOOSEIN","event_Protection",null,"Virtual Input 36",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_37",868,"SW","GOOSEIN","event_Protection",null,"Virtual Input 37",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_38",869,"SW","GOOSEIN","event_Protection",null,"Virtual Input 38",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_39",870,"SW","GOOSEIN","event_Protection",null,"Virtual Input 39",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_40",871,"SW","GOOSEIN","event_Protection",null,"Virtual Input 40",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_41",872,"SW","GOOSEIN","event_Protection",null,"Virtual Input 41",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_42",873,"SW","GOOSEIN","event_Protection",null,"Virtual Input 42",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_43",874,"SW","GOOSEIN","event_Protection",null,"Virtual Input 43",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_44",875,"SW","GOOSEIN","event_Protection",null,"Virtual Input 44",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_45",876,"SW","GOOSEIN","event_Protection",null,"Virtual Input 45",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_46",877,"SW","GOOSEIN","event_Protection",null,"Virtual Input 46",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_47",878,"SW","GOOSEIN","event_Protection",null,"Virtual Input 47",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_48",879,"SW","GOOSEIN","event_Protection",null,"Virtual Input 48",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_49",880,"SW","GOOSEIN","event_Protection",null,"Virtual Input 49",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_50",881,"SW","GOOSEIN","event_Protection",null,"Virtual Input 50",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_51",882,"SW","GOOSEIN","event_Protection",null,"Virtual Input 51",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_52",883,"SW","GOOSEIN","event_Protection",null,"Virtual Input 52",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_53",884,"SW","GOOSEIN","event_Protection",null,"Virtual Input 53",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_54",885,"SW","GOOSEIN","event_Protection",null,"Virtual Input 54",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_55",886,"SW","GOOSEIN","event_Protection",null,"Virtual Input 55",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_56",887,"SW","GOOSEIN","event_Protection",null,"Virtual Input 56",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_57",888,"SW","GOOSEIN","event_Protection",null,"Virtual Input 57",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_58",889,"SW","GOOSEIN","event_Protection",null,"Virtual Input 58",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_59",890,"SW","GOOSEIN","event_Protection",null,"Virtual Input 59",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_60",891,"SW","GOOSEIN","event_Protection",null,"Virtual Input 60",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_61",892,"SW","GOOSEIN","event_Protection",null,"Virtual Input 61",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_62",893,"SW","GOOSEIN","event_Protection",null,"Virtual Input 62",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_63",894,"SW","GOOSEIN","event_Protection",null,"Virtual Input 63",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEIN_64",895,"SW","GOOSEIN","event_Protection",null,"Virtual Input 64",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_INTERIN_1",896,"SW","INTERIN","event_Protection","InterMiCOM in 1","InterMiCOM in 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERIN_2",897,"SW","INTERIN","event_Protection","InterMiCOM in 2","InterMiCOM in 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERIN_3",898,"SW","INTERIN","event_Protection","InterMiCOM in 3","InterMiCOM in 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERIN_4",899,"SW","INTERIN","event_Protection","InterMiCOM in 4","InterMiCOM in 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERIN_5",900,"SW","INTERIN","event_Protection","InterMiCOM in 5","InterMiCOM in 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERIN_6",901,"SW","INTERIN","event_Protection","InterMiCOM in 6","InterMiCOM in 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERIN_7",902,"SW","INTERIN","event_Protection","InterMiCOM in 7","InterMiCOM in 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTERIN_8",903,"SW","INTERIN","event_Protection","InterMiCOM in 8","InterMiCOM in 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_1",904,"PSL","INTEROUT","event_Protection","InterMiCOM out 1","InterMiCOM out 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_2",905,"PSL","INTEROUT","event_Protection","InterMiCOM out 2","InterMiCOM out 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_3",906,"PSL","INTEROUT","event_Protection","InterMiCOM out 3","InterMiCOM out 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_4",907,"PSL","INTEROUT","event_Protection","InterMiCOM out 4","InterMiCOM out 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_5",908,"PSL","INTEROUT","event_Protection","InterMiCOM out 5","InterMiCOM out 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_6",909,"PSL","INTEROUT","event_Protection","InterMiCOM out 6","InterMiCOM out 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_7",910,"PSL","INTEROUT","event_Protection","InterMiCOM out 7","InterMiCOM out 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_INTEROUT_8",911,"PSL","INTEROUT","event_Protection","InterMiCOM out 8","InterMiCOM out 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_912",912,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_913",913,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_914",914,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_915",915,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_916",916,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_917",917,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_918",918,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_919",919,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_920",920,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_921",921,"SW","UNUSED","NO_RESPONSE"]
["DDB_RESERVED_DISTREC",922,"SW","UNUSED","NO_RESPONSE","Provides the \"Unused\" selection in G32",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_1",923,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 001","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_2",924,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 002","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_3",925,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 003","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_4",926,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 004","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_5",927,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 005","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_6",928,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 006","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_7",929,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 007","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_8",930,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 008","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_9",931,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 009","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_10",932,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 010","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_11",933,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 011","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_12",934,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 012","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_13",935,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 013","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_14",936,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 014","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_15",937,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 015","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_16",938,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 016","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_17",939,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 017","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_18",940,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 018","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_19",941,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 019","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_20",942,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 020","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_21",943,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 021","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_22",944,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 022","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_23",945,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 023","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_24",946,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 024","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_25",947,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 025","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_26",948,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 026","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_27",949,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 027","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_28",950,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 028","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_29",951,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 029","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_30",952,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 030","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_31",953,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 031","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_32",954,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 032","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_33",955,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 033","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_34",956,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 034","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_35",957,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 035","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_36",958,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 036","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_37",959,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 037","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_38",960,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 038","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_39",961,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 039","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_40",962,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 040","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_41",963,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 041","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_42",964,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 042","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_43",965,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 043","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_44",966,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 044","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_45",967,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 045","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_46",968,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 046","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_47",969,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 047","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_48",970,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 048","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_49",971,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 049","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_50",972,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 050","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_51",973,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 051","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_52",974,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 052","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_53",975,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 053","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_54",976,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 054","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_55",977,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 055","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_56",978,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 056","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_57",979,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 057","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_58",980,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 058","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_59",981,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 059","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_60",982,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 060","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_61",983,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 061","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_62",984,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 062","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_63",985,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 063","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_64",986,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 064","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_65",987,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 065","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_66",988,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 066","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_67",989,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 067","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_68",990,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 068","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_69",991,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 069","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_70",992,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 070","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_71",993,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 071","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_72",994,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 072","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_73",995,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 073","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_74",996,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 074","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_75",997,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 075","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_76",998,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 076","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_77",999,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 077","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_78",1000,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 078","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_79",1001,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 079","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_80",1002,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 080","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_81",1003,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 081","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_82",1004,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 082","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_83",1005,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 083","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_84",1006,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 084","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_85",1007,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 085","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_86",1008,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 086","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_87",1009,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 087","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_88",1010,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 088","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_89",1011,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 089","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_90",1012,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 090","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_91",1013,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 091","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_92",1014,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 092","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_93",1015,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 093","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_94",1016,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 094","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_95",1017,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 095","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_96",1018,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 096","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_97",1019,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 097","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_98",1020,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 098","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_99",1021,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 099","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_PSLINT_100",1022,"PSL","PSLINT","NO_RESPONSE",null,"PSL Internal 100","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1023",1023,"SW","UNUSED","NO_RESPONSE"]
["DDB_GOOSEOUT_1",1024,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 1",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_2",1025,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 2",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_3",1026,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 3",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_4",1027,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 4",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_5",1028,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 5",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_6",1029,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 6",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_7",1030,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 7",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_8",1031,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 8",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_9",1032,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output 9",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_10",1033,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output10",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_11",1034,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output11",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_12",1035,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output12",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_13",1036,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output13",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_14",1037,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output14",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_15",1038,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output15",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_16",1039,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output16",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_17",1040,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output17",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_18",1041,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output18",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_19",1042,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output19",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_20",1043,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output20",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_21",1044,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output21",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_22",1045,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output22",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_23",1046,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output23",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_24",1047,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output24",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_25",1048,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output25",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_26",1049,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output26",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_27",1050,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output27",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_28",1051,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output28",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_29",1052,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output29",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_30",1053,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output30",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_31",1054,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output31",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_GOOSEOUT_32",1055,"PSL","GOOSEOUT","event_Protection",null,"Virtual Output32",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_1",1056,"SW","PFSO","event_Protection","GOOSE Virtual input 1 Quality bit","Quality VIP 1 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_2",1057,"SW","PFSO","event_Protection","GOOSE Virtual input 2 Quality bit","Quality VIP 2 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_3",1058,"SW","PFSO","event_Protection","GOOSE Virtual input 3 Quality bit","Quality VIP 3 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_4",1059,"SW","PFSO","event_Protection","GOOSE Virtual input 4 Quality bit","Quality VIP 4 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_5",1060,"SW","PFSO","event_Protection","GOOSE Virtual input 5 Quality bit","Quality VIP 5 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_6",1061,"SW","PFSO","event_Protection","GOOSE Virtual input 6 Quality bit","Quality VIP 6 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_7",1062,"SW","PFSO","event_Protection","GOOSE Virtual input 7 Quality bit","Quality VIP 7 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_8",1063,"SW","PFSO","event_Protection","GOOSE Virtual input 8 Quality bit","Quality VIP 8 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_9",1064,"SW","PFSO","event_Protection","GOOSE Virtual input 9 Quality bit","Quality VIP 9 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_10",1065,"SW","PFSO","event_Protection","GOOSE Virtual input 10 Quality bit","Quality VIP 10 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_11",1066,"SW","PFSO","event_Protection","GOOSE Virtual input 11 Quality bit","Quality VIP 11 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_12",1067,"SW","PFSO","event_Protection","GOOSE Virtual input 12 Quality bit","Quality VIP 12 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_13",1068,"SW","PFSO","event_Protection","GOOSE Virtual input 13 Quality bit","Quality VIP 13 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_14",1069,"SW","PFSO","event_Protection","GOOSE Virtual input 14 Quality bit","Quality VIP 14 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_15",1070,"SW","PFSO","event_Protection","GOOSE Virtual input 15 Quality bit","Quality VIP 15 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_16",1071,"SW","PFSO","event_Protection","GOOSE Virtual input 16 Quality bit","Quality VIP 16 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_17",1072,"SW","PFSO","event_Protection","GOOSE Virtual input 17 Quality bit","Quality VIP 17 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_18",1073,"SW","PFSO","event_Protection","GOOSE Virtual input 18 Quality bit","Quality VIP 18 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_19",1074,"SW","PFSO","event_Protection","GOOSE Virtual input 19 Quality bit","Quality VIP 19 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_20",1075,"SW","PFSO","event_Protection","GOOSE Virtual input 20 Quality bit","Quality VIP 20 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_21",1076,"SW","PFSO","event_Protection","GOOSE Virtual input 21 Quality bit","Quality VIP 21 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_22",1077,"SW","PFSO","event_Protection","GOOSE Virtual input 22 Quality bit","Quality VIP 22 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_23",1078,"SW","PFSO","event_Protection","GOOSE Virtual input 23 Quality bit","Quality VIP 23 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_24",1079,"SW","PFSO","event_Protection","GOOSE Virtual input 24 Quality bit","Quality VIP 24 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_25",1080,"SW","PFSO","event_Protection","GOOSE Virtual input 25 Quality bit","Quality VIP 25 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_26",1081,"SW","PFSO","event_Protection","GOOSE Virtual input 26 Quality bit","Quality VIP 26 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_27",1082,"SW","PFSO","event_Protection","GOOSE Virtual input 27 Quality bit","Quality VIP 27 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_28",1083,"SW","PFSO","event_Protection","GOOSE Virtual input 28 Quality bit","Quality VIP 28 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_29",1084,"SW","PFSO","event_Protection","GOOSE Virtual input 29 Quality bit","Quality VIP 29 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_30",1085,"SW","PFSO","event_Protection","GOOSE Virtual input 30 Quality bit","Quality VIP 30 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_31",1086,"SW","PFSO","event_Protection","GOOSE Virtual input 31 Quality bit","Quality VIP 31 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_32",1087,"SW","PFSO","event_Protection","GOOSE Virtual input 32 Quality bit","Quality VIP 32 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_33",1088,"SW","PFSO","event_Protection","GOOSE Virtual input 33 Quality bit","Quality VIP 33 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_34",1089,"SW","PFSO","event_Protection","GOOSE Virtual input 34 Quality bit","Quality VIP 34 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_35",1090,"SW","PFSO","event_Protection","GOOSE Virtual input 35 Quality bit","Quality VIP 35 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_36",1091,"SW","PFSO","event_Protection","GOOSE Virtual input 36 Quality bit","Quality VIP 36 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_37",1092,"SW","PFSO","event_Protection","GOOSE Virtual input 37 Quality bit","Quality VIP 37 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_38",1093,"SW","PFSO","event_Protection","GOOSE Virtual input 38 Quality bit","Quality VIP 38 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_39",1094,"SW","PFSO","event_Protection","GOOSE Virtual input 39 Quality bit","Quality VIP 39 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_40",1095,"SW","PFSO","event_Protection","GOOSE Virtual input 40 Quality bit","Quality VIP 40 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_41",1096,"SW","PFSO","event_Protection","GOOSE Virtual input 41 Quality bit","Quality VIP 41 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_42",1097,"SW","PFSO","event_Protection","GOOSE Virtual input 42 Quality bit","Quality VIP 42 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_43",1098,"SW","PFSO","event_Protection","GOOSE Virtual input 43 Quality bit","Quality VIP 43 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_44",1099,"SW","PFSO","event_Protection","GOOSE Virtual input 44 Quality bit","Quality VIP 44 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_45",1100,"SW","PFSO","event_Protection","GOOSE Virtual input 45 Quality bit","Quality VIP 45 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_46",1101,"SW","PFSO","event_Protection","GOOSE Virtual input 46 Quality bit","Quality VIP 46 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_47",1102,"SW","PFSO","event_Protection","GOOSE Virtual input 47 Quality bit","Quality VIP 47 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_48",1103,"SW","PFSO","event_Protection","GOOSE Virtual input 48 Quality bit","Quality VIP 48 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_49",1104,"SW","PFSO","event_Protection","GOOSE Virtual input 49 Quality bit","Quality VIP 49 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_50",1105,"SW","PFSO","event_Protection","GOOSE Virtual input 50 Quality bit","Quality VIP 50 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_51",1106,"SW","PFSO","event_Protection","GOOSE Virtual input 51 Quality bit","Quality VIP 51 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_52",1107,"SW","PFSO","event_Protection","GOOSE Virtual input 52 Quality bit","Quality VIP 52 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_53",1108,"SW","PFSO","event_Protection","GOOSE Virtual input 53 Quality bit","Quality VIP 53 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_54",1109,"SW","PFSO","event_Protection","GOOSE Virtual input 54 Quality bit","Quality VIP 54 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_55",1110,"SW","PFSO","event_Protection","GOOSE Virtual input 55 Quality bit","Quality VIP 55 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_56",1111,"SW","PFSO","event_Protection","GOOSE Virtual input 56 Quality bit","Quality VIP 56 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_57",1112,"SW","PFSO","event_Protection","GOOSE Virtual input 57 Quality bit","Quality VIP 57 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_58",1113,"SW","PFSO","event_Protection","GOOSE Virtual input 58 Quality bit","Quality VIP 58 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_59",1114,"SW","PFSO","event_Protection","GOOSE Virtual input 59 Quality bit","Quality VIP 59 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_60",1115,"SW","PFSO","event_Protection","GOOSE Virtual input 60 Quality bit","Quality VIP 60 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_61",1116,"SW","PFSO","event_Protection","GOOSE Virtual input 61 Quality bit","Quality VIP 61 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_62",1117,"SW","PFSO","event_Protection","GOOSE Virtual input 62 Quality bit","Quality VIP 62 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_63",1118,"SW","PFSO","event_Protection","GOOSE Virtual input 63 Quality bit","Quality VIP 63 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_QUALITY_64",1119,"SW","PFSO","event_Protection","GOOSE Virtual input 64 Quality bit","Quality VIP 64 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_1",1120,"SW","PFSO","event_Protection","GOOSE Virtual input 1 publisher bit","PubPres VIP 1 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_2",1121,"SW","PFSO","event_Protection","GOOSE Virtual input 2 publisher bit","PubPres VIP 2 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_3",1122,"SW","PFSO","event_Protection","GOOSE Virtual input 3 publisher bit","PubPres VIP 3 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_4",1123,"SW","PFSO","event_Protection","GOOSE Virtual input 4 publisher bit","PubPres VIP 4 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_5",1124,"SW","PFSO","event_Protection","GOOSE Virtual input 5 publisher bit","PubPres VIP 5 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_6",1125,"SW","PFSO","event_Protection","GOOSE Virtual input 6 publisher bit","PubPres VIP 6 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_7",1126,"SW","PFSO","event_Protection","GOOSE Virtual input 7 publisher bit","PubPres VIP 7 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_8",1127,"SW","PFSO","event_Protection","GOOSE Virtual input 8 publisher bit","PubPres VIP 8 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_9",1128,"SW","PFSO","event_Protection","GOOSE Virtual input 9 publisher bit","PubPres VIP 9 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_10",1129,"SW","PFSO","event_Protection","GOOSE Virtual input 10 publisher bit","PubPres VIP 10 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_11",1130,"SW","PFSO","event_Protection","GOOSE Virtual input 11 publisher bit","PubPres VIP 11 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_12",1131,"SW","PFSO","event_Protection","GOOSE Virtual input 12 publisher bit","PubPres VIP 12 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_13",1132,"SW","PFSO","event_Protection","GOOSE Virtual input 13 publisher bit","PubPres VIP 13 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_14",1133,"SW","PFSO","event_Protection","GOOSE Virtual input 14 publisher bit","PubPres VIP 14 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_15",1134,"SW","PFSO","event_Protection","GOOSE Virtual input 15 publisher bit","PubPres VIP 15 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_16",1135,"SW","PFSO","event_Protection","GOOSE Virtual input 16 publisher bit","PubPres VIP 16 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_17",1136,"SW","PFSO","event_Protection","GOOSE Virtual input 17 publisher bit","PubPres VIP 17 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_18",1137,"SW","PFSO","event_Protection","GOOSE Virtual input 18 publisher bit","PubPres VIP 18 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_19",1138,"SW","PFSO","event_Protection","GOOSE Virtual input 19 publisher bit","PubPres VIP 19 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_20",1139,"SW","PFSO","event_Protection","GOOSE Virtual input 20 publisher bit","PubPres VIP 20 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_21",1140,"SW","PFSO","event_Protection","GOOSE Virtual input 21 publisher bit","PubPres VIP 21 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_22",1141,"SW","PFSO","event_Protection","GOOSE Virtual input 22 publisher bit","PubPres VIP 22 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_23",1142,"SW","PFSO","event_Protection","GOOSE Virtual input 23 publisher bit","PubPres VIP 23 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_24",1143,"SW","PFSO","event_Protection","GOOSE Virtual input 24 publisher bit","PubPres VIP 24 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_25",1144,"SW","PFSO","event_Protection","GOOSE Virtual input 25 publisher bit","PubPres VIP 25 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_26",1145,"SW","PFSO","event_Protection","GOOSE Virtual input 26 publisher bit","PubPres VIP 26 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_27",1146,"SW","PFSO","event_Protection","GOOSE Virtual input 27 publisher bit","PubPres VIP 27 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_28",1147,"SW","PFSO","event_Protection","GOOSE Virtual input 28 publisher bit","PubPres VIP 28 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_29",1148,"SW","PFSO","event_Protection","GOOSE Virtual input 29 publisher bit","PubPres VIP 29 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_30",1149,"SW","PFSO","event_Protection","GOOSE Virtual input 30 publisher bit","PubPres VIP 30 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_31",1150,"SW","PFSO","event_Protection","GOOSE Virtual input 31 publisher bit","PubPres VIP 31 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_32",1151,"SW","PFSO","event_Protection","GOOSE Virtual input 32 publisher bit","PubPres VIP 32 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_33",1152,"SW","PFSO","event_Protection","GOOSE Virtual input 33 publisher bit","PubPres VIP 33 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_34",1153,"SW","PFSO","event_Protection","GOOSE Virtual input 34 publisher bit","PubPres VIP 34 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_35",1154,"SW","PFSO","event_Protection","GOOSE Virtual input 35 publisher bit","PubPres VIP 35 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_36",1155,"SW","PFSO","event_Protection","GOOSE Virtual input 36 publisher bit","PubPres VIP 36 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_37",1156,"SW","PFSO","event_Protection","GOOSE Virtual input 37 publisher bit","PubPres VIP 37 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_38",1157,"SW","PFSO","event_Protection","GOOSE Virtual input 38 publisher bit","PubPres VIP 38 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_39",1158,"SW","PFSO","event_Protection","GOOSE Virtual input 39 publisher bit","PubPres VIP 39 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_40",1159,"SW","PFSO","event_Protection","GOOSE Virtual input 40 publisher bit","PubPres VIP 40 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_41",1160,"SW","PFSO","event_Protection","GOOSE Virtual input 41 publisher bit","PubPres VIP 41 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_42",1161,"SW","PFSO","event_Protection","GOOSE Virtual input 42 publisher bit","PubPres VIP 42 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_43",1162,"SW","PFSO","event_Protection","GOOSE Virtual input 43 publisher bit","PubPres VIP 43 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_44",1163,"SW","PFSO","event_Protection","GOOSE Virtual input 44 publisher bit","PubPres VIP 44 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_45",1164,"SW","PFSO","event_Protection","GOOSE Virtual input 45 publisher bit","PubPres VIP 45 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_46",1165,"SW","PFSO","event_Protection","GOOSE Virtual input 46 publisher bit","PubPres VIP 46 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_47",1166,"SW","PFSO","event_Protection","GOOSE Virtual input 47 publisher bit","PubPres VIP 47 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_48",1167,"SW","PFSO","event_Protection","GOOSE Virtual input 48 publisher bit","PubPres VIP 48 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_49",1168,"SW","PFSO","event_Protection","GOOSE Virtual input 49 publisher bit","PubPres VIP 49 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_50",1169,"SW","PFSO","event_Protection","GOOSE Virtual input 50 publisher bit","PubPres VIP 50 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_51",1170,"SW","PFSO","event_Protection","GOOSE Virtual input 51 publisher bit","PubPres VIP 51 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_52",1171,"SW","PFSO","event_Protection","GOOSE Virtual input 52 publisher bit","PubPres VIP 52 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_53",1172,"SW","PFSO","event_Protection","GOOSE Virtual input 53 publisher bit","PubPres VIP 53 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_54",1173,"SW","PFSO","event_Protection","GOOSE Virtual input 54 publisher bit","PubPres VIP 54 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_55",1174,"SW","PFSO","event_Protection","GOOSE Virtual input 55 publisher bit","PubPres VIP 55 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_56",1175,"SW","PFSO","event_Protection","GOOSE Virtual input 56 publisher bit","PubPres VIP 56 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_57",1176,"SW","PFSO","event_Protection","GOOSE Virtual input 57 publisher bit","PubPres VIP 57 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_58",1177,"SW","PFSO","event_Protection","GOOSE Virtual input 58 publisher bit","PubPres VIP 58 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_59",1178,"SW","PFSO","event_Protection","GOOSE Virtual input 59 publisher bit","PubPres VIP 59 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_60",1179,"SW","PFSO","event_Protection","GOOSE Virtual input 60 publisher bit","PubPres VIP 60 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_61",1180,"SW","PFSO","event_Protection","GOOSE Virtual input 61 publisher bit","PubPres VIP 61 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_62",1181,"SW","PFSO","event_Protection","GOOSE Virtual input 62 publisher bit","PubPres VIP 62 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_63",1182,"SW","PFSO","event_Protection","GOOSE Virtual input 63 publisher bit","PubPres VIP 63 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_VIP_PUB_PRES_64",1183,"SW","PFSO","event_Protection","GOOSE Virtual input 64 publisher bit","PubPres VIP 64 ",{"$nulls":11},"*","*","*","*","*","*","*"]
["DDB_UNUSED_1184",1184,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1185",1185,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1186",1186,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1187",1187,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1188",1188,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1189",1189,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1190",1190,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1191",1191,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1192",1192,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1193",1193,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1194",1194,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1195",1195,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1196",1196,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1197",1197,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1198",1198,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1199",1199,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1200",1200,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1201",1201,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1202",1202,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1203",1203,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1204",1204,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1205",1205,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1206",1206,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1207",1207,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1208",1208,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1209",1209,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1210",1210,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1211",1211,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1212",1212,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1213",1213,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1214",1214,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1215",1215,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1216",1216,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1217",1217,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1218",1218,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1219",1219,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1220",1220,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1221",1221,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1222",1222,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1223",1223,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1224",1224,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1225",1225,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1226",1226,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1227",1227,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1228",1228,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1229",1229,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1230",1230,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1231",1231,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1232",1232,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1233",1233,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1234",1234,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1235",1235,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1236",1236,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1237",1237,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1238",1238,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1239",1239,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1240",1240,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1241",1241,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1242",1242,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1243",1243,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1244",1244,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1245",1245,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1246",1246,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1247",1247,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1248",1248,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1249",1249,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1250",1250,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1251",1251,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1252",1252,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1253",1253,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1254",1254,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1255",1255,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1256",1256,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1257",1257,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1258",1258,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1259",1259,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1260",1260,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1261",1261,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1262",1262,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1263",1263,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1264",1264,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1265",1265,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1266",1266,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1267",1267,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1268",1268,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1269",1269,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1270",1270,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1271",1271,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1272",1272,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1273",1273,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1274",1274,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1275",1275,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1276",1276,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1277",1277,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1278",1278,"SW","UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1279",1279,"SW","UNUSED","NO_RESPONSE"]
["DDB_ADV_FREQ_INHIBIT",1280,"PFSI","NO_RESPONSE","Inhibits advanced frequency protection","Adv Freq Inh","Adv Freq Inh","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_F_T_START",1281,"PFSO","event_Protection","Stage 1 f+t Element Start","Stg1 f+t Sta","Stg1 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_F_T_TRIP",1282,"PFSO","event_Protection","Stage 1 f+t Element Trip","Stg1 f+t Trp","Stg1 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_F_DFDT_TRIP",1283,"PFSO","event_Protection","Stage 1 f+df/dt Element Trip","Stg1 f+df/dt Trp","Stg1 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_DFDT_T_START",1284,"PFSO","event_Protection","Stage 1 df/dt+t Element Start","Stg1 df/dt+t Sta","Stg1 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_DFDT_T_TRIP",1285,"PFSO","event_Protection","Stage 1 df/dt+t Element Trip","Stg1 df/dt+t Trp","Stg1 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_F_DELF_DELT_START",1286,"PFSO","event_Protection","Stage 1 f+DeltaF/DeltaT Element Start","Stg1 f+Df/Dt Sta","Stg1 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_F_DELF_DELT_TRIP",1287,"PFSO","event_Protection","Stage 1 f+DeltaF/DeltaT Element Trip","Stg1 f+Df/Dt Trp","Stg1 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_ADV_FREQ_BLOCK",1288,"PFSI","NO_RESPONSE","Blocks all stage 1 elements","Stg1 Block","Stg1 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1289",1289,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1290",1290,"UNUSED","NO_RESPONSE"]
["DDB_STG1_RESTORE_CLOSE",1291,"PFSO","event_Protection","Stage 1 Load Restoration Close","Stg1 Restore Cls","Stg1 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG1_RESTORE_START",1292,"PFSO","event_Protection","Stage 1 Load Restoration Start","Stg1 Restore Sta","Stg1 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1293",1293,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1294",1294,"UNUSED","NO_RESPONSE"]
["DDB_STG2_F_T_START",1295,"PFSO","event_Protection","Stage 2 f+t Element Start","Stg2 f+t Sta","Stg2 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_F_T_TRIP",1296,"PFSO","event_Protection","Stage 2 f+t Element Trip","Stg2 f+t Trp","Stg2 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_F_DFDT_TRIP",1297,"PFSO","event_Protection","Stage 2 f+df/dt Element Trip","Stg2 f+df/dt Trp","Stg2 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_DFDT_T_START",1298,"PFSO","event_Protection","Stage 2 df/dt+t Element Start","Stg2 df/dt+t Sta","Stg2 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_DFDT_T_TRIP",1299,"PFSO","event_Protection","Stage 2 df/dt+t Element Trip","Stg2 df/dt+t Trp","Stg2 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_F_DELF_DELT_START",1300,"PFSO","event_Protection","Stage 2 f+DeltaF/DeltaT Element Start","Stg2 f+Df/Dt Sta","Stg2 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_F_DELF_DELT_TRIP",1301,"PFSO","event_Protection","Stage 2 f+DeltaF/DeltaT Element Trip","Stg2 f+Df/Dt Trp","Stg2 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_ADV_FREQ_BLOCK",1302,"PFSI","NO_RESPONSE","Blocks all stage 2 elements","Stg2 Block","Stg2 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1303",1303,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1304",1304,"UNUSED","NO_RESPONSE"]
["DDB_STG2_RESTORE_CLOSE",1305,"PFSO","event_Protection","Stage 2 Load Restoration Close","Stg2 Restore Cls","Stg2 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG2_RESTORE_START",1306,"PFSO","event_Protection","Stage 2 Load Restoration Start","Stg2 Restore Sta","Stg2 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1307",1307,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1308",1308,"UNUSED","NO_RESPONSE"]
["DDB_STG3_F_T_START",1309,"PFSO","event_Protection","Stage 3 f+t Element Start","Stg3 f+t Sta","Stg3 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_F_T_TRIP",1310,"PFSO","event_Protection","Stage 3 f+t Element Trip","Stg3 f+t Trp","Stg3 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_F_DFDT_TRIP",1311,"PFSO","event_Protection","Stage 3 f+df/dt Element Trip","Stg3 f+df/dt Trp","Stg3 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_DFDT_T_START",1312,"PFSO","event_Protection","Stage 3 df/dt+t Element Start","Stg3 df/dt+t Sta","Stg3 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_DFDT_T_TRIP",1313,"PFSO","event_Protection","Stage 3 df/dt+t Element Trip","Stg3 df/dt+t Trp","Stg3 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_F_DELF_DELT_START",1314,"PFSO","event_Protection","Stage 3 f+DeltaF/DeltaT Element Start","Stg3 f+Df/Dt Sta","Stg3 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_F_DELF_DELT_TRIP",1315,"PFSO","event_Protection","Stage 3 f+DeltaF/DeltaT Element Trip","Stg3 f+Df/Dt Trp","Stg3 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_ADV_FREQ_BLOCK",1316,"PFSI","NO_RESPONSE","Blocks all stage 3 elements","Stg3 Block","Stg3 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1317",1317,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1318",1318,"UNUSED","NO_RESPONSE"]
["DDB_STG3_RESTORE_CLOSE",1319,"PFSO","event_Protection","Stage 3 Load Restoration Close","Stg3 Restore Cls","Stg3 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG3_RESTORE_START",1320,"PFSO","event_Protection","Stage 3 Load Restoration Start","Stg3 Restore Sta","Stg3 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1321",1321,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1322",1322,"UNUSED","NO_RESPONSE"]
["DDB_STG4_F_T_START",1323,"PFSO","event_Protection","Stage 4 f+t Element Start","Stg4 f+t Sta","Stg4 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_F_T_TRIP",1324,"PFSO","event_Protection","Stage 4 f+t Element Trip","Stg4 f+t Trp","Stg4 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_F_DFDT_TRIP",1325,"PFSO","event_Protection","Stage 4 f+df/dt Element Trip","Stg4 f+df/dt Trp","Stg4 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_DFDT_T_START",1326,"PFSO","event_Protection","Stage 4 df/dt+t Element Start","Stg4 df/dt+t Sta","Stg4 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_DFDT_T_TRIP",1327,"PFSO","event_Protection","Stage 4 df/dt+t Element Trip","Stg4 df/dt+t Trp","Stg4 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_F_DELF_DELT_START",1328,"PFSO","event_Protection","Stage 4 f+DeltaF/DeltaT Element Start","Stg4 f+Df/Dt Sta","Stg4 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_F_DELF_DELT_TRIP",1329,"PFSO","event_Protection","Stage 4 f+DeltaF/DeltaT Element Trip","Stg4 f+Df/Dt Trp","Stg4 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_ADV_FREQ_BLOCK",1330,"PFSI","NO_RESPONSE","Blocks all stage 4 elements","Stg4 Block","Stg4 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1331",1331,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1332",1332,"UNUSED","NO_RESPONSE"]
["DDB_STG4_RESTORE_CLOSE",1333,"PFSO","event_Protection","Stage 4 Load Restoration Close","Stg4 Restore Cls","Stg4 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG4_RESTORE_START",1334,"PFSO","event_Protection","Stage 4 Load Restoration Start","Stg4 Restore Sta","Stg4 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1335",1335,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1336",1336,"UNUSED","NO_RESPONSE"]
["DDB_STG5_F_T_START",1337,"PFSO","event_Protection","Stage 5 f+t Element Start","Stg5 f+t Sta","Stg5 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_F_T_TRIP",1338,"PFSO","event_Protection","Stage 5 f+t Element Trip","Stg5 f+t Trp","Stg5 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_F_DFDT_TRIP",1339,"PFSO","event_Protection","Stage 5 f+df/dt Element Trip","Stg5 f+df/dt Trp","Stg5 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_DFDT_T_START",1340,"PFSO","event_Protection","Stage 5 df/dt+t Element Start","Stg5 df/dt+t Sta","Stg5 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_DFDT_T_TRIP",1341,"PFSO","event_Protection","Stage 5 df/dt+t Element Trip","Stg5 df/dt+t Trp","Stg5 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_F_DELF_DELT_START",1342,"PFSO","event_Protection","Stage 5 f+DeltaF/DeltaT Element Start","Stg5 f+Df/Dt Sta","Stg5 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_F_DELF_DELT_TRIP",1343,"PFSO","event_Protection","Stage 5 f+DeltaF/DeltaT Element Trip","Stg5 f+Df/Dt Trp","Stg5 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_ADV_FREQ_BLOCK",1344,"PFSI","NO_RESPONSE","Blocks all stage 5 elements","Stg5 Block","Stg5 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1345",1345,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1346",1346,"UNUSED","NO_RESPONSE"]
["DDB_STG5_RESTORE_CLOSE",1347,"PFSO","event_Protection","Stage 5 Load Restoration Close","Stg5 Restore Cls","Stg5 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG5_RESTORE_START",1348,"PFSO","event_Protection","Stage 5 Load Restoration Start","Stg5 Restore Sta","Stg5 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1349",1349,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1350",1350,"UNUSED","NO_RESPONSE"]
["DDB_STG6_F_T_START",1351,"PFSO","event_Protection","Stage 6 f+t Element Start","Stg6 f+t Sta","Stg6 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_F_T_TRIP",1352,"PFSO","event_Protection","Stage 6 f+t Element Trip","Stg6 f+t Trp","Stg6 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_F_DFDT_TRIP",1353,"PFSO","event_Protection","Stage 6 f+df/dt Element Trip","Stg6 f+df/dt Trp","Stg6 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_DFDT_T_START",1354,"PFSO","event_Protection","Stage 6 df/dt+t Element Start","Stg6 df/dt+t Sta","Stg6 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_DFDT_T_TRIP",1355,"PFSO","event_Protection","Stage 6 df/dt+t Element Trip","Stg6 df/dt+t Trp","Stg6 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_F_DELF_DELT_START",1356,"PFSO","event_Protection","Stage 6 f+DeltaF/DeltaT Element Start","Stg6 f+Df/Dt Sta","Stg6 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_F_DELF_DELT_TRIP",1357,"PFSO","event_Protection","Stage 6 f+DeltaF/DeltaT Element Trip","Stg6 f+Df/Dt Trp","Stg6 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_ADV_FREQ_BLOCK",1358,"PFSI","NO_RESPONSE","Blocks all stage 6 elements","Stg6 Block","Stg6 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1359",1359,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1360",1360,"UNUSED","NO_RESPONSE"]
["DDB_STG6_RESTORE_CLOSE",1361,"PFSO","event_Protection","Stage 6 Load Restoration Close","Stg6 Restore Cls","Stg6 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG6_RESTORE_START",1362,"PFSO","event_Protection","Stage 6 Load Restoration Start","Stg6 Restore Sta","Stg6 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1363",1363,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1364",1364,"UNUSED","NO_RESPONSE"]
["DDB_STG7_F_T_START",1365,"PFSO","event_Protection","Stage 7 f+t Element Start","Stg7 f+t Sta","Stg7 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_F_T_TRIP",1366,"PFSO","event_Protection","Stage 7 f+t Element Trip","Stg7 f+t Trp","Stg7 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_F_DFDT_TRIP",1367,"PFSO","event_Protection","Stage 7 f+df/dt Element Trip","Stg7 f+df/dt Trp","Stg7 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_DFDT_T_START",1368,"PFSO","event_Protection","Stage 7 df/dt+t Element Start","Stg7 df/dt+t Sta","Stg7 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_DFDT_T_TRIP",1369,"PFSO","event_Protection","Stage 7 df/dt+t Element Trip","Stg7 df/dt+t Trp","Stg7 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_F_DELF_DELT_START",1370,"PFSO","event_Protection","Stage 7 f+DeltaF/DeltaT Element Start","Stg7 f+Df/Dt Sta","Stg7 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_F_DELF_DELT_TRIP",1371,"PFSO","event_Protection","Stage 7 f+DeltaF/DeltaT Element Trip","Stg7 f+Df/Dt Trp","Stg7 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_ADV_FREQ_BLOCK",1372,"PFSI","NO_RESPONSE","Blocks all stage 7 elements","Stg7 Block","Stg7 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1373",1373,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1374",1374,"UNUSED","NO_RESPONSE"]
["DDB_STG7_RESTORE_CLOSE",1375,"PFSO","event_Protection","Stage 7 Load Restoration Close","Stg7 Restore Cls","Stg7 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG7_RESTORE_START",1376,"PFSO","event_Protection","Stage 7 Load Restoration Start","Stg7 Restore Sta","Stg7 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1377",1377,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1378",1378,"UNUSED","NO_RESPONSE"]
["DDB_STG8_F_T_START",1379,"PFSO","event_Protection","Stage 8 f+t Element Start","Stg8 f+t Sta","Stg8 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_F_T_TRIP",1380,"PFSO","event_Protection","Stage 8 f+t Element Trip","Stg8 f+t Trp","Stg8 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_F_DFDT_TRIP",1381,"PFSO","event_Protection","Stage 8 f+df/dt Element Trip","Stg8 f+df/dt Trp","Stg8 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_DFDT_T_START",1382,"PFSO","event_Protection","Stage 8 df/dt+t Element Start","Stg8 df/dt+t Sta","Stg8 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_DFDT_T_TRIP",1383,"PFSO","event_Protection","Stage 8 df/dt+t Element Trip","Stg8 df/dt+t Trp","Stg8 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_F_DELF_DELT_START",1384,"PFSO","event_Protection","Stage 8 f+DeltaF/DeltaT Element Start","Stg8 f+Df/Dt Sta","Stg8 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_F_DELF_DELT_TRIP",1385,"PFSO","event_Protection","Stage 8 f+DeltaF/DeltaT Element Trip","Stg8 f+Df/Dt Trp","Stg8 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_ADV_FREQ_BLOCK",1386,"PFSI","NO_RESPONSE","Blocks all stage 8 elements","Stg8 Block","Stg8 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1387",1387,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1388",1388,"UNUSED","NO_RESPONSE"]
["DDB_STG8_RESTORE_CLOSE",1389,"PFSO","event_Protection","Stage 8 Load Restoration Close","Stg8 Restore Cls","Stg8 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG8_RESTORE_START",1390,"PFSO","event_Protection","Stage 8 Load Restoration Start","Stg8 Restore Sta","Stg8 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1391",1391,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1392",1392,"UNUSED","NO_RESPONSE"]
["DDB_STG9_F_T_START",1393,"PFSO","event_Protection","Stage 9 f+t Element Start","Stg9 f+t Sta","Stg9 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_F_T_TRIP",1394,"PFSO","event_Protection","Stage 9 f+t Element Trip","Stg9 f+t Trp","Stg9 f+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_F_DFDT_TRIP",1395,"PFSO","event_Protection","Stage 9 f+df/dt Element Trip","Stg9 f+df/dt Trp","Stg9 f+df/dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_DFDT_T_START",1396,"PFSO","event_Protection","Stage 9 df/dt+t Element Start","Stg9 df/dt+t Sta","Stg9 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_DFDT_T_TRIP",1397,"PFSO","event_Protection","Stage 9 df/dt+t Element Trip","Stg9 df/dt+t Trp","Stg9 df/dt+t Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_F_DELF_DELT_START",1398,"PFSO","event_Protection","Stage 9 f+DeltaF/DeltaT Element Start","Stg9 f+Df/Dt Sta","Stg9 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_F_DELF_DELT_TRIP",1399,"PFSO","event_Protection","Stage 9 f+DeltaF/DeltaT Element Trip","Stg9 f+Df/Dt Trp","Stg9 f+Df/Dt Trp","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_ADV_FREQ_BLOCK",1400,"PFSI","NO_RESPONSE","Blocks all stage 9 elements","Stg9 Block","Stg9 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1401",1401,"UNUSED","NO_RESPONSE"]
["DDB_UNUSED_1402",1402,"UNUSED","NO_RESPONSE"]
["DDB_STG9_RESTORE_CLOSE",1403,"PFSO","event_Protection","Stage 9 Load Restoration Close","Stg9 Restore Cls","Stg9 Restore Cls","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_STG9_RESTORE_START",1404,"PFSO","event_Protection","Stage 9 Load Restoration Start","Stg9 Restore Sta","Stg9 Restore Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESTORE_RESET",1405,"PFSI","NO_RESPONSE","Resets all load restoration stages","Restore Reset","Restore Reset","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_RESET_STATISTICS",1406,"PFSI","NO_RESPONSE","Resets all Statistics counters","Reset Stats","Reset Stats","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["DDB_UNUSED_1403",1407]
["DDB_UNUSED_1404",1408]
["DDB_UNUSED_1405",1409]
["DDB_UNUSED_1406",1410]
["DDB_UNUSED_1407",1411]
["DDB_UNUSED_1408",1412]
["DDB_UNUSED_1409",1413]
["DDB_UNUSED_1410",1414]
["DDB_UNUSED_1411",1415]
["DDB_UNUSED_1412",1416]
["DDB_UNUSED_1413",1417]
["DDB_UNUSED_1414",1418]
["DDB_UNUSED_1415",1419]
["DDB_UNUSED_1416",1420]
["DDB_UNUSED_1417",1421]
["DDB_UNUSED_1418",1422]
["DDB_UNUSED_1419",1423]
["DDB_UNUSED_1420",1424]
["DDB_UNUSED_1421",1425]
["DDB_UNUSED_1422",1426]
["DDB_UNUSED_1423",1427]
["DDB_UNUSED_1424",1428]
["DDB_UNUSED_1425",1429]
["DDB_UNUSED_1426",1430]
["DDB_UNUSED_1427",1431]
["DDB_UNUSED_1428",1432]
["DDB_UNUSED_1429",1433]
["DDB_UNUSED_1430",1434]
["DDB_UNUSED_1431",1435]
["DDB_UNUSED_1432",1436]
["DDB_UNUSED_1433",1437]
["DDB_UNUSED_1434",1438]
["DDB_UNUSED_1435",1439]
["DDB_UNUSED_1436",1440]
["DDB_UNUSED_1437",1441]
["DDB_UNUSED_1438",1442]
["DDB_UNUSED_1439",1443]
["DDB_UNUSED_1440",1444]
["DDB_UNUSED_1441",1445]
["DDB_UNUSED_1442",1446]
["DDB_UNUSED_1443",1447]
["DDB_UNUSED_1444",1448]
["DDB_UNUSED_1445",1449]
["DDB_UNUSED_1446",1450]
["DDB_UNUSED_1447",1451]
["DDB_UNUSED_1448",1452]
["DDB_UNUSED_1449",1453]
["DDB_UNUSED_1450",1454]
["DDB_UNUSED_1451",1455]
["DDB_UNUSED_1452",1456]
["DDB_UNUSED_1453",1457]
["DDB_UNUSED_1454",1458]
["DDB_UNUSED_1455",1459]
["DDB_UNUSED_1456",1460]
["DDB_UNUSED_1457",1461]
["DDB_UNUSED_1458",1462]
["DDB_UNUSED_1459",1463]
["DDB_UNUSED_1460",1464]
["DDB_UNUSED_1461",1465]
["DDB_UNUSED_1462",1466]
["DDB_UNUSED_1463",1467]
["DDB_UNUSED_1464",1468]
["DDB_UNUSED_1465",1469]
["DDB_UNUSED_1466",1470]
["DDB_UNUSED_1467",1471]
["DDB_UNUSED_1468",1472]
["DDB_UNUSED_1469",1473]
["DDB_UNUSED_1470",1474]
["DDB_UNUSED_1471",1475]
["DDB_UNUSED_1472",1476]
["DDB_UNUSED_1473",1477]
["DDB_UNUSED_1474",1478]
["DDB_UNUSED_1475",1479]
["DDB_UNUSED_1476",1480]
["DDB_UNUSED_1477",1481]
["DDB_UNUSED_1478",1482]
["DDB_UNUSED_1479",1483]
["DDB_UNUSED_1480",1484]
["DDB_UNUSED_1481",1485]
["DDB_UNUSED_1482",1486]
["DDB_UNUSED_1483",1487]
["DDB_UNUSED_1484",1488]
["DDB_UNUSED_1485",1489]
["DDB_UNUSED_1486",1490]
["DDB_UNUSED_1487",1491]
["DDB_UNUSED_1488",1492]
["DDB_UNUSED_1489",1493]
["DDB_UNUSED_1490",1494]
["DDB_UNUSED_1491",1495]
["DDB_UNUSED_1492",1496]
["DDB_UNUSED_1493",1497]
["DDB_UNUSED_1494",1498]
["DDB_UNUSED_1495",1499]
["DDB_UNUSED_1496",1500]
["DDB_UNUSED_1497",1501]
["DDB_UNUSED_1498",1502]
["DDB_UNUSED_1499",1503]
["DDB_UNUSED_1500",1504]
["DDB_UNUSED_1501",1505]
["DDB_UNUSED_1502",1506]
["DDB_UNUSED_1503",1507]
["DDB_UNUSED_1504",1508]
["DDB_UNUSED_1505",1509]
["DDB_UNUSED_1506",1510]
["DDB_UNUSED_1507",1511]
["DDB_UNUSED_1508",1512]
["DDB_UNUSED_1509",1513]
["DDB_UNUSED_1510",1514]
["DDB_UNUSED_1511",1515]
["DDB_UNUSED_1512",1516]
["DDB_UNUSED_1513",1517]
["DDB_UNUSED_1514",1518]
["DDB_UNUSED_1515",1519]
["DDB_UNUSED_1516",1520]
["DDB_UNUSED_1517",1521]
["DDB_UNUSED_1518",1522]
["DDB_UNUSED_1519",1523]
["DDB_UNUSED_1520",1524]
["DDB_UNUSED_1521",1525]
["DDB_UNUSED_1522",1526]
["DDB_UNUSED_1523",1527]
["DDB_UNUSED_1524",1528]
["DDB_UNUSED_1525",1529]
["DDB_UNUSED_1526",1530]
["DDB_UNUSED_1527",1531]
["DDB_UNUSED_1528",1532]
["DDB_UNUSED_1529",1533]
["DDB_UNUSED_1530",1534]
["DDB_UNUSED_1531",1535]

{"sheet":"Events & Other Text","index":4,"n_rows":178,"n_cols":7,"rows_kept":178,"cut":false,"hidden":false,"merged":[[0,0,0,6],[1,0,3,0],[1,1,3,1],[1,2,3,2],[1,3,3,3],[1,4,3,4],[1,5,3,5],[1,6,3,6]],"flags":["formulas_cached_only"]}
["Courier Events"]
["Event Group","Event Name","Event Cell Ref.","Event Ext. Col.","Event Text","Event Value","Comments"]
[]
[]
["Opto Input Events",null,"0020/0030",null,"Logic Inputs","0000000000000001","New opto state"]
["Contact Events",null,"0021/0040",null,"Output Contacts","000000000000000000001","New contact state"]
["Alarm Events","Unused","0022/0050",null,"Reserved","0x0000, 0x0001","Bit 1"]
[null,"Unused","0022/0050",null,"Reserved","0x0000, 0x0002","Bit 2"]
[null,"Setting group via opto invalid","0022/0050",null,"SG-opto Invalid ON/OFF","0x0000, 0x0004","Bit 3"]
[null,"Protection Disabled","0022/0050",null,"Prot'n Disabled ON/OFF","0x0000, 0x0008","Bit 4"]
[null,"Frequency out of range","0022/0050",null,"F out of Range ON/OFF","0x0000, 0x0010","Bit 5"]
[null,"VTS Alarm","0022/0050",null,"VT Fail Alarm ON/OFF","0x0000, 0x0020","Bit 6"]
[null,"CTS Alarm","0022/0050",null,"CT Fail Alarm ON/OFF","0x0000, 0x0040","Bit 7"]
[null,"CB Trip Fail Protection","0022/0050",null,"CB Fail Alarm ON/OFF","0x0000, 0x0080","Bit 8"]
[null,"Broken current Maintenance Alarm","0022/0050",null,"I^ Maint Alarm ON/OFF","0x0000, 0x0100","Bit 9"]
[null,"Broken current Lockout Alarm","0022/0050",null,"I^ Lockout Alarm ON/OFF","0x0000, 0x0200","Bit 10"]
[null,"No of CB Ops Maintenance Alarm","0022/0050",null,"CB Ops Maint ON/OFF","0x0000, 0x0400","Bit 11"]
[null,"No of CB Ops Lockout Alarm","0022/0050",null,"CB Ops Lockout ON/OFF","0x0000, 0x0800","Bit 12"]
[null,"CB Op Time Maintenance Alarm","0022/0050",null,"CB Op Time Maint ON/OFF","0x0000, 0x1000","Bit 13"]
[null,"CB Op Time Lockout Alarm","0022/0050",null,"CB Op Time Lock ON/OFF","0x0000, 0x2000","Bit 14"]
[null,"Excessive Fault Frequency Lockout Alarm","0022/0050",null,"Fault Freq Lock ON/OFF","0x0000, 0x4000","Bit 15"]
[null,"CB Status Alarm","0022/0050",null,"CB Status Alarm ON/OFF","0x0000, 0x8000","Bit 16"]
[null,"CB Fail Trip Control","0022/0050",null,"Man CB Trip Fail ON/OFF","0x0001, 0x0000","Bit 17"]
[null,"CB Fail Close Control","0022/0050",null,"Man CB Cls Fail ON/OFF","0x0002, 0x0000","Bit 18"]
[null,"No Healthy Control Close","0022/0050",null,"Man CB Unhealthy ON/OFF","0x0004, 0x0000","Bit 19"]
[null,"No C/S control close","0022/0050",null,"Man No Checksync ON/OFF","0x0008, 0x0000","Bit 20"]
[null,"A/R Lockout","0022/0050",null,"A/R Lockout ON/OFF","0x0010, 0x0000","Bit 21"]
[null,"A/R CB Not healthy","0022/0050",null,"A/R CB Unhealthy ON/OFF","0x0020, 0x0000","Bit 22"]
[null,"A/R No Checksync","0022/0050",null,"A/R No Checksync ON/OFF","0x0040, 0x0000","Bit 23"]
[null,"System Split","0022/0050",null,"System Split ON/OFF","0x0080, 0x0000","Bit 24"]
[null,"User Definable Alarm 1 (Self Reset)","0022/0050",null,"SR User Alarm 1  ON/OFF","0x0100, 0x0000","Bit 25"]
[null,"User Definable Alarm 2 (Self Reset)","0022/0050",null,"SR User Alarm 2  ON/OFF","0x0200, 0x0000","Bit 26"]
[null,"User Definable Alarm 3 (Self Reset)","0022/0050",null,"SR User Alarm 3  ON/OFF","0x0400, 0x0000","Bit 27"]
[null,"User Definable Alarm 4 (Self Reset)","0022/0050",null,"SR User Alarm 4  ON/OFF","0x0800, 0x0000","Bit 28"]
[null,"User Definable Alarm 5 (Self Reset)","0022/0050",null,"SR User Alarm 5  ON/OFF","0x1000, 0x0000","Bit 29"]
[null,"User Definable Alarm 6 (Self Reset)","0022/0050",null,"SR User Alarm 6  ON/OFF","0x2000, 0x0000","Bit 30"]
[null,"User Definable Alarm 7 (Self Reset)","0022/0050",null,"SR User Alarm 7  ON/OFF","0x4000, 0x0000","Bit 31"]
[null,"User Definable Alarm 8 (Self Reset)","0022/0050",null,"SR User Alarm 8  ON/OFF","0x8000, 0x0000","Bit 32"]
[null,"Reserved for Px40 Platform","0051",null,"Reserved","0x0000, 0x0001","Bit 1"]
[null,"Reserved for Px40 Platform","0051",null,"Reserved","0x0000, 0x0002","Bit 2"]
[null,"Reserved for Px40 Platform","0051",null,"Reserved","0x0000, 0x0004","Bit 3"]
[null,"Reserved for Px40 Platform","0051",null,"Reserved","0x0000, 0x0008","Bit 4"]
[null,"User Definable Alarm 9 (Self Reset)","0051",null,"SR User Alarm 9  ON/OFF","0x0000, 0x0010","Bit 5"]
[null,"User Definable Alarm 10 (Self Reset)","0051",null,"SR User Alarm 10  ON/OFF","0x0000, 0x0020","Bit 6"]
[null,"User Definable Alarm 11 (Self Reset)","0051",null,"SR User Alarm 11  ON/OFF","0x0000, 0x0040","Bit 7"]
[null,"User Definable Alarm 12 (Self Reset)","0051",null,"SR User Alarm 12  ON/OFF","0x0000, 0x0080","Bit 8"]
[null,"User Definable Alarm 13 (Self Reset)","0051",null,"SR User Alarm 13  ON/OFF","0x0000, 0x0100","Bit 9"]
[null,"User Definable Alarm 14 (Self Reset)","0051",null,"SR User Alarm 14  ON/OFF","0x0000, 0x0200","Bit 10"]
[null,"User Definable Alarm 15 (Self Reset)","0051",null,"SR User Alarm 15  ON/OFF","0x0000, 0x0400","Bit 11"]
[null,"User Definable Alarm 16 (Self Reset)","0051",null,"SR User Alarm 16  ON/OFF","0x0000, 0x0800","Bit 12"]
[null,"User Definable Alarm 17 (Self Reset)","0051",null,"SR User Alarm 17  ON/OFF","0x0000, 0x1000","Bit 13"]
[null,"User Definable Alarm 18 (Self Reset)","0051",null,"SR User Alarm 18  ON/OFF","0x0000, 0x2000","Bit 14"]
[null,"User Definable Alarm 19 (Latched)","0051",null,"MR User Alarm 19  ON/OFF","0x0000, 0x4000","Bit 15"]
[null,"User Definable Alarm 20 (Latched)","0051",null,"MR User Alarm 20  ON/OFF","0x0000, 0x8000","Bit 16"]
[null,"User Definable Alarm 21 (Latched)","0051",null,"MR User Alarm 21  ON/OFF","0x0001, 0x0000","Bit 17"]
[null,"User Definable Alarm 22 (Latched)","0051",null,"MR User Alarm 22  ON/OFF","0x0002, 0x0000","Bit 18"]
[null,"User Definable Alarm 23 (Latched)","0051",null,"MR User Alarm 23  ON/OFF","0x0004, 0x0000","Bit 19"]
[null,"User Definable Alarm 24 (Latched)","0051",null,"MR User Alarm 24  ON/OFF","0x0008, 0x0000","Bit 20"]
[null,"User Definable Alarm 25 (Latched)","0051",null,"MR User Alarm 25  ON/OFF","0x0010, 0x0000","Bit 21"]
[null,"User Definable Alarm 26 (Latched)","0051",null,"MR User Alarm 26  ON/OFF","0x0020, 0x0000","Bit 22"]
[null,"User Definable Alarm 27 (Latched)","0051",null,"MR User Alarm 27  ON/OFF","0x0040, 0x0000","Bit 23"]
[null,"User Definable Alarm 28 (Latched)","0051",null,"MR User Alarm 28  ON/OFF","0x0080, 0x0000","Bit 24"]
[null,"User Definable Alarm 29 (Latched)","0051",null,"MR User Alarm 29  ON/OFF","0x0100, 0x0000","Bit 25"]
[null,"User Definable Alarm 30 (Latched)","0051",null,"MR User Alarm 30  ON/OFF","0x0200, 0x0000","Bit 26"]
[null,"User Definable Alarm 31 (Latched)","0051",null,"MR User Alarm 31  ON/OFF","0x0400, 0x0000","Bit 27"]
[null,"User Definable Alarm 32 (Latched)","0051",null,"MR User Alarm 32  ON/OFF","0x0800, 0x0000","Bit 28"]
[null,"User Definable Alarm 33 (Latched)","0051",null,"MR User Alarm 33  ON/OFF","0x1000, 0x0000","Bit 29"]
[null,"User Definable Alarm 34 (Latched)","0051",null,"MR User Alarm 34  ON/OFF","0x2000, 0x0000","Bit 30"]
[null,"User Definable Alarm 35 (Latched)","0051",null,"MR User Alarm 35  ON/OFF","0x4000, 0x0000","Bit 31"]
[null,"User Definable Alarm 36 (Latched)","0051",null,"MR User Alarm 36  ON/OFF","0x8000, 0x0000","Bit 32"]
[null,"Battery Fail","0052",null,"Battery Fail ON/OFF","0x0000, 0x0001","Bit 1"]
[null,"Field Volt Fail","0052",null,"Field Volt Fail ON/OFF","0x0000, 0x0002","Bit 2"]
[null,"Comm2 H/W FAIL","0052",null,"Second Courier Port Hardware Failure","0x0000, 0x0004","Bit 3"]
[null,"GOOSE IED Absent","0052",null,"GOOSE IED Absent ON/OFF","0x0000, 0x0008","Bit 4"]
[null,"NIC Not Fitted","0052",null,"NIC Not Fitted ON/OFF","0x0000, 0x0010","Bit 5"]
[null,"NIC No Response","0052",null,"NIC No Response ON/OFF","0x0000, 0x0020","Bit 6"]
[null,"NIC Fatal Error","0052",null,"NIC Fatal Error ON/OFF","0x0000, 0x0040","Bit 7"]
[null,"NIC Soft. Reload","0052",null,"NIC Software Reload ON/OFF","0x0000, 0x0080","Bit 8"]
[null,"Bad TCP/IP Cfg.","0052",null,"Bad TCP/IP Configuration ON/OFF","0x0000, 0x0100","Bit 9"]
[null,"Bad OSI Cfg.","0052",null,"Bad OSI Configuration ON/OFF","0x0000, 0x0200","Bit 10"]
[null,"NIC Link Fail","0052",null,"NIC Link Fail ON/OFF","0x0000, 0x0400","Bit 11"]
[null,"NIC SW Mis-Match","0052",null,"NIC Software Mis-match ON/OFF","0x0000, 0x0800","Bit 12"]
[null,"IP Addr Conflict","0052",null,"IP Address Conflict ON/OFF","0x0000, 0x1000","Bit 13"]
[null,"IM Loopback","0052",null,"InterMiCOM Loopback Fail","0x0000, 0x2000","Bit 14"]
[null,"IM Message Fail","0052",null,"InterMiCOM Message Fail","0x0000, 0x4000","Bit 15"]
[null,"IM Data CD Fail","0052",null,"InterMiCOM Data CD Fail","0x0000, 0x8000","Bit 16"]
[null,"IM Channel Fail","0052",null,"InterMiCOM Channel Fail","0x0001, 0x0000","Bit 17"]
[null,"Backup Setting","0052",null,"Backup settings in use ON/OFF","0x0002, 0x0000","Bit 18"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0004, 0x0000","Bit 19"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0008, 0x0000","Bit 20"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0010, 0x0000","Bit 21"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0020, 0x0000","Bit 22"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0040, 0x0000","Bit 23"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0080, 0x0000","Bit 24"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0100, 0x0000","Bit 25"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0200, 0x0000","Bit 26"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0400, 0x0000","Bit 27"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x0800, 0x0000","Bit 28"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x1000, 0x0000","Bit 29"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x2000, 0x0000","Bit 30"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x4000, 0x0000","Bit 31"]
[null,"Unused","0052",null,"Reserved (Platform alarms)","0x8000, 0x0000","Bit 32"]
["Protection Events",null,"Col =0F ",null,"DDB Signal Name ON/OFF","32bit DDB Word containing the"]
[null,null,"Row = 20+int(ddb/32)",null,null,"changed DDB."]
["Fault Records",null,"0100","B000","Fault Record",0,"16bit UINT Record Number"]
["Self Monitoring","Secondary self-test: Fast Watchdog Failure","FFFF","B100","Fast W'Dog Error",0,"16bit UINT Record Number"]
[null,"Secondary self-test: Battery Failure","FFFF",null,"Battery Failure",1]
[null,"Secondary self-test: Battery Backed RAM Failure","FFFF",null,"BBRAM Failure",2]
[null,"Secondary self-test: Field Voltage Failure","FFFF",null,"Field Volt Fail",3]
[null,"Secondary self-test: Bus reset error","FFFF",null,"Bus Reset Error",4]
[null,"Secondary self-test: Slow Watchdog Failure","FFFF",null,"Slow W'Dog Error",5]
[null,"Cont. self-test: SRAM Bus Failure","FFFF",null,"SRAM Failure Bus",6]
[null,"Cont. self-test: SRAM Memory block Failure","FFFF",null,"SRAM Failure Blk",7]
[null,"Cont. self-test: FLASH Checksum Failure","FFFF",null,"FLASH Failure",8]
[null,"Cont. self-test: Code Verify Failure","FFFF",null,"Code Verify Fail",9]
[null,"Cont. self-test: Battery Backed RAM Failure","FFFF",null,"BBRAM Failure",10]
[null,"Cont. self-test: Battery Failure","FFFF",null,"Battery Failure",11]
[null,"Cont. self-test: Field Voltage Failure","FFFF",null,"Field Volt Fail",12]
[null,"Cont. self-test: EEPROM Memory Failure","FFFF",null,"EEPROM Failure",13]
[null,"Cont. self-test: Analog Sampling Failure","FFFF",null,"Ana. Sample Fail",17]
[null,"Fatal software error","FFFF",null,"Software Failure",14]
[null,"Hardware verification Failure","FFFF",null,"H/W Verify Fail",15]
[null,"Non standard Failure","FFFF",null,"Non Standard",16]
[null,"Ethernet software error","FFFF",null,"NIC Soft Error",18]
[null,"Flash settings commit error","FFFF",null,"Set. Commit Err.",19,"Settings using backup:"]
[{"$nulls":6},"1 = C&S Settings"]
[{"$nulls":6},"2 = DR Settings"]
[{"$nulls":6},"3 = Protection Group 1"]
[{"$nulls":6},"4 = Protection Group 2"]
[{"$nulls":6},"5 = Protection Group 3"]
[{"$nulls":6},"6 = Protection Group 4"]
["Setting Changes","C&S settings changed","FFFF",null,"C&S Changed",22]
[null,"Group 1 settings changed","0904",null,"Group 1 Changed",24]
[null,"Group 2 settings changed","0904",null,"Group 2 Changed",25]
[null,"Group 3 settings changed","0904",null,"Group 3 Changed",26]
[null,"Group 4 settings changed","0904",null,"Group 4 Changed",27]
[null,"Disturbance Recorder","0C01",null,"Dist Changed",23]
[null,"Active Group Change","0903",null,"Active Group Changed","0x0001001C : Active group = 1","28 + Group << 16"]
[{"$nulls":5},"0x0002001C : Active group = 2"]
[{"$nulls":5},"0x0003001C : Active group = 3"]
[{"$nulls":5},"0x0004001C : Active group = 4"]
["Password Control","Password Unlocked - User Interface","0002",null,"PW Unlocked UI",4]
[null,"Password Invalid - User Interface","0002",null,"PW Invalid UI",5]
[null,"Password Modified level 1 - User Interface","00D2",null,"PW1 Modified UI",6]
[null,"Password Modified level 2 - User Interface","00D3",null,"PW2 Modified UI",7]
[null,"Password Expired - User Interface","0002",null,"PW Expired UI",8]
[null,"Password Unlocked - Front Port","0002",null,"PW Unlocked F",9]
[null,"Password Invalid - Front Port","0002",null,"PW Invalid F",10]
[null,"Password Modified level 1 - Front Port","00D2",null,"PW1 Modified F",11]
[null,"Password Modified level 2 - Front Port","00D3",null,"PW2 Modified F",12]
[null,"Password Expired - Front Port","0002",null,"PW Expired F",13]
[null,"Password Unlocked - Rear Port 1","0002",null,"PW Unlocked R",14]
[null,"Password Invalid - Rear Port 1","0002",null,"PW Invalid R",15]
[null,"Password Modified level 1 - Rear Port 1","00D2",null,"PW1 Modified R",16]
[null,"Password Modified level 2 - Rear Port 1","00D3",null,"PW2 Modified R",17]
[null,"Password Expired - Rear Port 1","0002",null,"PW Expired R",18]
[null,"Password Unlocked - Rear Port 2","0002",null,"PW Unlocked R2",36]
[null,"Password Invalid - Rear Port 2","0002",null,"PW Invalid R2",37]
[null,"Password Modified level 1 - Rear Port 2","00D2",null,"PW1 Modified R2",38]
[null,"Password Modified level 2 - Rear Port 2","00D3",null,"PW2 Modified R2",39]
[null,"Password Expired - Rear Port 2","0002",null,"PW Expired R2",40]
["General Events","IRIG-B Active","0805",null,"IRIG-B Active",19]
[null,"IRIG-B Inactive","0805",null,"IRIG-B Inactive",20]
[null,"Time Synchronisation","0801",null,"Time Synch",21]
[null,"Indications Reset (LED's & Latched Relays)","01FF",null,"Indication Reset",29]
[null,"Power On","FFFF",null,"Power On",30]
[null,"Bad GOOSE Scheme Logic (UCA2 Only)","FFFF",null,"Bad GOOSE Logic",31]
[null,"Bad Masks (UCA2 Only)","FFFF",null,"Bad Masks",32]
[null,"Bad Reporting Deadbands (UCA2 Only)","FFFF",null,"Bad Deadbands",33]
[null,"Bad Device Identity (UCA2 Only)","FFFF",null,"Bad DI Object",34]
[null,"Second Rear Port Card Failure","FFFF",null,"Rear Comm 2 Fail",35]
[null,"Fibre Port not fitted","FFFF",null,"No Fibre Card",41]
[null,"Ethernet Card network link fail (UCA2 Only)","FFFF",null,"NIC Link Fail",42]
["Events and Records","Alarms Cleared","FFFF",null,"Alarms Cleared",0]
[null,"Events Cleared","0B01",null,"Events Cleared",1]
[null,"Fault Records Cleared","0B02",null,"Faults Cleared",2]
[null,"Maintenance Records Cleared","0B03",null,"Maint Cleared",3]
[null,"Disturbance Records Cleared","0B30",null,"Dist Rec Cleared",43]

{"sheet":"IEC60870-5-103","index":5,"n_rows":1771,"n_cols":40,"rows_kept":1771,"cut":false,"hidden":false,"merged":[[1770,38,1770,39],[1766,38,1767,39],[1765,0,1765,39],[1768,4,1768,5],[1769,4,1769,5],[1770,4,1770,5],[1766,4,1767,5],[1766,6,1766,37],[1768,38,1768,39],[1769,38,1769,39],[1766,0,1767,0],[1766,1,1767,1],[1766,2,1767,2],[1766,3,1767,3],[1763,4,1763,5],[1763,38,1763,39],[1761,4,1761,5],[1761,38,1761,39],[1762,4,1762,5],[1762,38,1762,39],[1759,4,1759,5],[1759,38,1759,39],[1760,4,1760,5],[1760,38,1760,39],[1757,4,1757,5],[1757,38,1757,39],[1758,4,1758,5],[1758,38,1758,39],[1755,4,1755,5],[1755,38,1755,39],[1756,4,1756,5],[1756,38,1756,39],[1753,4,1753,5],[1753,38,1753,39],[1754,4,1754,5],[1754,38,1754,39],[1751,4,1751,5],[1751,38,1751,39],[1752,4,1752,5],[1752,38,1752,39],[1749,4,1749,5],[1749,38,1749,39],[1750,4,1750,5],[1750,38,1750,39],[1747,4,1747,5],[1747,38,1747,39],[1748,4,1748,5],[1748,38,1748,39],[1745,4,1745,5],[1745,38,1745,39],[1746,4,1746,5],[1746,38,1746,39],[1743,4,1743,5],[1743,38,1743,39],[1744,4,1744,5],[1744,38,1744,39],[1741,4,1741,5],[1741,38,1741,39],[1742,4,1742,5],[1742,38,1742,39],[1739,4,1739,5],[1739,38,1739,39],[1740,4,1740,5],[1740,38,1740,39],[1737,4,1737,5],[1737,38,1737,39],[1738,4,1738,5],[1738,38,1738,39],[1733,4,1733,5],[1733,38,1733,39],[1734,4,1734,5],[1734,38,1734,39],[1731,4,1731,5],[1731,38,1731,39],[1732,4,1732,5],[1732,38,1732,39],[1729,4,1729,5],[1729,38,1729,39],[1730,4,1730,5],[1730,38,1730,39],[1727,4,1727,5],[1727,38,1727,39],[1728,4,1728,5],[1728,38,1728,39],[1725,4,1725,5],[1725,38,1725,39],[1726,4,1726,5],[1726,38,1726,39],[1723,4,1723,5],[1723,38,1723,39],[1724,4,1724,5],[1724,38,1724,39],[1721,4,1721,5],[1721,38,1721,39],[1722,4,1722,5],[1722,38,1722,39],[1719,4,1719,5],[1719,38,1719,39],[1720,4,1720,5],[1720,38,1720,39],[1717,4,1717,5],[1717,38,1717,39],[1718,4,1718,5],[1718,38,1718,39],[1715,4,1715,5],[1715,38,1715,39],[1716,4,1716,5],[1716,38,1716,39],[1713,4,1713,5],[1713,38,1713,39],[1714,4,1714,5],[1714,38,1714,39],[1711,4,1711,5],[1711,38,1711,39],[1712,4,1712,5],[1712,38,1712,39],[1709,4,1709,5],[1709,38,1709,39],[1710,4,1710,5],[1710,38,1710,39],[1707,4,1707,5],[1707,38,1707,39],[1708,4,1708,5],[1708,38,1708,39],[1705,4,1705,5],[1705,38,1705,39],[1706,4,1706,5],[1706,38,1706,39],[1703,4,1703,5],[1703,38,1703,39],[1704,4,1704,5],[1704,38,1704,39],[1701,4,1701,5],[1701,38,1701,39],[1702,4,1702,5],[1702,38,1702,39],[1699,4,1699,5],[1699,38,1699,39],[1700,4,1700,5],[1700,38,1700,39],[1698,4,1698,5],[1698,38,1698,39],[1696,4,1696,5],[1696,38,1696,39],[1697,4,1697,5],[1697,38,1697,39],[1694,4,1694,5],[1694,38,1694,39],[1695,4,1695,5],[1695,38,1695,39],[1692,4,1692,5],[1692,38,1692,39],[1693,4,1693,5],[1693,38,1693,39],[1690,4,1690,5],[1690,38,1690,39],[1691,4,1691,5],[1691,38,1691,39],[1684,4,1684,5],[1685,4,1685,5],[1689,4,1689,5],[1689,38,1689,39],[1687,4,1687,5],[1687,38,1687,39],[1688,4,1688,5],[1688,38,1688,39],[1679,4,1679,5],[1679,38,1679,39],[1686,4,1686,5],[1686,38,1686,39],[1681,38,1681,39],[1682,38,1682,39],[1680,4,1680,5],[1681,4,1681,5],[1682,4,1682,5],[1683,4,1683,5],[1677,4,1677,5],[1677,38,1677,39],[1678,4,1678,5],[1678,38,1678,39],[1675,4,1675,5],[1675,38,1675,39],[1676,4,1676,5],[1676,38,1676,39],[1673,4,1673,5],[1673,38,1673,39],[1674,4,1674,5],[1674,38,1674,39],[1667,4,1667,5],[1672,38,1672,39],[1672,4,1672,5],[1668,4,1668,5],[1669,4,1669,5],[1670,4,1670,5],[1671,4,1671,5],[1669,38,1669,39],[1670,38,1670,39],[1663,4,1663,5],[1664,4,1664,5],[1665,4,1665,5],[1666,4,1666,5],[1654,4,1655,5],[1660,4,1660,5],[1661,4,1661,5],[1662,4,1662,5],[1656,4,1656,5],[1657,4,1657,5],[1658,4,1658,5],[1659,4,1659,5],[1650,4,1650,5],[1651,4,1651,5],[1652,4,1652,5],[1653,4,1653,5],[1646,4,1646,5],[1647,4,1647,5],[1648,4,1648,5],[1649,4,1649,5],[1642,4,1642,5],[1643,4,1643,5],[1644,4,1644,5],[1645,4,1645,5],[1638,4,1638,5],[1639,4,1639,5],[1640,4,1640,5],[1641,4,1641,5],[1634,4,1634,5],[1635,4,1635,5],[1636,4,1636,5],[1637,4,1637,5],[1630,4,1630,5],[1631,4,1631,5],[1632,4,1632,5],[1633,4,1633,5],[1626,4,1626,5],[1627,4,1627,5],[1628,4,1628,5],[1629,4,1629,5],[1622,4,1622,5],[1623,4,1623,5],[1624,4,1624,5],[1625,4,1625,5],[1618,4,1618,5],[1619,4,1619,5],[1620,4,1620,5],[1621,4,1621,5],[1616,4,1616,5],[1616,38,1616,39],[1617,4,1617,5],[1617,38,1617,39],[1613,4,1613,5],[1613,38,1613,39],[1614,4,1614,5],[1615,4,1615,5],[1609,4,1609,5],[1610,4,1610,5],[1611,4,1611,5],[1612,4,1612,5],[1605,4,1605,5],[1606,4,1606,5],[1607,4,1607,5],[1608,4,1608,5],[1601,4,1601,5],[1602,4,1602,5],[1603,4,1603,5],[1604,4,1604,5],[1597,4,1597,5],[1598,4,1598,5],[1599,4,1599,5],[1600,4,1600,5],[1683,38,1683,39],[1684,38,1684,39],[1685,38,1685,39],[1574,0,1589,1],[1590,4,1590,5],[1591,4,1591,5],[1592,4,1592,5],[1593,4,1593,5],[1594,4,1594,5],[1668,38,1668,39],[1680,38,1680,39],[1671,38,1671,39],[1664,38,1664,39],[1665,38,1665,39],[1666,38,1666,39],[1667,38,1667,39],[1660,38,1660,39],[1661,38,1661,39],[1662,38,1662,39],[1663,38,1663,39],[1656,38,1656,39],[1657,38,1657,39],[1658,38,1658,39],[1659,38,1659,39],[1650,38,1650,39],[1651,38,1651,39],[1652,38,1652,39],[1653,38,1653,39],[1646,38,1646,39],[1647,38,1647,39],[1648,38,1648,39],[1649,38,1649,39],[1642,38,1642,39],[1643,38,1643,39],[1644,38,1644,39],[1645,38,1645,39],[1638,38,1638,39],[1639,38,1639,39],[1640,38,1640,39],[1641,38,1641,39],[1634,38,1634,39],[1635,38,1635,39],[1636,38,1636,39],[1637,38,1637,39],[1630,38,1630,39],[1631,38,1631,39],[1632,38,1632,39],[1633,38,1633,39],[1626,38,1626,39],[1627,38,1627,39],[1628,38,1628,39],[1629,38,1629,39],[1622,38,1622,39],[1623,38,1623,39],[1624,38,1624,39],[1625,38,1625,39],[1618,38,1618,39],[1619,38,1619,39],[1620,38,1620,39],[1621,38,1621,39],[1611,38,1611,39],[1612,38,1612,39],[1614,38,1614,39],[1615,38,1615,39],[1608,38,1608,39],[1609,38,1609,39],[1610,38,1610,39],[1605,38,1605,39],[1606,38,1606,39],[1607,38,1607,39],[1601,38,1601,39],[1602,38,1602,39],[1603,38,1603,39],[1604,38,1604,39],[1597,38,1597,39],[1598,38,1598,39],[1599,38,1599,39],[1600,38,1600,39],[1593,38,1593,39],[1594,38,1594,39],[1595,38,1595,39],[1596,38,1596,39],[1590,38,1590,39],[1591,38,1591,39],[1592,38,1592,39],[1588,38,1588,39],[1589,4,1589,5],[1589,38,1589,39],[1585,38,1585,39],[1586,4,1586,5],[1586,38,1586,39],[1587,4,1587,5],[1587,38,1587,39],[1582,38,1582,39],[1583,4,1583,5],[1583,38,1583,39],[1584,4,1584,5],[1584,38,1584,39],[1579,38,1579,39],[1580,4,1580,5],[1580,38,1580,39],[1581,4,1581,5],[1581,38,1581,39],[1575,6,1575,37],[1575,38,1576,39],[1578,4,1578,5],[1578,38,1578,39],[1577,4,1577,5],[1577,38,1577,39],[1761,2,1761,3],[1762,2,1762,3],[1763,2,1763,3],[1575,4,1576,5],[1579,4,1579,5],[1582,4,1582,5],[1585,4,1585,5],[1588,4,1588,5],[1595,4,1595,5],[1596,4,1596,5],[1757,2,1757,3],[1758,2,1758,3],[1759,2,1759,3],[1760,2,1760,3],[1753,2,1753,3],[1754,2,1754,3],[1755,2,1755,3],[1756,2,1756,3],[1749,2,1749,3],[1750,2,1750,3],[1751,2,1751,3],[1752,2,1752,3],[1745,2,1745,3],[1746,2,1746,3],[1747,2,1747,3],[1748,2,1748,3],[1741,2,1741,3],[1742,2,1742,3],[1743,2,1743,3],[1744,2,1744,3],[1737,2,1737,3],[1738,2,1738,3],[1739,2,1739,3],[1740,2,1740,3],[1731,2,1731,3],[1732,2,1732,3],[1733,2,1733,3],[1734,2,1734,3],[1727,2,1727,3],[1728,2,1728,3],[1729,2,1729,3],[1730,2,1730,3],[1723,2,1723,3],[1724,2,1724,3],[1725,2,1725,3],[1726,2,1726,3],[1719,2,1719,3],[1720,2,1720,3],[1721,2,1721,3],[1722,2,1722,3],[1715,2,1715,3],[1716,2,1716,3],[1717,2,1717,3],[1718,2,1718,3],[1711,2,1711,3],[1712,2,1712,3],[1713,2,1713,3],[1714,2,1714,3],[1707,2,1707,3],[1708,2,1708,3],[1709,2,1709,3],[1710,2,1710,3],[1703,2,1703,3],[1704,2,1704,3],[1705,2,1705,3],[1706,2,1706,3],[1699,2,1699,3],[1700,2,1700,3],[1701,2,1701,3],[1702,2,1702,3],[1696,2,1696,3],[1697,2,1697,3],[1698,2,1698,3],[1692,2,1692,3],[1693,2,1693,3],[1694,2,1694,3],[1695,2,1695,3],[1689,2,1689,3],[1690,2,1690,3],[1691,2,1691,3],[1685,2,1685,3],[1686,2,1686,3],[1687,2,1687,3],[1688,2,1688,3],[1681,2,1681,3],[1682,2,1682,3],[1683,2,1683,3],[1684,2,1684,3],[1677,2,1677,3],[1678,2,1678,3],[1679,2,1679,3],[1680,2,1680,3],[1673,2,1673,3],[1674,2,1674,3],[1675,2,1675,3],[1676,2,1676,3],[1670,2,1670,3],[1671,2,1671,3],[1672,2,1672,3],[1666,2,1666,3],[1667,2,1667,3],[1668,2,1668,3],[1669,2,1669,3],[1662,2,1662,3],[1663,2,1663,3],[1664,2,1664,3],[1665,2,1665,3],[1652,2,1652,3],[1653,2,1653,3],[1656,2,1656,3],[1657,2,1657,3],[1654,2,1655,3],[1648,2,1648,3],[1649,2,1649,3],[1650,2,1650,3],[1651,2,1651,3],[1644,2,1644,3],[1645,2,1645,3],[1646,2,1646,3],[1647,2,1647,3],[1641,2,1641,3],[1642,2,1642,3],[1643,2,1643,3],[1637,2,1637,3],[1638,2,1638,3],[1639,2,1639,3],[1640,2,1640,3],[1633,2,1633,3],[1634,2,1634,3],[1635,2,1635,3],[1636,2,1636,3],[1630,2,1630,3],[1631,2,1631,3],[1632,2,1632,3],[1626,2,1626,3],[1627,2,1627,3],[1628,2,1628,3],[1629,2,1629,3],[1622,2,1622,3],[1623,2,1623,3],[1624,2,1624,3],[1625,2,1625,3],[1618,2,1618,3],[1619,2,1619,3],[1620,2,1620,3],[1621,2,1621,3],[1615,2,1615,3],[1616,2,1616,3],[1617,2,1617,3],[1611,2,1611,3],[1612,2,1612,3],[1613,2,1613,3],[1614,2,1614,3],[1607,2,1607,3],[1608,2,1608,3],[1609,2,1609,3],[1610,2,1610,3],[1604,2,1604,3],[1605,2,1605,3],[1606,2,1606,3],[1600,2,1600,3],[1601,2,1601,3],[1602,2,1602,3],[1603,2,1603,3],[1596,2,1596,3],[1597,2,1597,3],[1598,2,1598,3],[1599,2,1599,3],[1593,2,1593,3],[1594,2,1594,3],[1595,2,1595,3],[1590,2,1590,3],[1591,2,1591,3],[1592,2,1592,3],[1586,2,1586,3],[1587,2,1587,3],[1588,2,1588,3],[1589,2,1589,3],[1582,2,1582,3],[1583,2,1583,3],[1584,2,1584,3],[1585,2,1585,3],[1579,2,1579,3],[1580,2,1580,3],[1575,2,1576,3],[1581,2,1581,3],[1577,2,1577,3],[1578,2,1578,3],[1573,0,1573,255],[1574,2,1574,39],[1568,38,1568,39],[1569,38,1569,39],[1571,38,1571,39],[1572,38,1572,39],[1570,38,1570,39],[1564,38,1564,39],[1565,0,1565,39],[1566,38,1566,39],[1567,38,1567,39],[1560,0,1561,0],[1560,1,1561,1],[1562,38,1562,39],[1563,38,1563,39],[1560,36,1561,36],[1560,37,1561,37],[1560,4,1561,5],[1560,2,1561,2],[1560,3,1561,3],[1560,32,1561,32],[1560,33,1561,33],[1560,34,1561,34],[1560,35,1561,35],[1560,28,1561,28],[1560,29,1561,29],[1560,30,1561,30],[1560,31,1561,31],[1560,24,1561,24],[1560,25,1561,25],[1560,26,1561,26],[1560,27,1561,27],[1560,20,1561,20],[1560,21,1561,21],[1560,22,1561,22],[1560,23,1561,23],[1560,16,1561,16],[1560,17,1561,17],[1560,18,1561,18],[1560,19,1561,19],[1560,12,1561,12],[1560,13,1561,13],[1560,14,1561,14],[1560,15,1561,15],[1557,6,1557,37],[1557,0,1558,5],[1559,0,1559,39],[1560,38,1561,39],[1560,6,1561,6],[1560,7,1561,7],[1560,8,1561,8],[1560,9,1561,9],[1560,10,1561,10],[1560,11,1561,11],[1553,0,1553,39],[1554,0,1554,39],[1555,0,1555,39],[1556,0,1556,39],[1557,38,1558,39],[1542,38,1542,39],[1543,38,1543,39],[1544,38,1544,39],[1545,38,1545,39],[1551,0,1551,39],[1552,0,1552,39],[1546,38,1546,39],[1547,38,1547,39],[1548,38,1549,39],[1538,38,1538,39],[1539,38,1539,39],[1540,38,1540,39],[1541,38,1541,39],[1534,38,1534,39],[1535,38,1535,39],[1536,38,1536,39],[1537,38,1537,39],[1531,38,1531,39],[1532,38,1532,39],[1525,0,1525,39],[1533,38,1533,39],[1527,38,1528,39],[1527,6,1527,37],[1529,38,1529,39],[1530,38,1530,39],[1526,0,1526,30],[1527,0,1528,0],[1527,1,1528,1],[1527,2,1528,2],[1527,3,1528,3],[1527,4,1528,5],[1521,2,1521,4],[1512,5,1520,39],[1522,5,1524,39],[1521,6,1521,39],[1518,2,1518,4],[1519,2,1519,4],[1520,2,1520,4],[1522,2,1522,4],[1511,0,1511,30],[1512,2,1512,4],[1513,2,1513,4],[1550,38,1550,39],[1514,2,1514,4],[1515,2,1515,4],[1516,2,1516,4],[1517,2,1517,4],[1523,2,1523,4],[1524,2,1524,4],[1476,5,1477,5],[1476,38,1477,38],[1476,39,1477,39],[1476,6,1476,37],[147,0,147,5],[1475,0,1475,30],[147,13,147,21],[148,13,148,21],[151,22,151,29],[153,0,153,5],[153,13,153,21],[152,22,152,29],[153,22,153,29],[154,0,154,5],[1476,0,1477,0],[1476,1,1477,1],[1476,2,1477,2],[1476,3,1477,3],[1476,4,1477,4],[0,0,0,39],[1,0,1,4],[1,5,1,39],[12,0,12,4],[2,0,2,4],[2,5,2,39],[3,0,3,4],[4,0,4,4],[3,5,3,39],[4,5,4,39],[5,5,5,39],[6,5,6,39],[7,5,7,39],[8,0,8,4],[8,5,8,39],[5,0,5,4],[6,0,6,4],[7,0,7,4],[9,0,9,4],[9,5,9,39],[10,5,10,39],[10,0,10,4],[13,0,13,4],[11,5,11,39],[12,5,12,39],[13,5,13,39],[11,0,11,4],[14,0,14,4],[14,5,14,39],[15,0,15,4],[15,5,15,39],[16,0,16,39],[17,0,17,39],[18,0,19,0],[18,1,19,1],[18,2,19,2],[18,3,19,3],[18,4,19,4],[18,5,19,5],[18,6,18,37],[18,38,19,38],[18,39,19,39],[20,0,20,39],[27,0,27,39],[28,0,28,39],[44,0,44,39],[54,0,54,39],[60,0,60,39],[93,0,93,39],[80,0,81,0],[80,1,81,1],[80,2,81,2],[80,3,81,3],[80,4,81,4],[80,5,81,5],[97,0,97,39],[103,0,103,39],[113,0,113,39],[114,0,115,0],[114,1,115,1],[114,2,115,2],[114,3,115,3],[114,4,115,4],[114,5,115,5],[114,6,114,37],[114,38,115,38],[114,39,115,39],[116,0,116,39],[119,0,119,39],[128,0,128,39],[138,0,138,39],[139,0,139,1],[140,0,140,1],[141,0,141,1],[142,0,142,1],[143,0,143,1],[158,0,159,0],[158,1,159,1],[144,0,144,5],[148,0,148,5],[149,0,149,5],[150,0,150,5],[151,0,151,5],[144,6,144,39],[145,0,145,5],[146,0,146,5],[145,13,145,21],[146,13,146,21],[146,22,146,29],[146,31,146,37],[145,6,145,12],[145,22,145,37],[146,6,146,12],[147,6,147,12],[148,6,148,12],[149,6,149,12],[150,6,150,12],[151,6,151,12],[152,6,152,12],[153,6,153,12],[152,0,152,5],[149,13,149,21],[150,13,150,21],[151,13,151,21],[152,13,152,21],[147,22,147,29],[148,22,148,29],[149,22,149,29],[150,22,150,29],[147,31,147,37],[148,31,148,37],[149,31,149,37],[153,31,153,37],[152,31,152,37],[150,31,150,37],[151,31,151,37],[154,31,154,37],[155,31,155,37],[157,0,157,39],[154,6,154,12],[155,0,155,5],[155,6,155,12],[154,13,154,21],[155,13,155,21],[154,22,154,29],[155,22,155,29],[158,6,158,37],[158,38,159,38],[158,39,159,39],[156,0,156,39],[158,2,159,2],[158,3,159,3],[158,4,159,4],[158,5,159,5],[80,6,80,37],[80,38,81,38],[80,39,81,39],[238,0,239,0],[238,1,239,1],[238,2,239,2],[238,3,239,3],[238,4,239,4],[238,5,239,5],[238,6,238,37],[238,38,239,38],[238,39,239,39],[317,0,318,0],[317,1,318,1],[317,2,318,2],[317,3,318,3],[317,4,318,4],[317,5,318,5],[317,6,317,37],[317,38,318,38],[317,39,318,39],[396,0,397,0],[396,1,397,1],[396,2,397,2],[396,3,397,3],[396,4,397,4],[396,5,397,5],[396,6,396,37],[396,38,397,38],[396,39,397,39],[476,0,477,0],[476,1,477,1],[476,2,477,2],[476,3,477,3],[476,4,477,4],[476,5,477,5],[476,6,476,37],[476,38,477,38],[476,39,477,39],[550,0,551,0],[550,1,551,1],[550,2,551,2],[550,3,551,3],[550,4,551,4],[550,5,551,5],[550,6,550,37],[550,38,551,38],[550,39,551,39],[623,0,624,0],[623,1,624,1],[623,2,624,2],[623,3,624,3],[623,4,624,4],[623,5,624,5],[623,6,623,37],[623,38,624,38],[623,39,624,39],[697,0,698,0],[697,1,698,1],[697,2,698,2],[697,3,698,3],[697,4,698,4],[697,5,698,5],[697,6,697,37],[697,38,698,38],[697,39,698,39],[775,0,776,0],[775,1,776,1],[775,2,776,2],[775,3,776,3],[775,4,776,4],[775,5,776,5],[775,6,775,37],[775,38,776,38],[775,39,776,39],[848,0,849,0],[848,1,849,1],[848,2,849,2],[848,3,849,3],[848,4,849,4],[848,5,849,5],[848,6,848,37],[848,38,849,38],[848,39,849,39],[917,0,918,0],[917,1,918,1],[917,2,918,2],[917,3,918,3],[917,4,918,4],[917,5,918,5],[917,6,917,37],[917,38,918,38],[917,39,918,39],[982,0,983,0],[982,1,983,1],[982,2,983,2],[982,3,983,3],[982,4,983,4],[982,5,983,5],[982,6,982,37],[982,38,983,38],[982,39,983,39],[1063,0,1064,0],[1063,1,1064,1],[1063,2,1064,2],[1063,3,1064,3],[1063,4,1064,4],[1063,5,1064,5],[1063,6,1063,37],[1063,38,1064,38],[1063,39,1064,39],[1144,0,1145,0],[1144,1,1145,1],[1144,2,1145,2],[1144,3,1145,3],[1144,4,1145,4],[1144,5,1145,5],[1144,6,1144,37],[1144,38,1145,38],[1144,39,1145,39],[1223,0,1224,0],[1223,1,1224,1],[1223,2,1224,2],[1223,3,1224,3],[1223,4,1224,4],[1223,5,1224,5],[1223,6,1223,37],[1223,38,1224,38],[1223,39,1224,39],[1296,0,1297,0],[1296,1,1297,1],[1296,2,1297,2],[1296,3,1297,3],[1296,4,1297,4],[1296,5,1297,5],[1296,6,1296,37],[1296,38,1297,38],[1296,39,1297,39],[1372,0,1373,0],[1372,1,1373,1],[1372,2,1373,2],[1372,3,1373,3],[1372,4,1373,4],[1372,5,1373,5],[1372,6,1372,37],[1372,38,1373,38],[1372,39,1373,39],[1453,0,1454,0],[1453,1,1454,1],[1453,2,1454,2],[1453,3,1454,3],[1453,4,1454,4],[1453,5,1454,5],[1453,6,1453,37],[1453,38,1454,38],[1453,39,1454,39],[1654,6,1654,37],[1654,38,1655,39],[1735,2,1736,3],[1735,4,1736,5],[1735,6,1735,37],[1735,38,1736,39],[1658,2,1658,3],[1659,2,1659,3],[1660,2,1660,3],[1661,2,1661,3]],"flags":["formulas_cached_only"]}
["IEC60870-5-103 Device Profile"]
["Vendor Name:",{"$nulls":4},"Schneider Electric "]
["Device Name:",{"$nulls":4},"P140 Feeder Protection"]
["Models Covered:",{"$nulls":4},"P141****3**41**"]
[{"$nulls":5},"P142****3**41**"]
[{"$nulls":5},"P143****3**41**"]
[{"$nulls":5},"P144****3**41**"]
[{"$nulls":5},"P145****3**41**"]
["Compatibility Level:",{"$nulls":4},2]
["Physical Layer"]
["Electrical Interface:",{"$nulls":4},"EIA485"]
["Number of Loads:",{"$nulls":4},"1 for one protection equipment"]
["Optical Interface (Order Option)",{"$nulls":4},"Plastic fibre BFOC/2.5 type connector"]
["Transmission Speed:",{"$nulls":4},"9600 or 19200bps (user setting)"]
["Application Layer"]
["Common address of ASDU = Link Address"]
[]
["Compatible Range Information Numbers in Monitor Direction"]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"Interpretation","DDB Ordinal"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
["System Functions"]
[8,10,255,0,"End of General Interrogration",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[6,8,255,0,"Time Synchronisation",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[5,3,160,2,"Reset FCB",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[5,4,160,3,"Reset CU",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[5,5,160,4,"Start/Restart",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[5,6,160,5,"Power On",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["Note: Indentification message in ASDU 5: \"MiCOM P\" + 16bit model + 8bit major version + 1 character minor version e.g. MiCOM P\" + 143 +  11 + 'C'"]
["Status Indications"]
[1,"1, 7, 9, 11, 12, 20, 21",160,16,"Auto-recloser active","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Autoreclose In Service",361]
[1,"1, 7, 9, 11, 12, 20, 21",160,17,"Tele-protection active","*"]
[1,"1, 7, 9, 11, 12, 20, 21",160,18,"Protection active","*"]
[1,"1, 7, 11, 12, 20,  21",160,19,"LED Reset",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Reset Indications"]
[1,"9, 11",160,20,"Monitor direction blocked","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Monitor Direction Blocked",465]
[1,"1, 9, 11",160,21,"Test mode","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Test Mode (Protection Disabled)",441]
[1,"9, 11",160,22,"Local parameter setting","*"]
[1,"1, 7, 9, 11, 12, 20, 21",160,23,"Characteristic 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","PG1 Changed"]
[1,"1, 7, 9, 11, 12, 20, 21",160,24,"Characteristic 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","PG2 Changed"]
[1,"1, 7, 9, 11, 12, 20, 21",160,25,"Characteristic 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","PG3 Changed"]
[1,"1, 7, 9, 11, 12, 20, 21",160,26,"Characteristic 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","PG4 Changed"]
[1,"1, 7, 9, 11",160,27,"Auxillary input 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_1",32]
[1,"1, 7, 9, 11",160,28,"Auxillary input 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_2",33]
[1,"1, 7, 9, 11",160,29,"Auxillary input 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_3",34]
[1,"1, 7, 9, 11",160,30,"Auxillary input 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_4",35]
["Supervision Indications"]
[1,"1, 7, 9",160,32,"Measurand supervision I","*"]
[1,"1, 7, 9",160,33,"Measurand supervision V","*"]
[1,"1, 7, 9",160,35,"Phase sequence supervision","*"]
[1,"1, 7, 9",160,36,"Trip circuit supervision","*"]
[1,"1, 7, 9",160,37,"I>> back-up supervision","*"]
[1,"1, 7, 9",160,38,"VT fuse failure","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_INDICATION",148]
[1,"1, 7, 9",160,39,"Teleprotection disturbed","*"]
[1,"1, 7, 9",160,46,"Group warning","*"]
[1,"1, 7, 9",160,47,"Group alarm","*"]
["Earth Fault Indications"]
[1,"1, 7, 9",160,48,"Earth Fault L1","*"]
[1,"1, 7, 9",160,49,"Earth Fault L2","*"]
[1,"1, 7, 9",160,50,"Earth Fault L3","*"]
[1,"1, 7, 9",160,51,"Earth Fault Fwd","*"]
[1,"1, 7, 9",160,52,"Earth Fault Rev","*"]
["Fault Indications"]
[1,"1, 7, 9",160,64,"Start /pickup L1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_A_START",296]
[1,"1, 7, 9",160,65,"Start /pickup L2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_B_START",297]
[1,"1, 7, 9",160,66,"Start /pickup L3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_C_START",298]
[1,"1, 7, 9",160,67,"Start /pickup N","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_1_START",315]
[2,"1, 7",160,68,"General Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ANY_TRIP",536]
[2,"1, 7",160,69,"Trip L1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_A_TRIP",244]
[2,"1, 7",160,70,"Trip L2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_B_TRIP",245]
[2,"1, 7",160,71,"Trip L3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_C_TRIP",246]
[2,"1, 7",160,72,"Trip I>> (back up)"]
[4,"1, 7",160,73,"Fault Location in ohms",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[2,"1, 7",160,74,"Fault forward"]
[2,"1, 7",160,75,"Fault reverse"]
[2,"1, 7",160,76,"Teleprotection signal sent"]
[2,"1, 7",160,77,"Teleprotection signal received"]
[2,"1, 7",160,78,"Zone 1"]
[2,"1, 7",160,79,"Zone 2"]
[2,"1, 7",160,80,"Zone 3"]
[2,"1, 7",160,81,"Zone 4"]
[2,"1, 7",160,82,"Zone 5"]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"Interpretation","DDB Ordinal"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
[2,"1, 7",160,83,"Zone 6"]
[1,"1, 7, 9",160,84,"General Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Any Start",294]
[2,"1, 7",160,85,"Breaker Failure",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","CB Fail Alarm",150]
[2,"1, 7",160,86,"Trip measuring system L1"]
[2,"1, 7",160,87,"Trip measuring system L2"]
[2,"1, 7",160,88,"Trip measuring system L3"]
[2,"1, 7",160,89,"Trip measuring system E"]
[2,"1, 7",160,90,"Trip I>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","I>1 Trip",243]
[2,"1, 7",160,91,"Trip I>>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","I>3 Trip",251]
[2,"1, 7",160,92,"Trip IN>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","IN1>1 Trip",261]
[2,"1, 7",160,93,"Trip IN>>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","IN1>3 Trip",263]
["Auto-Reclose Indications"]
[2,"1, 7",160,128,"CB 'on' by A/R",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Autoreclose Close Signal",371]
[2,"1, 7",160,129,"CB 'on' by long time A/R"]
[1,"1, 7, 9",160,130,"AR blocked","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Autoreclose Lockout",163]
["Measurands"]
[3.1,"2, 7",160,144,"Measurand I"]
[3.2,"2, 7",160,145,"Measurands I, V"]
[3.3,"2, 7",160,146,"Measurands I, V, P, Q"]
[3.4,"2, 7",160,147,"Measurands IN, VEN"]
[9,"2, 7",160,148,"Measurands IL1, 2, 3, VL1, 2, 3, P, Q, f",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Note unavailable measurands sent as invalid"]
["Generic Functions"]
[10,"42, 43",160,240,"Read Headings"]
[10,"42, 43",160,241,"Read attributes of all entries of a group"]
[10,"42, 43",160,243,"Read directory of entry"]
[10,"1, 2, 7, 9, 11, 12,  42, 43",160,244,"Real attribute of entry","*"]
[10,10,160,245,"End of GGI"]
[10,"41, 44",160,249,"Write entry with confirm"]
[10,"40, 41",160,250,"Write entry with execute"]
[10,40,160,251,"Write entry aborted"]
[]
["Compatible Range Information Numbers in Control Direction"]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"Interpretation","DDB Ordinal"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
["System Functions"]
[7,9,255,0,"Init General Interrogation",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[6,8,255,0,"Time Synchronisation",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["General Commands"]
[20,20,160,16,"Auto-recloser on/off",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Autoreclose in Service",361]
[20,20,160,17,"Teleprotection on/off"]
[20,20,160,18,"Protection on/off"]
[20,20,160,19,"LED Reset",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Reset Indications and Latches"]
[20,20,160,23,"Activate characteristic 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Activate Setting Group 1"]
[20,20,160,24,"Activate characteristic 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Activate Setting Group 2"]
[20,20,160,25,"Activate characteristic 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Activate Setting Group 3"]
[20,20,160,26,"Activate characteristic 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Activate Setting Group 4"]
["Generic Functions"]
[21,42,160,240,"Read headings of all defined groups"]
[21,42,160,241,"Read single attribute of all entries of a group"]
[21,42,160,243,"Read directory of single entry"]
[21,42,160,244,"Read attribute of sngle entry"]
[21,9,160,245,"Generic General Interrogation (GGI)"]
[10,40,160,248,"Write entry"]
[10,40,160,249,"Write with confirm"]
[10,40,160,250,"Write with execute"]
[10,40,160,251,"Write entry abort"]
["Basic Application Functions"]
["Test Mode ",null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Test Mode (Protection Disabled)",441]
["Blocking of monitor direction",null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Monitor Direction Blocked",465]
["Disturbance data",null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["Generic services",null,"*","*"]
["Private data",null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
["Miscellaneous",{"$nulls":5},"Max. MVAL = times rated value"]
["Measurands",{"$nulls":5},1.2,{"$nulls":15},2.4]
["Current L1",{"$nulls":29},"*"]
["Current L2",{"$nulls":29},"*"]
["Current L3",{"$nulls":29},"*"]
["Voltage L1-E",{"$nulls":29},"*"]
["Voltage L2-E",{"$nulls":29},"*"]
["Voltage L3-E",{"$nulls":29},"*"]
["Active Power P",{"$nulls":29},"*"]
["Reactive Power Q",{"$nulls":29},"*"]
["Frequency F",{"$nulls":29},"*"]
["Voltage L1-L2"]
[]
["Private Range Information Numbers in Monitor Direction"]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[1,"1, 7, 9",162,0,"See menu cell [4B01]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_1",0]
[1,"1, 7, 9",162,1,"See menu cell [4B02]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_2",1]
[1,"1, 7, 9",162,2,"See menu cell [4B03]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_3",2]
[1,"1, 7, 9",162,3,"See menu cell [4B04]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_4",3]
[1,"1, 7, 9",162,4,"See menu cell [4B05]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_5",4]
[1,"1, 7, 9",162,5,"See menu cell [4B06]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_6",5]
[1,"1, 7, 9",162,6,"See menu cell [4B07]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_7",6]
[1,"1, 7, 9",162,7,"See menu cell [4B08]","*",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_8",7]
[1,"1, 7, 9",162,8,"See menu cell [4B09]","*",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_9",8]
[1,"1, 7, 9",162,9,"See menu cell [4B0A]","*",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_10",9]
[1,"1, 7, 9",162,10,"See menu cell [4B0B]","*",null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_11",10]
[1,"1, 7, 9",162,11,"See menu cell [4B0C]","*",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_12",11]
[1,"1, 7, 9",162,12,"See menu cell [4B0D]","*",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_13",12]
[1,"1, 7, 9",162,13,"See menu cell [4B0E]","*",{"$nulls":4},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_14",13]
[1,"1, 7, 9",162,14,"See menu cell [4B0F]","*",{"$nulls":4},"*",null,null,null,"*","*",null,"*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_15",14]
[1,"1, 7, 9",162,15,"See menu cell [4B10]","*",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":5},"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_RELAY_16",15]
[1,"1, 7, 9",162,16,"See menu cell [4B11]","*",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_RELAY_17",16]
[1,"1, 7, 9",162,17,"See menu cell [4B12]","*",{"$nulls":8},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_RELAY_18",17]
[1,"1, 7, 9",162,18,"See menu cell [4B13]","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_RELAY_19",18]
[1,"1, 7, 9",162,19,"See menu cell [4B14]","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_RELAY_20",19]
[1,"1, 7, 9",162,20,"See menu cell [4B15]","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_RELAY_21",20]
[1,"1, 7, 9",162,21,"See menu cell [4B16]","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_RELAY_22",21]
[1,"1, 7, 9",162,22,"See menu cell [4B17]","*",{"$nulls":11},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_RELAY_23",22]
[1,"1, 7, 9",162,23,"See menu cell [4B18]","*",{"$nulls":11},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_RELAY_24",23]
[1,"1, 7, 9",162,24,"See menu cell [4B19]","*",{"$nulls":11},"*",null,null,"*",{"$nulls":12},"*",null,null,"*",null,"DDB_OUTPUT_RELAY_25",24]
[1,"1, 7, 9",162,25,"See menu cell [4B1A]","*",{"$nulls":11},"*",null,null,"*",{"$nulls":12},"*",null,null,"*",null,"DDB_OUTPUT_RELAY_26",25]
[1,"1, 7, 9",162,26,"See menu cell [4B1B]","*",{"$nulls":11},"*",{"$nulls":15},"*",null,null,"*",null,"DDB_OUTPUT_RELAY_27",26]
[1,"1, 7, 9",162,27,"See menu cell [4B1C]","*",{"$nulls":11},"*",{"$nulls":15},"*",null,null,"*",null,"DDB_OUTPUT_RELAY_28",27]
[1,"1, 7, 9",162,28,"See menu cell [4B1D]","*",{"$nulls":11},"*",{"$nulls":15},"*",{"$nulls":4},"DDB_OUTPUT_RELAY_29",28]
[1,"1, 7, 9",162,29,"See menu cell [4B1E]","*",{"$nulls":11},"*",{"$nulls":15},"*",{"$nulls":4},"DDB_OUTPUT_RELAY_30",29]
[1,"1, 7, 9",162,30,"See menu cell [4B1F]","*",{"$nulls":27},"*",{"$nulls":4},"DDB_OUTPUT_RELAY_31",30]
[1,"1, 7, 9",162,31,"See menu cell [4B20]","*",{"$nulls":27},"*",{"$nulls":4},"DDB_OUTPUT_RELAY_32",31]
[1,"1, 7, 9, 11",160,27,"See menu cell [4A01]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_1",32]
[1,"1, 7, 9, 11",160,28,"See menu cell [4A02]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_2",33]
[1,"1, 7, 9, 11",160,29,"See menu cell [4A03]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_3",34]
[1,"1, 7, 9, 11",160,30,"See menu cell [4A04]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_4",35]
[1,"1, 7, 9, 11",162,36,"See menu cell [4A05]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_5",36]
[1,"1, 7, 9, 11",162,37,"See menu cell [4A06]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_6",37]
[1,"1, 7, 9, 11",162,38,"See menu cell [4A07]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_7",38]
[1,"1, 7, 9, 11",162,39,"See menu cell [4A08]","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OPTO_ISOLATOR_8",39]
[1,"1, 7, 9, 11",162,40,"See menu cell [4A09]","*",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_9",40]
[1,"1, 7, 9, 11",162,41,"See menu cell [4A0A]","*",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_10",41]
[1,"1, 7, 9, 11",162,42,"See menu cell [4A0B]","*",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_11",42]
[1,"1, 7, 9, 11",162,43,"See menu cell [4A0C]","*",null,null,"*","*",null,null,"*","*","*","*","*","*","*","*","*","*",null,"*","*",null,null,"*","*","*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_12",43]
[1,"1, 7, 9, 11",162,44,"See menu cell [4A0D]","*",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_13",44]
[1,"1, 7, 9, 11",162,45,"See menu cell [4A0E]","*",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_14",45]
[1,"1, 7, 9, 11",162,46,"See menu cell [4A0F]","*",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_15",46]
[1,"1, 7, 9, 11",162,47,"See menu cell [4A10]","*",null,null,null,"*",null,null,"*","*","*","*","*","*","*","*","*","*",null,null,"*",null,null,"*",null,"*","*","*","*",null,null,"*",null,null,"DDB_OPTO_ISOLATOR_16",47]
[1,"1, 7, 9, 11",162,48,"See menu cell [4A11]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_17",48]
[1,"1, 7, 9, 11",162,49,"See menu cell [4A12]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_18",49]
[1,"1, 7, 9, 11",162,50,"See menu cell [4A13]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_19",50]
[1,"1, 7, 9, 11",162,51,"See menu cell [4A14]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_20",51]
[1,"1, 7, 9, 11",162,52,"See menu cell [4A15]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_21",52]
[1,"1, 7, 9, 11",162,53,"See menu cell [4A16]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_22",53]
[1,"1, 7, 9, 11",162,54,"See menu cell [4A17]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_23",54]
[1,"1, 7, 9, 11",162,55,"See menu cell [4A18]","*",{"$nulls":7},"*",null,"*","*",null,null,"*",{"$nulls":9},"*",null,"*","*",{"$nulls":5},"DDB_OPTO_ISOLATOR_24",55]
[1,"1, 7, 9, 11",162,56,"See menu cell [4A19]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_25",56]
[1,"1, 7, 9, 11",162,57,"See menu cell [4A1A]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_26",57]
[1,"1, 7, 9, 11",162,58,"See menu cell [4A1B]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_27",58]
[1,"1, 7, 9, 11",162,59,"See menu cell [4A1C]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_28",59]
[1,"1, 7, 9, 11",162,60,"See menu cell [4A1D]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_29",60]
[1,"1, 7, 9, 11",162,61,"See menu cell [4A1E]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_30",61]
[1,"1, 7, 9, 11",162,62,"See menu cell [4A1F]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_31",62]
[1,"1, 7, 9, 11",162,63,"See menu cell [4A20]","*",{"$nulls":10},"*",{"$nulls":15},"*",{"$nulls":5},"DDB_OPTO_ISOLATOR_32",63]
[null,null,162,64,"LED 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_1",64]
[null,null,162,65,"LED 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_2",65]
[null,null,162,66,"LED 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_3",66]
[null,null,162,67,"LED 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_4",67]
[null,null,162,68,"LED 5",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_5",68]
[null,null,162,69,"LED 6",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_6",69]
[null,null,162,70,"LED 7",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_7",70]
[null,null,162,71,"LED 8",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_OUTPUT_LED_8",71]
[null,null,162,72,"Relay Cond 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_1",72]
[null,null,162,73,"Relay Cond 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_2",73]
[null,null,162,74,"Relay Cond 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_3",74]
[null,null,162,75,"Relay Cond 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_4",75]
[null,null,162,76,"Relay Cond 5",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_5",76]
[null,null,162,77,"Relay Cond 6",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_6",77]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,162,78,"Relay Cond 7",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_7",78]
[null,null,162,79,"Relay Cond 8",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_8",79]
[null,null,162,80,"Relay Cond 9",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_9",80]
[null,null,162,81,"Relay Cond 10",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_10",81]
[null,null,162,82,"Relay Cond 11",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*",null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_11",82]
[null,null,162,83,"Relay Cond 12",{"$nulls":5},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_12",83]
[null,null,162,84,"Relay Cond 13",{"$nulls":5},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_13",84]
[null,null,162,85,"Relay Cond 14",{"$nulls":5},"*",null,"*","*","*","*","*","*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_14",85]
[null,null,162,86,"Relay Cond 15",{"$nulls":5},"*",null,null,null,"*","*",null,"*","*","*","*","*",null,null,null,"*",null,"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_15",86]
[null,null,162,87,"Relay Cond 16",{"$nulls":9},"*","*",null,"*","*","*","*","*",{"$nulls":5},"*",null,"*","*","*","*","*","*","*","*","*","DDB_OUTPUT_CON_16",87]
[null,null,162,88,"Relay Cond 17",{"$nulls":9},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_CON_17",88]
[null,null,162,89,"Relay Cond 18",{"$nulls":9},"*","*",null,"*","*","*","*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_CON_18",89]
[null,null,162,90,"Relay Cond 19",{"$nulls":9},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_CON_19",90]
[null,null,162,91,"Relay Cond 20",{"$nulls":9},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*","*","*","*","*","DDB_OUTPUT_CON_20",91]
[null,null,162,92,"Relay Cond 21",{"$nulls":9},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_CON_21",92]
[null,null,162,93,"Relay Cond 22",{"$nulls":9},"*","*",null,"*",null,null,"*","*",{"$nulls":8},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_CON_22",93]
[null,null,162,94,"Relay Cond 23",{"$nulls":12},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_CON_23",94]
[null,null,162,95,"Relay Cond 24",{"$nulls":12},"*",null,null,"*",{"$nulls":9},"*","*",null,"*",null,null,"*","*","DDB_OUTPUT_CON_24",95]
[null,null,162,96,"Relay Cond 25",{"$nulls":12},"*",null,null,"*",{"$nulls":12},"*",null,null,"*",null,"DDB_OUTPUT_CON_25",96]
[null,null,162,97,"Relay Cond 26",{"$nulls":12},"*",null,null,"*",{"$nulls":12},"*",null,null,"*",null,"DDB_OUTPUT_CON_26",97]
[null,null,162,98,"Relay Cond 27",{"$nulls":12},"*",{"$nulls":15},"*",null,null,"*",null,"DDB_OUTPUT_CON_27",98]
[null,null,162,99,"Relay Cond 28",{"$nulls":12},"*",{"$nulls":15},"*",null,null,"*",null,"DDB_OUTPUT_CON_28",99]
[null,null,162,100,"Relay Cond 29",{"$nulls":12},"*",{"$nulls":15},"*",{"$nulls":4},"DDB_OUTPUT_CON_29",100]
[null,null,162,101,"Relay Cond 30",{"$nulls":12},"*",{"$nulls":15},"*",{"$nulls":4},"DDB_OUTPUT_CON_30",101]
[null,null,162,102,"Relay Cond 31",{"$nulls":28},"*",{"$nulls":4},"DDB_OUTPUT_CON_31",102]
[null,null,162,103,"Relay Cond 32",{"$nulls":28},"*",{"$nulls":4},"DDB_OUTPUT_CON_32",103]
[null,null,162,104,"LED Cond IN 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_1",104]
[null,null,162,105,"LED Cond IN 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_2",105]
[null,null,162,106,"LED Cond IN 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_3",106]
[null,null,162,107,"LED Cond IN 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_4",107]
[null,null,162,108,"LED Cond IN 5",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_5",108]
[null,null,162,109,"LED Cond IN 6",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_6",109]
[null,null,162,110,"LED Cond IN 7",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_7",110]
[null,null,162,111,"LED Cond IN 8",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":11},"DDB_LED_CON_8",111]
[null,null,162,112,"Timer in 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_1",112]
[null,null,162,113,"Timer in 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_2",113]
[null,null,162,114,"Timer in 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_3",114]
[null,null,162,115,"Timer in 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_4",115]
[null,null,162,116,"Timer in 5",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_5",116]
[null,null,162,117,"Timer in 6",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_6",117]
[null,null,162,118,"Timer in 7",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_7",118]
[null,null,162,119,"Timer in 8",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_8",119]
[null,null,162,120,"Timer in 9",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_9",120]
[null,null,162,121,"Timer in 10",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_10",121]
[null,null,162,122,"Timer in 11",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_11",122]
[null,null,162,123,"Timer in 12",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_12",123]
[null,null,162,124,"Timer in 13",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_13",124]
[null,null,162,125,"Timer in 14",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_14",125]
[null,null,162,126,"Timer in 15",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_15",126]
[null,null,162,127,"Timer in 16",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMERIN_16",127]
[null,null,162,128,"Timer out 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_1",128]
[null,null,162,129,"Timer out 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_2",129]
[null,null,162,130,"Timer out 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_3",130]
[null,null,162,131,"Timer out 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_4",131]
[null,null,162,132,"Timer out 5",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_5",132]
[null,null,162,133,"Timer out 6",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_6",133]
[null,null,162,134,"Timer out 7",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_7",134]
[null,null,162,135,"Timer out 8",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_8",135]
[null,null,162,136,"Timer out 9",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_9",136]
[null,null,162,137,"Timer out 10",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_10",137]
[null,null,162,138,"Timer out 11",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_11",138]
[null,null,162,139,"Timer out 12",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_12",139]
[null,null,162,140,"Timer out 13",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_13",140]
[null,null,162,141,"Timer out 14",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_14",141]
[null,null,162,142,"Timer out 15",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_15",142]
[null,null,162,143,"Timer out 16",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIMEROUT_16",143]
[null,null,162,144,"Fault REC TRIG",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_FAULT_RECORDER_              START",144]
[1,"1, 7, 9",162,145,"SG-opto Invalid","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ILLEGAL_OPTO_                    SETTINGS_GROUP",145]
[1,"9, 11",160,21,"Prot'n Disabled","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OOS_ALARM",146]
[1,"1, 7, 9",162,147,"F out of Range","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_FREQ_ALARM",147]
[1,"1, 7, 9",160,38,"VT Fail Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_INDICATION",148]
[1,"1, 7, 9",162,149,"CT Fail Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CTS_INDICATION",149]
[2,"1, 7",160,85,"CB Fail Alarm",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BREAKER_FAIL_ALARM",150]
[1,"1, 7, 9",162,151,"I^ Maint Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BROKEN_CURRENT_        ALARM",151]
[1,"1, 7, 9",162,152,"I^ Lockout Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BROKEN_CURRENT_       LOCKOUT",152]
[1,"1, 7, 9",162,153,"CB Ops Maint","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_MAINTENANCE_ALARM",153]
[1,"1, 7, 9",162,154,"CB Ops Lockout","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_MAINTENANCE_LOCKOUT",154]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[1,"1, 7, 9",162,155,"CB Op Time Maint","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXCESSIVE_OP_TIME_       ALARM",155]
[1,"1, 7, 9",162,156,"CB Op Time Lock","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXCESSIVE_OP_TIME_          LOCKOUT",156]
[1,"1, 7, 9",162,157,"Fault Freq Lock","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EFF_LOCKOUT",157]
[1,"1, 7, 9",162,158,"CB Status Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_STATUS_ALARM",158]
[1,"1, 7, 9",162,159,"Man CB Trip Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_FAILED_TO_TRIP",159]
[1,"1, 7.9",162,160,"Man CB Cls Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_FAILED_TO_CLOSE",160]
[1,"1, 7, 9",162,161,"Man CB Unhealthy","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_CB_                UNHEALTHY",161]
[1,"1, 7, 9",162,162,"Man No Checksync","*",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_NO_CHECK_           SYNC",162]
[1,"1, 7, 9",160,130,"A/R Lockout","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_LOCKOUT",163]
[1,"1, 7, 9",162,164,"A/R CB Unhealthy","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_CB_UNHEALTHY",164]
[1,"1, 7, 9",162,165,"A/R No Checksync","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_NO_SYS_CHECK",165]
[1,"1, 7, 9",162,166,"System Split","*",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSTEM_SPLIT_ALARM",166]
[1,"1, 7, 9",162,167,"UV Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDERVOLTAGE_BLOCK",167]
[1,"1, 7, 9",162,168,"SR User Alarm 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_1",168]
[1,"1, 7, 9",162,169,"SR User Alarm 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_2",169]
[1,"1, 7, 9",162,170,"SR User Alarm 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_3",170]
[1,"1, 7, 9",162,171,"SR User Alarm 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_4",171]
[1,"1, 7, 9",162,172,"SR User Alarm 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_5",172]
[1,"1, 7, 9",162,173,"SR User Alarm 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_6",173]
[1,"1, 7, 9",162,174,"SR User Alarm 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_7",174]
[1,"1, 7, 9",162,175,"SR User Alarm 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_8",175]
[1,"1, 7, 9",162,176,"SR User Alarm 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_9",176]
[1,"1, 7, 9",162,177,"SR User Alarm 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_10",177]
[1,"1, 7, 9",162,178,"SR User Alarm 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_11",178]
[1,"1, 7, 9",162,179,"SR User Alarm 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_12",179]
[1,"1, 7, 9",162,180,"SR User Alarm 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_13",180]
[1,"1, 7, 9",162,181,"SR User Alarm 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_14",181]
[1,"1, 7, 9",162,182,"SR User Alarm 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_15",182]
[1,"1, 7, 9",162,183,"SR User Alarm 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_16",183]
[1,"1, 7, 9",162,184,"SR User Alarm 17","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_17",184]
[1,"1, 7, 9",162,185,"SR User Alarm 18","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_18",185]
[1,"1, 7, 9",162,186,"MR User Alarm 19","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_19",186]
[1,"1, 7, 9",162,187,"MR User Alarm 20","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_20",187]
[1,"1, 7, 9",162,188,"MR User Alarm 21","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_21",188]
[1,"1, 7, 9",162,189,"MR User Alarm 22","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_22",189]
[1,"1, 7, 9",162,190,"MR User Alarm 23","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_23",190]
[1,"1, 7, 9",162,191,"MR User Alarm 24","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_24",191]
[1,"1, 7, 9",162,192,"MR User Alarm 25","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_25",192]
[1,"1, 7, 9",162,193,"MR User Alarm 26","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_26",193]
[1,"1, 7, 9",162,194,"MR User Alarm 27","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_27",194]
[1,"1, 7, 9",162,195,"MR User Alarm 28","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_28",195]
[1,"1, 7, 9",162,196,"MR User Alarm 29","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_29",196]
[1,"1, 7, 9",162,197,"MR User Alarm 30","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_30",197]
[1,"1, 7, 9",162,198,"MR User Alarm 31","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_31",198]
[1,"1, 7, 9",162,199,"MR User Alarm 32","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_32",199]
[1,"1, 7, 9",162,200,"MR User Alarm 33","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_33",200]
[1,"1, 7, 9",162,201,"MR User Alarm 34","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_34",201]
[1,"1, 7, 9",162,202,"MR User Alarm 35","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_USER_ALARM_35",202]
[null,null,162,203,"I>1 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_TIMER_BLOCK",203]
[null,null,162,204,"I>2 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_TIMER_BLOCK",204]
[null,null,162,205,"I>3 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_TIMER_BLOCK",205]
[null,null,162,206,"I>4 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_TIMER_BLOCK",206]
[null,null,162,207,{"$nulls":34},"DDB_UNUSED_207",207]
[null,null,162,208,"IN1>1 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_1_TIMER_BLOCK",208]
[null,null,162,209,"IN1>2 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_2_TIMER_BLOCK",209]
[null,null,162,210,"IN1>3 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_3_TIMER_BLOCK",210]
[null,null,162,211,"IN1>4 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_4_TIMER_BLOCK",211]
[null,null,162,212,"IN2>1 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_1_TIMER_BLOCK",212]
[null,null,162,213,"IN2>2 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_2_TIMER_BLOCK",213]
[null,null,162,214,"IN2>3 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_3_TIMER_BLOCK",214]
[null,null,162,215,"IN2>4 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_4_TIMER_BLOCK",215]
[null,null,162,216,"ISEF>1 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_1_TIMER_BLOCK",216]
[null,null,162,217,"ISEF>2 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_2_TIMER_BLOCK",217]
[null,null,162,218,"ISEF>3 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_3_TIMER_BLOCK",218]
[null,null,162,219,"ISEF>4 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_4_TIMER_BLOCK",219]
[null,null,162,220,"VN>1 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESOV_1_TIMER_BLOCK",220]
[null,null,162,221,"VN>2 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESOV_2_TIMER_BLOCK",221]
[null,null,162,222,"V<1 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_TIMER_BLOCK",222]
[null,null,162,223,"V<2 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_TIMER_BLOCK",223]
[null,null,162,224,"V>1 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_TIMER_BLOCK",224]
[null,null,162,225,"V>2 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_TIMER_BLOCK",225]
[null,null,162,226,"CLP Initiate",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CLP_INITIATE",226]
[null,null,162,227,"Ext.Trip 3ph",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXTERNAL_TRIP_3PH",227]
[null,null,162,228,"CB Aux 3ph(52-A)",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_THREE_PHASE_52A",228]
[null,null,162,229,"CB Aux 3ph(52-B)",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_THREE_PHASE_52B",229]
[null,null,162,230,"CB Healthy",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_HEALTHY",230]
[null,null,162,231,"MCB/VTS",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_MCB_OPTO",231]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,162,232,"Init Trip CB",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_LOGIC_INPUT_TRIP",232]
[null,null,162,233,"Init Close CB",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_LOGIC_INPUT_CLOSE",233]
[null,null,162,234,"Reset Close Dly",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESET_CB_CLOSE_                DELAY",234]
[null,null,162,235,"Reset Relays/LED",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESET_RELAYS_LEDS",235]
[null,null,162,236,"Reset Thermal",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESET_THERMAL",236]
[null,null,162,237,"Reset Lockout",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESET_LOCKOUT",237]
[null,null,162,238,"Reset CB Data",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESET_ALL_VALUES",238]
[null,null,162,239,"Block A/R",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BLOCK_AR",239]
[null,null,162,240,"Live Line Mode",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_LIVE_LINE_MODE",240]
[null,null,162,241,"Auto Mode",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AUTO_MODE",241]
[null,null,162,242,"Telecontrol Mode",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TELECONTROL_MODE",242]
[2,"1, 7",160,90,"I>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_3PH_TRIP",243]
[2,"1, 7",160,69,"I>1 Trip A",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_A_TRIP",244]
[2,"1, 7",160,70,"I>1 Trip B",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_B_TRIP",245]
[2,"1, 7",160,71,"I>1 Trip C",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_C_TRIP",246]
[2,"1, 7",162,247,"I>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_3PH_TRIP",247]
[2,"1, 7",162,248,"I>2 Trip A",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_PH_A_TRIP",248]
[2,"1, 7",162,249,"I>2 Trip B",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_PH_B_TRIP",249]
[2,"1, 7",162,250,"I>2 Trip C",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_PH_C_TRIP",250]
[2,"1, 7",160,91,"I>3 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_3PH_TRIP",251]
[2,"1, 7",162,252,"I>3 Trip A",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_PH_A_TRIP",252]
[2,"1, 7",162,253,"I>3 Trip B",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_PH_B_TRIP",253]
[2,"1, 7",162,254,"I>3 Trip C",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_PH_C_TRIP",254]
[2,"1, 7",162,255,"I>4 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_3PH_TRIP",255]
[2,"1, 7",163,0,"I>4 Trip A",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_PH_A_TRIP",256]
[2,"1, 7",163,1,"I>4 Trip B",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_PH_B_TRIP",257]
[2,"1, 7",163,2,"I>4 Trip C",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_PH_C_TRIP",258]
[null,null,163,3,{"$nulls":34},"DDB_UNUSED_259",259]
[2,"1, 7",163,4,"Broken Line Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BROKEN_CONDUCTOR_   TRIP",260]
[2,"1, 7",160,92,"IN1>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_1_TRIP",261]
[2,"1, 7",163,6,"IN1>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_2_TRIP",262]
[2,"1, 7",160,93,"IN1>3 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_3_TRIP",263]
[2,"1, 7",163,8,"IN1>4 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_4_TRIP",264]
[2,"1, 7",163,9,"IN2>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_1_TRIP",265]
[2,"1, 7",163,10,"IN2>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_2_TRIP",266]
[2,"1, 7",163,11,"IN2>3 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_3_TRIP",267]
[2,"1, 7",163,12,"IN2>4 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_4_TRIP",268]
[2,"1, 7",163,13,"ISEF>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_1_TRIP",269]
[2,"1, 7",163,14,"ISEF>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_2_TRIP",270]
[2,"1, 7",163,15,"ISEF>3 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_3_TRIP",271]
[2,"1, 7",163,16,"ISEF>4 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_4_TRIP",272]
[2,"1, 7",163,17,"IREF> Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_REF_TRIP",273]
[2,"1, 7",163,18,"VN>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESOV_1_TRIP",274]
[2,"1, 7",163,19,"VN>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESOV_2_TRIP",275]
[2,"1, 7",163,20,"Thermal Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_THERMAL_TRIP",276]
[2,"1, 7",163,21,"V2> Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NEGSEQOV_TRIP",277]
[2,"1, 7",163,22,"V<1 Trip  ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_3PH_TRIP",278]
[2,"1, 7",163,23,"V<1 Trip A/AB",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_PH_A_TRIP",279]
[2,"1, 7",163,24,"V<1 Trip B/BC",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_PH_B_TRIP",280]
[2,"1, 7",163,25,"V<1 Trip C/CA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_PH_C_TRIP",281]
[2,"1, 7",163,26,"V<2 Trip  ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_3PH_TRIP",282]
[2,"1, 7",163,27,"V<2 Trip A/AB ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_PH_A_TRIP",283]
[2,"1, 7",163,28,"V<2 Trip B/BC",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_PH_B_TRIP",284]
[2,"1, 7",163,29,"V<2 Trip C/CA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_PH_C_TRIP",285]
[2,"1, 7",163,30,"V>1 Trip  ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_3PH_TRIP",286]
[2,"1, 7",163,31,"V>1 Trip A/AB",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_PH_A_TRIP",287]
[2,"1, 7",163,32,"V>1 Trip B/BC",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_PH_B_TRIP",288]
[2,"1, 7",163,33,"V>1 Trip C/CA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_PH_C_TRIP",289]
[2,"1, 7",163,34,"V>2  Trip ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_3PH_TRIP",290]
[2,"1, 7",163,35,"V>2 Trip A/AB ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_PH_A_TRIP",291]
[2,"1, 7",163,36,"V>2 Trip B/BC",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_PH_B_TRIP",292]
[2,"1, 7",163,37,"V>2 Trip C/CA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_PH_C_TRIP",293]
[1,"1, 7, 9",160,84,"Any Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ANY_START",294]
[1,"1, 7, 9",163,39,"I>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_3PH_START",295]
[1,"1, 7, 9",160,64,"I>1 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_A_START",296]
[1,"1, 7, 9",160,65,"I>1 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_B_START",297]
[1,"1, 7, 9",160,66,"I>1 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_1_PH_C_START",298]
[1,"1, 7, 9",163,43,"I>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_3PH_START",299]
[1,"1, 7, 9",163,44,"I>2 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_PH_A_START",300]
[1,"1, 7, 9",163,45,"I>2 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_PH_B_START",301]
[1,"1, 7, 9",163,46,"I>2 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_2_PH_C_START",302]
[1,"1, 7, 9",163,47,"I>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_3PH_START",303]
[1,"1, 7, 9",163,48,"I>3 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_PH_A_START",304]
[1,"1, 7, 9",163,49,"I>3 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_PH_B_START",305]
[1,"1, 7, 9",163,50,"I>3 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_3_PH_C_START",306]
[1,"1, 7, 9",163,51,"I>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_3PH_START",307]
[1,"1, 7, 9",163,52,"I>4 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_PH_A_START",308]
[1,"1, 7, 9",163,53,"I>4 Start B","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_PH_B_START",309]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[1,"1, 7, 9",163,54,"I>4 Start C","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POC_4_PH_C_START",310]
[1,"1, 7, 9",163,55,"VCO Start AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VCO_PH_AB_START",311]
[1,"1, 7, 9",163,56,"VCO Start BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VCO_PH_BC_START",312]
[1,"1, 7, 9",163,57,"VCO Start CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VCO_PH_CA_START",313]
[null,null,163,58,{"$nulls":34},"DDB_UNUSED_314",314]
[1,"1, 7, 9",160,67,"IN1>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_1_START",315]
[1,"1, 7, 9",163,60,"IN1>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_2_START",316]
[1,"1, 7, 9",163,61,"IN1>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_3_START",317]
[1,"1, 7, 9",163,62,"IN1>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_4_START",318]
[1,"1, 7, 9",163,63,"IN2>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_1_START",319]
[1,"1, 7, 9",163,64,"IN2>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_2_START",320]
[1,"1, 7, 9",163,65,"IN2>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_3_START",321]
[1,"1, 7, 9",163,66,"IN2>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_4_START",322]
[1,"1, 7, 9",163,67,"ISEF>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_1_START",323]
[1,"1, 7, 9",163,68,"ISEF>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_2_START",324]
[1,"1, 7, 9",163,69,"ISEF>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_3_START",325]
[1,"1, 7, 9",163,70,"ISEF>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_4_START",326]
[1,"1, 7, 9",163,71,"VN>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESOV_1_START",327]
[1,"1, 7, 9",163,72,"VN>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESOV_2_START",328]
[1,"1, 7, 9",163,73,"Thermal Alarm","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_THERMAL_ALARM",329]
[1,"1, 7, 9",163,74,"V2> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NEGSEQOV_START",330]
[1,"1, 7, 9",163,75,"V<1 Start ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_3PH_START",331]
[1,"1, 7, 9",163,76,"V<1 Start A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_PH_A_START",332]
[1,"1, 7, 9",163,77,"V<1 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_PH_B_START",333]
[1,"1, 7, 9",163,78,"V<1 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_1_PH_C_START",334]
[1,"1, 7, 9",163,79,"V<2 Start ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_3PH_START",335]
[1,"1, 7, 9",163,80,"V<2 Start A/AB ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_PH_A_START",336]
[1,"1, 7, 9",163,81,"V<2 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_PH_B_START",337]
[1,"1, 7, 9",163,82,"V<2 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PUV_2_PH_C_START",338]
[1,"1, 7, 9",163,83,"V>1 Start ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_3PH_START",339]
[1,"1, 7, 9",163,84,"V>1 Start A/AB","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_PH_A_START",340]
[1,"1, 7, 9",163,85,"V>1 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_PH_B_START",341]
[1,"1, 7, 9",163,86,"V>1 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_1_PH_C_START",342]
[1,"1, 7, 9",163,87,"V>2 Start ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_3PH_START",343]
[1,"1, 7, 9",163,88,"V>2 Start A/AB ","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_PH_A_START",344]
[1,"1, 7, 9",163,89,"V>2 Start B/BC","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_PH_B_START",345]
[1,"1, 7, 9",163,90,"V>2 Start C/CA","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_POV_2_PH_C_START",346]
[1,"1, 7, 9",163,91,"CLP Operation","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CLP_OPERATION",347]
[1,"1, 7, 9",163,92,"I> BlockStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PH_BLOCKED_OC_          START",348]
[1,"1, 7, 9",163,93,"IN/SEF>Blk Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_N_BLOCKED_OC_START",349]
[null,null,163,94,"VTS Fast Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_FAST_BLOCK",350]
[null,null,163,95,"VTS Slow Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_SLOW_BLOCK",351]
[null,null,163,96,"CTS Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CTS_BLOCK",352]
[1,"1, 7, 9",163,97,"Bfail1 Trip 3ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CBF1_TRIP_3PH",353]
[1,"1, 7, 9",163,98,"Bfail2 Trip 3ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CBF2_TRIP_3PH",354]
[2,"1, 7",163,99,"Control Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_TRIP",355]
[2,"1, 7",163,100,"Control Close",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_CLOSE",356]
[2,"1, 7",163,101,"Close in Prog",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_CLOSE_IN_         PROGRESS",357]
[2,"1, 7",163,102,"Block Main Prot",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_BLOCK_MAIN_        PROTECTION",358]
[2,"1, 7",163,103,"Block SEF Prot",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_BLOCK_SEF_      PROTECTION",359]
[2,"1, 7",163,104,"AR In Progress",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_3_POLE_IN_            PROGRESS",360]
[1,"1, 7, 9, 11, 12, 20, 21",160,16,"AR In Service",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_IN_SERVICE",361]
[null,null,163,106,"Seq Counter = 0",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEQ_COUNT_0",362]
[2,"1, 7",163,107,"Seq Counter = 1",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEQ_COUNT_1",363]
[2,"1, 7",163,108,"Seq Counter = 2",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEQ_COUNT_2",364]
[2,"1, 7",163,109,"Seq Counter = 3",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEQ_COUNT_3",365]
[2,"1, 7",163,110,"Seq Counter = 4",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEQ_COUNT_4",366]
[1,"1, 7, 9",163,111,"Successful Close","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_SUCCESSFUL_         RECLOSE",367]
[2,"1, 7",163,112,"Dead T in Prog",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DEAD_TIME_IN_          PROGRESS",368]
[1,"1, 7, 9",163,113,"Protection Lockt","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_PROTECTION_           LOCKOUT",369]
[1,"1, 7, 9",163,114,"Reset Lckout Alm","*",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_RESET_LOCKOUT_           ALARM",370]
[2,"1, 7",163,115,"Auto Close",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AUTO_CLOSE",371]
[2,"1, 7",163,116,"A/R Trip Test",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_TRIP_TEST",372]
[null,null,163,117,"IA< Start",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PHASE_A_             UNDERCURRENT",373]
[null,null,163,118,"IB< Start",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PHASE_B_             UNDERCURRENT",374]
[null,null,163,119,"IC< Start",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PHASE_C_          UNDERCURRENT",375]
[null,null,163,120,"IN< Start",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF_UNDERCURRENT",376]
[null,null,163,121,"ISEF< Start",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_UNDERCURRENT",377]
[1,"1, 7, 9",163,122,"CB Open 3 ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_OPEN",378]
[1,"1, 7, 9",163,123,"CB Closed 3 ph","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_CLOSED",379]
[null,null,163,124,"All Poles Dead",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ALL_POLEDEAD",380]
[null,null,163,125,"Any Pole Dead",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ANY_POLEDEAD",381]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,163,126,"Pole Dead A",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PHASE_A_POLEDEAD",382]
[null,null,163,127,"Pole Dead B",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PHASE_B_POLEDEAD",383]
[null,null,163,128,"Pole Dead C",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PHASE_C_POLEDEAD",384]
[null,null,163,129,"VTS Acc Ind",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_ACCELERATE_       INPUT",385]
[null,null,163,130,"VTS Volt Dep",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_ANY_VOLTAGE_      DEP_FN",386]
[null,null,163,131,"VTS Ia>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_IA_OPERATED",387]
[null,null,163,132,"VTS Ib>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_IB_OPERATED",388]
[null,null,163,133,"VTS Ic>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_IC_OPERATED",389]
[null,null,163,134,"VTS Va>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_VA_OPERATED",390]
[null,null,163,135,"VTS Vb>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_VB_OPERATED",391]
[null,null,163,136,"VTS Vc>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_VC_OPERATED",392]
[null,null,163,137,"VTS I2>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_I2_OPERATED",393]
[null,null,163,138,"VTS V2>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_V2_OPERATED",394]
[null,null,163,139,"VTS Ia delta>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_DELTA_IA_               OPERATED",395]
[null,null,163,140,"VTS Ib delta>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_DELTA_IB_              OPERATED",396]
[null,null,163,141,"VTS Ic delta > ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_VTS_DELTA_IC_            OPERATED",397]
[null,null,163,142,"CBF SEF Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CURRENT_PROT_SEF_        TRIP",398]
[null,null,163,143,"CBF Non I Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CBF_NON_CURRENT_          PROT_TRIP",399]
[null,null,163,144,"CBF SEF Trip-1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CBF_SEF_STAGE_TRIP",400]
[null,null,163,145,"CBF Non I Trip-1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CBF_NON_CURRENT_        STAGE_TRIP",401]
[null,null,163,146,"Man Check Synch",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYNC_CTRL_SYS_         CHECK_OK",402]
[null,null,163,147,"AR SysChecks OK",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SYNC_AR_SYS_CHECK_OK",403]
[null,null,163,148,"Lockout Alarm",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_LOCKOUT_ALARM",404]
[null,null,163,149,"Pre-Lockout",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_PRE_LOCKOUT",405]
[null,null,163,150,"Freq High",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_FREQ_ABOVE_RANGE_       LIMIT",406]
[null,null,163,151,"Freq Low",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_FREQ_BELOW_RANGE_     LIMIT",407]
[null,null,163,152,"Stop Freq Track",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_FREQ_STOP_TRACK",408]
[null,null,163,153,"Start N",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF_START",409]
[1,"1, 7, 9",163,154,"Field Volts Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_FIELD_VOLTS_FAIL",410]
[null,null,163,155,"Freq Not Found",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_FREQ_NOT_FOUND",411]
[null,null,163,156,"F<1 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_1_TIMER_BLOCK",412]
[null,null,163,157,"F<2 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_2_TIMER_BLOCK",413]
[null,null,163,158,"F<3 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_3_TIMER_BLOCK",414]
[null,null,163,159,"F<4 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_4_TIMER_BLOCK",415]
[null,null,163,160,"F>1 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OFREQ_1_TIMER_BLOCK",416]
[null,null,163,161,"F>2 Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OFREQ_2_TIMER_BLOCK",417]
[1,"1, 7, 9",163,162,"F<1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_1_START",418]
[1,"1, 7, 9",163,163,"F<2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_2_START",419]
[1,"1, 7, 9",163,164,"F<3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_3_START",420]
[1,"1, 7, 9",163,165,"F<4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_4_START",421]
[1,"1, 7, 9",163,166,"F>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OFREQ_1_START",422]
[1,"1, 7, 9",163,167,"F>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OFREQ_2_START",423]
[2,"1, 7",163,168,"F<1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_1_TRIP",424]
[2,"1, 7",163,169,"F<2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_2_TRIP",425]
[2,"1, 7",163,170,"F<3 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_3_TRIP",426]
[2,"1, 7",163,171,"F<4 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UFREQ_4_TRIP",427]
[2,"1, 7",163,172,"F>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OFREQ_1_TRIP",428]
[2,"1, 7",163,173,"F>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OFREQ_2_TRIP",429]
[null,null,163,174,"YN> Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_YN_TIMER_BLOCK",430]
[null,null,163,175,"GN> Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GN_TIMER_BLOCK",431]
[null,null,163,176,"BN> Timer Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BN_TIMER_BLOCK",432]
[1,"1, 7, 9",163,177,"YN> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_YN_START",433]
[1,"1, 7, 9",163,178,"GN> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GN_START",434]
[1,"1, 7, 9",163,179,"BN> Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BN_START",435]
[2,"1, 7",163,180,"YN> Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_YN_TRIP",436]
[2,"1, 7",163,181,"GN> Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GN_TRIP",437]
[2,"1, 7",163,182,"BN> Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BN_TRIP",438]
[null,null,163,183,"Ext AR Prot Trip",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXT_AR_PROT_TRIP",439]
[null,null,163,184,"Ext AR Prot Strt",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXT_AR_PROT_START",440]
[1,"1, 9, 11",160,21,"Test Mode",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TEST_MODE",441]
[null,null,163,186,"Inhibit SEF",null,"*","*",{"$nulls":4},"*",{"$nulls":9},"*",{"$nulls":7},"*",{"$nulls":7},"DDB_SEF_INHIBIT",442]
[null,null,163,187,"Live Line",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_LINE_LIVE",443]
[null,null,163,188,"Dead Line",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_LINE_DEAD",444]
[null,null,163,189,"Live Bus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_BUS_LIVE",445]
[null,null,163,190,"Dead Bus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_BUS_DEAD",446]
[null,null,163,191,"Check Sync 1 OK",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CHECKSYNC_1_OK",447]
[null,null,163,192,"Check Sync 2 OK",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CHECKSYNC_2_OK",448]
[null,null,163,193,"SysChks Inactive",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_INACTIVE",449]
[null,null,163,194,"CS1 Enabled.",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CHECKSYNC_1_           Enabled.",450]
[null,null,163,195,"CS2 Enabled.",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CHECKSYNC_2_         Enabled.",451]
[null,null,163,196,"SysSplit Enabled.",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSTEM_SPLIT_              Enabled.",452]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,163,197,"DAR Complete",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DAR_COMPLETE",453]
[null,null,163,198,"CB in Service",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CB_IN_SERVICE",454]
[null,null,163,199,"AR Restart",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_RESTART",455]
[null,null,163,200,"AR In Progress 1",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_IP_1",456]
[null,null,163,201,"DeadTime Enabled.",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DEADTIME_ENABLE",457]
[null,null,163,202,"DT OK To Start",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DEADTIME_OK_TO_        START",458]
[null,null,163,203,"DT Complete",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DEADTIME_COMPLETE",459]
[null,null,163,204,"Reclose Checks",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ARCHECKS_IN_           PROGRESS",460]
[null,null,163,205,"Circuits OK",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_LIVEDEAD_CCTS_OK",461]
[null,null,163,206,"AR Sync Check",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_AR_SYNC_CHECK",462]
[null,null,163,207,"AR SysChecks OK",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_SYSTEMCHECKS_OK",463]
[null,null,163,208,"AR Init TripTest",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INIT_AR_TRIP_TEST",464]
[1,"1, 7, 9, 11",160,20,"Monitor Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CS103_BLOCK",465]
[1,"1, 7, 9, 11",163,210,"Command Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CS103_CMD_BLOCK",466]
[1,"1, 7, 9",163,211,"SEF 1 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_1_START_2",467]
[1,"1, 7, 9",163,212,"SEF 2 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_2_START_2",468]
[1,"1, 7, 9",163,213,"SEF 3 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_3_START_2",469]
[1,"1, 7, 9",163,214,"SEF 4 Start 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SEF_4_START_2",470]
[1,"1, 7, 9",163,215,"CS1 Slip>","*",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS1_SLIP_ABOVE_        SETTING",471]
[null,null,163,216,"CS1 Slip<",{"$nulls":33},"DDB_CS1_SLIP_BELOW_        SETTING",472]
[1,"1, 7, 9",163,217,"CS2 Slip>","*",{"$nulls":6},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS2_SLIP_ABOVE_         SETTING",473]
[null,null,163,218,"CS2 Slip<",{"$nulls":33},"DDB_CS2_SLIP_BELOW_      SETTING",474]
[null,null,163,219,"Time Synch",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TIME_SYNCH",475]
[null,null,163,220,"df/dt> Inhibit",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_INHIBIT",476]
[null,null,163,221,"df/dt>1 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_1_TIMER_BLOCK",477]
[null,null,163,222,"df/dt>2 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_2_TIMER_BLOCK",478]
[null,null,163,223,"df/dt>3 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_3_TIMER_BLOCK",479]
[null,null,163,224,"df/dt>4 Timer Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_4_TIMER_BLOCK",480]
[1,"1, 7, 9",163,225,"df/dt>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_1_START",481]
[1,"1, 7, 9",163,226,"df/dt>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_2_START",482]
[1,"1, 7, 9",163,227,"df/dt>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_3_START",483]
[1,"1, 7, 9",163,228,"df/dt>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_4_START",484]
[2,"1, 7",163,229,"df/dt>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_1_TRIP",485]
[2,"1, 7",163,230,"df/dt>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_2_TRIP",486]
[2,"1, 7",163,231,"df/dt>3 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_3_TRIP",487]
[2,"1, 7",163,232,"df/dt>4 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_DFDT_4_TRIP",488]
[null,null,163,233,"CS Vline<",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_VLINE_UV",489]
[null,null,163,234,"CS Vbus<",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_VBUS_UV",490]
[null,null,163,235,"CS Vline>",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_VLINE_OV",491]
[null,null,163,236,"CS Vbus>",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_VBUS_OV",492]
[null,null,163,237,"CS Vline>Vbus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_VLINE_      DIFF_HIGH",493]
[null,null,163,238,"CS Vline<Vbus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_VBUS_        DIFF_HIGH",494]
[null,null,163,239,"CS1 Fline>Fbus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS1_LINE_FREQ_GT_BUS_FREQ",495]
[null,null,163,240,"CS1 Fline<Fbus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS1_LINE_FREQ_LT_BUS_FREQ",496]
[null,null,163,241,"CS1 Ang Not OK +",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS1_ANG_NOT_OK_POS",497]
[null,null,163,242,"CS1 Ang Not OK -",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS1_ANG_NOT_OK_NEG",498]
[null,null,163,243,"CBF Ext Trip A",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXTERNAL_TRIP_A",499]
[null,null,163,244,"CBF Ext Trip B",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXTERNAL_TRIP_B",500]
[null,null,163,245,"CBF Ext Trip C",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXTERNAL_TRIP_C",501]
[null,null,163,246,"CBF Ext Trip EF",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXTERNAL_TRIP_EF",502]
[null,null,163,247,"CBF Ext Trip SEF",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EXTERNAL_TRIP_SEF",503]
[null,null,163,248,"I2> Inhibit",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_INHIBIT",504]
[null,null,163,249,"I2>1 Tmr Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_1_TIMER_BLOCK",505]
[null,null,163,250,"I2>2 Tmr Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_2_TIMER_BLOCK",506]
[null,null,163,251,"I2>3 Tmr Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_3_TIMER_BLOCK",507]
[null,null,163,252,"I2>4 Tmr Blk",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_4_TIMER_BLOCK",508]
[1,"1, 7, 9",163,253,"I2>1 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_1_START",509]
[1,"1, 7, 9",163,254,"I2>2 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_2_START",510]
[1,"1, 7, 9",163,255,"I2>3 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_3_START",511]
[1,"1, 7, 9",164,0,"I2>4 Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_4_START",512]
[2,"1, 7",164,1,"I2>1 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_1_TRIP",513]
[2,"1, 7",164,2,"I2>2 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_2_TRIP",514]
[2,"1, 7",164,3,"I2>3 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_3_TRIP",515]
[2,"1, 7",164,4,"I2>4 Trip",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NPSOC_4_TRIP",516]
[null,null,164,5,"V2> Accelerate",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ACCELERATE_NPSOV",517]
[null,null,164,6,"Trip LED",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TRIP_LED_TRIGGER",518]
[null,null,164,7,"CS2 Fline>Fbus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS2_LINE_FREQ_GT_BUS_FREQ",519]
[null,null,164,8,"CS2 Fline<Fbus",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS2_LINE_FREQ_LT_BUS_FREQ",520]
[null,null,164,9,"CS2 Ang Not OK +",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS2_ANG_NOT_OK_POS",521]
[null,null,164,10,"CS2 Ang Not OK -",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_CS2_ANG_NOT_OK_NEG",522]
[null,null,164,11,"CS Ang Rot ACW",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_ANG_ACW",523]
[null,null,164,12,"CS Ang Rot CW",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","DDB_SYSCHECKS_ANG_CW",524]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,164,13,"Block Rem CB Cmd",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BLOCK_REMOTE_CB_       OPS",525]
[null,null,164,14,"Opto SG Low",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SG_SELECTOR_X1",526]
[null,null,164,15,"Opto SG High",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SG_SELECTOR_1X",527]
[null,null,164,16,"Inhibit IN1>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF1_INHIBIT",528]
[null,null,164,17,"Inhibit IN2>",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_EF2_INHIBIT",529]
[null,null,164,18,"AR Skip Shot 1",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_SKIP_SHOT_1",530]
[null,null,164,19,"Logic 0 Ref.",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_LOGIC_0",531]
[null,null,164,20,"Inh Reclaim Time",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_INHIBIT_RECLAIM_         TIME",532]
[null,null,164,21,"Reclaim In Prog",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_RECLAIM_IN_              PROGRESS",533]
[null,null,164,22,"Reclaim Complete",null,null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_AR_RECLAIM_TIME_         COMPLETE",534]
[1,"1, 7, 9",164,23,"BrokenLine Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BROKEN_CONDUCTOR_              START",535]
[2,"1, 7",160,68,"Trip Command In",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ANY_TRIP",536]
[null,null,164,25,"Trip Command Out",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_TRIP_INITIATE",537]
[1,"1, 7, 9",164,26,"IA2H Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_2ND_HARMONIC_IA",538]
[1,"1, 7, 9",164,27,"IB2H Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_2ND_HARMONIC_IB",539]
[1,"1, 7, 9",164,28,"IC2H Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_2ND_HARMONIC_IC",540]
[1,"1, 7, 9",164,29,"I2H Any Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_2ND_HARMONIC",541]
[null,null,164,30,"RP1 Read Only Mode","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RP1_READ_ONLY",542]
[null,null,164,31,"RP2 Read Only Mode","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RP2_READ_ONLY",543]
[null,null,164,32,"NIC Read Only Mode","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NIC_READ_ONLY",544]
[null,null,164,33,{"$nulls":34},"DDB_UNUSED_545",545]
[null,null,164,34,{"$nulls":34},"DDB_UNUSED_546",546]
[null,null,164,35,{"$nulls":34},"DDB_UNUSED_547",547]
[null,null,164,36,{"$nulls":34},"DDB_UNUSED_548",548]
[null,null,164,37,{"$nulls":34},"DDB_UNUSED_549",549]
[null,null,164,38,{"$nulls":34},"DDB_UNUSED_550",550]
[null,null,164,39,{"$nulls":34},"DDB_UNUSED_551",551]
[null,null,164,40,{"$nulls":34},"DDB_UNUSED_552",552]
[null,null,164,41,{"$nulls":34},"DDB_UNUSED_553",553]
[null,null,164,42,{"$nulls":34},"DDB_UNUSED_554",554]
[null,null,164,43,{"$nulls":34},"DDB_UNUSED_555",555]
[null,null,164,44,{"$nulls":34},"DDB_UNUSED_556",556]
[null,null,164,45,{"$nulls":34},"DDB_UNUSED_557",557]
[null,null,164,46,{"$nulls":34},"DDB_UNUSED_558",558]
[null,null,164,47,{"$nulls":34},"DDB_UNUSED_559",559]
[null,null,164,48,{"$nulls":34},"DDB_UNUSED_560",560]
[null,null,164,49,{"$nulls":34},"DDB_UNUSED_561",561]
[null,null,164,50,{"$nulls":34},"DDB_UNUSED_562",562]
[null,null,164,51,{"$nulls":34},"DDB_UNUSED_563",563]
[null,null,164,52,{"$nulls":34},"DDB_UNUSED_564",564]
[null,null,164,53,{"$nulls":34},"DDB_UNUSED_565",565]
[null,null,164,54,{"$nulls":34},"DDB_UNUSED_566",566]
[null,null,164,55,{"$nulls":34},"DDB_UNUSED_567",567]
[null,null,164,56,{"$nulls":34},"DDB_UNUSED_568",568]
[null,null,164,57,{"$nulls":34},"DDB_UNUSED_569",569]
[null,null,164,58,{"$nulls":34},"DDB_UNUSED_570",570]
[null,null,164,59,{"$nulls":34},"DDB_UNUSED_571",571]
[null,null,164,60,{"$nulls":34},"DDB_UNUSED_572",572]
[null,null,164,61,{"$nulls":34},"DDB_UNUSED_573",573]
[null,null,164,62,{"$nulls":34},"DDB_UNUSED_574",574]
[null,null,164,63,{"$nulls":34},"DDB_UNUSED_575",575]
[null,null,164,64,{"$nulls":34},"DDB_UNUSED_576",576]
[null,null,164,65,{"$nulls":34},"DDB_UNUSED_577",577]
[null,null,164,66,{"$nulls":34},"DDB_UNUSED_578",578]
[null,null,164,67,{"$nulls":34},"DDB_UNUSED_579",579]
[null,null,164,68,{"$nulls":34},"DDB_UNUSED_580",580]
[null,null,164,69,{"$nulls":34},"DDB_UNUSED_581",581]
[null,null,164,70,{"$nulls":34},"DDB_UNUSED_582",582]
[null,null,164,71,{"$nulls":34},"DDB_UNUSED_583",583]
[null,null,164,72,{"$nulls":34},"DDB_UNUSED_584",584]
[null,null,164,73,{"$nulls":34},"DDB_UNUSED_585",585]
[null,null,164,74,{"$nulls":34},"DDB_UNUSED_586",586]
[null,null,164,75,{"$nulls":34},"DDB_UNUSED_587",587]
[null,null,164,76,{"$nulls":34},"DDB_UNUSED_588",588]
[null,null,164,77,{"$nulls":34},"DDB_UNUSED_589",589]
[null,null,164,78,{"$nulls":34},"DDB_UNUSED_590",590]
[null,null,164,79,{"$nulls":34},"DDB_UNUSED_591",591]
[null,null,164,80,{"$nulls":34},"DDB_UNUSED_592",592]
[null,null,164,81,{"$nulls":34},"DDB_UNUSED_593",593]
[null,null,164,82,{"$nulls":34},"DDB_UNUSED_594",594]
[null,null,164,83,{"$nulls":34},"DDB_UNUSED_595",595]
[null,null,164,84,{"$nulls":34},"DDB_UNUSED_596",596]
[null,null,164,85,{"$nulls":34},"DDB_UNUSED_597",597]
[null,null,164,86,{"$nulls":34},"DDB_UNUSED_598",598]
[null,null,164,87,{"$nulls":34},"DDB_UNUSED_599",599]
[null,null,164,88,{"$nulls":34},"DDB_UNUSED_600",600]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,164,89,{"$nulls":34},"DDB_UNUSED_601",601]
[null,null,164,90,{"$nulls":34},"DDB_UNUSED_602",602]
[null,null,164,91,{"$nulls":34},"DDB_UNUSED_603",603]
[null,null,164,92,{"$nulls":34},"DDB_UNUSED_604",604]
[null,null,164,93,{"$nulls":34},"DDB_UNUSED_605",605]
[null,null,164,94,{"$nulls":34},"DDB_UNUSED_606",606]
[null,null,164,95,{"$nulls":34},"DDB_UNUSED_607",607]
[null,null,164,96,{"$nulls":34},"DDB_UNUSED_608",608]
[null,null,164,97,{"$nulls":34},"DDB_UNUSED_609",609]
[null,null,164,98,{"$nulls":34},"DDB_UNUSED_610",610]
[null,null,164,99,{"$nulls":34},"DDB_UNUSED_611",611]
[null,null,164,100,{"$nulls":34},"DDB_UNUSED_612",612]
[null,null,164,101,{"$nulls":34},"DDB_UNUSED_613",613]
[null,null,164,102,{"$nulls":34},"DDB_UNUSED_614",614]
[null,null,164,103,{"$nulls":34},"DDB_UNUSED_615",615]
[null,null,164,104,{"$nulls":34},"DDB_UNUSED_616",616]
[null,null,164,105,{"$nulls":34},"DDB_UNUSED_617",617]
[null,null,164,106,{"$nulls":34},"DDB_UNUSED_618",618]
[null,null,164,107,{"$nulls":34},"DDB_UNUSED_619",619]
[null,null,164,108,{"$nulls":34},"DDB_UNUSED_620",620]
[null,null,164,109,{"$nulls":34},"DDB_UNUSED_621",621]
[null,null,164,110,{"$nulls":34},"DDB_UNUSED_622",622]
[null,null,164,111,{"$nulls":34},"DDB_UNUSED_623",623]
[null,null,164,112,{"$nulls":34},"DDB_UNUSED_624",624]
[null,null,164,113,{"$nulls":34},"DDB_UNUSED_625",625]
[null,null,164,114,{"$nulls":34},"DDB_UNUSED_626",626]
[null,null,164,115,{"$nulls":34},"DDB_UNUSED_627",627]
[null,null,164,116,{"$nulls":34},"DDB_UNUSED_628",628]
[null,null,164,117,{"$nulls":34},"DDB_UNUSED_629",629]
[null,null,164,118,{"$nulls":34},"DDB_UNUSED_630",630]
[null,null,164,119,{"$nulls":34},"DDB_UNUSED_631",631]
[null,null,164,120,{"$nulls":34},"DDB_UNUSED_632",632]
[null,null,164,121,{"$nulls":34},"DDB_UNUSED_633",633]
[null,null,164,122,{"$nulls":34},"DDB_UNUSED_634",634]
[null,null,164,123,{"$nulls":34},"DDB_UNUSED_635",635]
[null,null,164,124,{"$nulls":34},"DDB_UNUSED_636",636]
[null,null,164,125,{"$nulls":34},"DDB_UNUSED_637",637]
[null,null,164,126,{"$nulls":34},"DDB_UNUSED_638",638]
[null,null,164,127,{"$nulls":34},"DDB_UNUSED_639",639]
[null,null,164,128,"LED1 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_1_RED",640]
[null,null,164,129,"LED1 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_1_GRN",641]
[null,null,164,130,"LED2 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_2_RED",642]
[null,null,164,131,"LED2 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_2_GRN",643]
[null,null,164,132,"LED3 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_3_RED",644]
[null,null,164,133,"LED3 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_3_GRN",645]
[null,null,164,134,"LED4 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_4_RED",646]
[null,null,164,135,"LED4 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_4_GRN",647]
[null,null,164,136,"LED5 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_5_RED",648]
[null,null,164,137,"LED5 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_5_GRN",649]
[null,null,164,138,"LED6 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_6_RED",650]
[null,null,164,139,"LED6 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_6_GRN",651]
[null,null,164,140,"LED7 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_7_RED",652]
[null,null,164,141,"LED7 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_7_GRN",653]
[null,null,164,142,"LED8 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_8_RED",654]
[null,null,164,143,"LED8 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_8_GRN",655]
[null,null,164,144,"FnKey LED1 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_9_RED",656]
[null,null,164,145,"FnKey LED1 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_9_GRN",657]
[null,null,164,146,"FnKey LED2 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_10_          RED",658]
[null,null,164,147,"FnKey LED2 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_10_       GRN",659]
[null,null,164,148,"FnKey LED3 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_11_    RED",660]
[null,null,164,149,"FnKey LED3 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_11_   GRN",661]
[null,null,164,150,"FnKey LED4 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_12_       RED",662]
[null,null,164,151,"FnKey LED4 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_12_        GRN",663]
[null,null,164,152,"FnKey LED5 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_13_        RED",664]
[null,null,164,153,"FnKey LED5 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_13_         GRN",665]
[null,null,164,154,"FnKey LED6 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_14_         RED",666]
[null,null,164,155,"FnKey LED6 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_14_        GRN",667]
[null,null,164,156,"FnKey LED7 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_15_        RED",668]
[null,null,164,157,"FnKey LED7 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_15_         GRN",669]
[null,null,164,158,"FnKey LED8 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_16_        RED",670]
[null,null,164,159,"FnKey LED8 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_16_      GRN",671]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,164,160,"FnKey LED9 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_17_     RED",672]
[null,null,164,161,"FnKey LED9 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_17_   GRN",673]
[null,null,164,162,"FnKey LED10 Red",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_18_    RED",674]
[null,null,164,163,"FnKey LED10 Grn",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_OUTPUT_TRI_LED_18_   GRN",675]
[null,null,164,164,"LED1 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_1",676]
[null,null,164,165,"LED1 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_1",677]
[null,null,164,166,"LED2 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_2",678]
[null,null,164,167,"LED2 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_2",679]
[null,null,164,168,"LED3 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_3",680]
[null,null,164,169,"LED3 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_3",681]
[null,null,164,170,"LED4 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_4",682]
[null,null,164,171,"LED4 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_4",683]
[null,null,164,172,"LED5 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_5",684]
[null,null,164,173,"LED5 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_5",685]
[null,null,164,174,"LED6 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_6",686]
[null,null,164,175,"LED6 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_6",687]
[null,null,164,176,"LED7 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_7",688]
[null,null,164,177,"LED7 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_7",689]
[null,null,164,178,"LED8 Con R",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_8",690]
[null,null,164,179,"LED8 Con G",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_8",691]
[null,null,164,180,"FnKey LED1 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_9",692]
[null,null,164,181,"FnKey LED1 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_9",693]
[null,null,164,182,"FnKey LED2 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_10",694]
[null,null,164,183,"FnKey LED2 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_10",695]
[null,null,164,184,"FnKey LED3 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_11",696]
[null,null,164,185,"FnKey LED3 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_11",697]
[null,null,164,186,"FnKey LED4 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_12",698]
[null,null,164,187,"FnKey LED4 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_12",699]
[null,null,164,188,"FnKey LED5 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_13",700]
[null,null,164,189,"FnKey LED5 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_13",701]
[null,null,164,190,"FnKey LED6 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_14",702]
[null,null,164,191,"FnKey LED6 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_14",703]
[null,null,164,192,"FnKey LED7 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_15",704]
[null,null,164,193,"FnKey LED7 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_15",705]
[null,null,164,194,"FnKey LED8 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_16",706]
[null,null,164,195,"FnKey LED8 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_16",707]
[null,null,164,196,"FnKey LED9 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_17",708]
[null,null,164,197,"FnKey LED9 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_17",709]
[null,null,164,198,"FnKey LED10 ConR",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_RED_CON_18",710]
[null,null,164,199,"FnKey LED10 ConG",{"$nulls":22},"*","*","*","*","*","*","*","*","*","*","*","DDB_TRI_LED_GRN_CON_18",711]
[1,"1, 7, 9, 11",164,200,"Function Key 1","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_1",712]
[1,"1, 7, 9, 11",164,201,"Function Key 2","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_2",713]
[1,"1, 7, 9, 11",164,202,"Function Key 3","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_3",714]
[1,"1, 7, 9, 11",164,203,"Function Key 4","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_4",715]
[1,"1, 7, 9, 11",164,204,"Function Key 5","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_5",716]
[1,"1, 7, 9, 11",164,205,"Function Key 6","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_6",717]
[1,"1, 7, 9, 11",164,206,"Function Key 7","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_7",718]
[1,"1, 7, 9, 11",164,207,"Function Key 8","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_8",719]
[1,"1, 7, 9, 11",164,208,"Function Key 9","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_9",720]
[1,"1, 7, 9, 11",164,209,"Function Key 10","*",{"$nulls":21},"*","*","*","*","*","*","*","*","*","*","*","DDB_FN_KEY_10",721]
[1,"1, 7, 9",164,210,"Power>1 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_3PH_  START",722]
[1,"1, 7, 9",164,211,"Power>1 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_A_PH_START",723]
[1,"1, 7, 9",164,212,"Power>1 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_B_PH_START",724]
[1,"1, 7, 9",164,213,"Power>1 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_C_PH_START",725]
[1,"1, 7, 9",164,214,"Power>2 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_3PH_ START",726]
[1,"1, 7, 9",164,215,"Power>2 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_A_PH_START",727]
[1,"1, 7, 9",164,216,"Power>2 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_B_PH_START",728]
[1,"1, 7, 9",164,217,"Power>2 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_C_PH_START",729]
[1,"1, 7, 9",164,218,"Power<1 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_3PH_   START",730]
[1,"1, 7, 9",164,219,"Power<1 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_A_PH_START",731]
[1,"1, 7, 9",164,220,"Power<1 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_B_PH_START",732]
[1,"1, 7, 9",164,221,"Power<1 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_C_PH_START",733]
[1,"1, 7, 9",164,222,"Power<2 3PhStart","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_3PH_ START",734]
[1,"1, 7, 9",164,223,"Power<2 A Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_A_PH_START",735]
[1,"1, 7, 9",164,224,"Power<2 B Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_B_PH_START",736]
[1,"1, 7, 9",164,225,"Power<2 C Start","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_C_PH_START",737]
[2,"1, 7",164,226,"Power>1 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_3PH_ TRIP",738]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[2,"1, 7",164,227,"Power>1 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_A_PH_TRIP",739]
[2,"1, 7",164,228,"Power>1 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_B_PH_TRIP",740]
[2,"1, 7",164,229,"Power>1 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_C_PH_TRIP",741]
[2,"1, 7",164,230,"Power>2 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_3PH_ TRIP",742]
[2,"1, 7",164,231,"Power>2 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_A_PH_TRIP",743]
[2,"1, 7",164,232,"Power>2 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_B_PH_TRIP",744]
[2,"1, 7",164,233,"Power>2 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_C_PH_TRIP",745]
[2,"1, 7",164,234,"Power<1 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_3PH_ TRIP",746]
[2,"1, 7",164,235,"Power<1 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_A_PH_TRIP",747]
[2,"1, 7",164,236,"Power<1 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_B_PH_TRIP",748]
[2,"1, 7",164,237,"Power<1 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_C_PH_TRIP",749]
[2,"1, 7",164,238,"Power<2 3Ph Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_3PH_ TRIP",750]
[2,"1, 7",164,239,"Power<2 A Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_A_PH_TRIP",751]
[2,"1, 7",164,240,"Power<2 B Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_B_PH_TRIP",752]
[2,"1, 7",164,241,"Power<2 C Trip","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_C_PH_TRIP",753]
[null,null,164,242,"Power>1 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_1_BLOCK",754]
[null,null,164,243,"Power>2 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_OVER_POWER_2_BLOCK",755]
[null,null,164,244,"Power<1 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_1_          BLOCK",756]
[null,null,164,245,"Power<2 Block","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_UNDER_POWER_2_               BLOCK",757]
[1,"1, 7, 9",164,246,"SensP1 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SPOWER_1_START",758]
[1,"1, 7, 9",164,247,"SensP2 Start A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SPOWER_2_START",759]
[2,"1, 7",164,248,"SensP1 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SPOWER_1_TRIP",760]
[2,"1, 7",164,249,"SensP2 Trip A","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SPOWER_2_TRIP",761]
[null,null,164,250,{"$nulls":34},"DDB_UNUSED_762",762]
[null,null,164,251,{"$nulls":34},"DDB_UNUSED_763",763]
[null,null,164,252,{"$nulls":34},"DDB_UNUSED_764",764]
[null,null,164,253,{"$nulls":34},"DDB_UNUSED_765",765]
[null,null,164,254,{"$nulls":34},"DDB_UNUSED_766",766]
[null,null,164,255,{"$nulls":34},"DDB_UNUSED_767",767]
[null,null,165,0,{"$nulls":34},"DDB_UNUSED_768",768]
[1,"1, 7, 9",165,1,"Battery Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BATTERY_FAIL_ALARM",769]
[1,"1, 7, 9",165,2,"Comm2 H/W FAIL","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_REAR_COMMS_FAIL",770]
[1,"1, 7, 9",165,3,"GOOSE IED Absent","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSE_MISSING_IED_     ALARM",771]
[1,"1, 7, 9",165,4,"NIC Not Fitted","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ECARD_NOT_FITTED_      ALARM",772]
[1,"1, 7, 9",165,5,"NIC No Response","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NIC_NOT_RESPONDING_ALARM",773]
[1,"1, 7, 9",165,6,"NIC Fatal Error","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NIC_FATAL_ERROR_    ALARM",774]
[1,"1, 7, 9",165,7,"NIC Soft. Reload","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NIC_SOFTWARE_     RELOAD_ALARM",775]
[1,"1, 7, 9",165,8,"Bad TCP/IP Cfg.","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INVALID_TCP_IP_CONFIG_ALARM",776]
[1,"1, 7, 9",165,9,"Bad OSI Config.","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INVALID_OSI_CONFIG_    ALARM",777]
[1,"1, 7, 9",165,10,"NIC Link Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_NIC_LINK_FAIL_ALARM",778]
[1,"1, 7, 9",165,11,"NIC SW Mis-Match","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_SW_MISMATCH_ALARM",779]
[1,"1, 7, 9",165,12,"IP Addr Conflict","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_IP_ADDRESS_CONFLICT_ALARM",780]
[1,"1, 7, 9",165,13,"IM Loopback","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERMICOM_LOOPBACK_ALARM",781]
[1,"1, 7, 9",165,14,"IM Message Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERMICOM_MESSAGE_ALARM",782]
[1,"1, 7, 9",165,15,"IM Data CD Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERMICOM_DCD_        ALARM",783]
[1,"1, 7, 9",165,16,"IM Channel Fail","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERMICOM_CHANNEL_ALARM",784]
[1,"1, 7, 9",165,17,"Backup Setting","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_BACKUP_SETTINGS_         ALARM",785]
[null,null,165,18,{"$nulls":34},"DDB_UNUSED_786",786]
[null,null,165,19,{"$nulls":34},"DDB_UNUSED_787",787]
[null,null,165,20,{"$nulls":34},"DDB_UNUSED_788",788]
[null,null,165,21,{"$nulls":34},"DDB_UNUSED_789",789]
[null,null,165,22,{"$nulls":34},"DDB_UNUSED_790",790]
[null,null,165,23,{"$nulls":34},"DDB_UNUSED_791",791]
[null,null,165,24,{"$nulls":34},"DDB_UNUSED_792",792]
[null,null,165,25,{"$nulls":34},"DDB_UNUSED_793",793]
[null,null,165,26,{"$nulls":34},"DDB_UNUSED_794",794]
[null,null,165,27,{"$nulls":34},"DDB_UNUSED_795",795]
[null,null,165,28,{"$nulls":34},"DDB_UNUSED_796",796]
[null,null,165,29,{"$nulls":34},"DDB_UNUSED_797",797]
[null,null,165,30,{"$nulls":34},"DDB_UNUSED_798",798]
[null,null,165,31,{"$nulls":34},"DDB_UNUSED_799",799]
[1,"9, 11, 12, 20, 21",165,32,"Control Input 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_1",800]
[1,"9, 11, 12, 20, 21",165,33,"Control Input 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_2",801]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[1,"9, 11, 12, 20, 21",165,34,"Control Input 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_3",802]
[1,"9, 11, 12, 20, 21",165,35,"Control Input 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_4",803]
[1,"9, 11, 12, 20, 21",165,36,"Control Input 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_5",804]
[1,"9, 11, 12, 20, 21",165,37,"Control Input 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_6",805]
[1,"9, 11, 12, 20, 21",165,38,"Control Input 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_7",806]
[1,"9, 11, 12, 20, 21",165,39,"Control Input 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_8",807]
[1,"9, 11, 12, 20, 21",165,40,"Control Input 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_9",808]
[1,"9, 11, 12, 20, 21",165,41,"Control Input 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_10",809]
[1,"9, 11, 12, 20, 21",165,42,"Control Input 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_11",810]
[1,"9, 11, 12, 20, 21",165,43,"Control Input 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_12",811]
[1,"9, 11, 12, 20, 21",165,44,"Control Input 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_13",812]
[1,"9, 11, 12, 20, 21",165,45,"Control Input 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_14",813]
[1,"9, 11, 12, 20, 21",165,46,"Control Input 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_15",814]
[1,"9, 11, 12, 20, 21",165,47,"Control Input 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_16",815]
[1,"9, 11, 12, 20, 21",165,48,"Control Input 17","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_17",816]
[1,"9, 11, 12, 20, 21",165,49,"Control Input 18","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_18",817]
[1,"9, 11, 12, 20, 21",165,50,"Control Input 19","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_19",818]
[1,"9, 11, 12, 20, 21",165,51,"Control Input 20","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_20",819]
[1,"9, 11, 12, 20, 21",165,52,"Control Input 21","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_21",820]
[1,"9, 11, 12, 20, 21",165,53,"Control Input 22","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_22",821]
[1,"9, 11, 12, 20, 21",165,54,"Control Input 23","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_23",822]
[1,"9, 11, 12, 20, 21",165,55,"Control Input 24","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_24",823]
[1,"9, 11, 12, 20, 21",165,56,"Control Input 25","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_25",824]
[1,"9, 11, 12, 20, 21",165,57,"Control Input 26","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_26",825]
[1,"9, 11, 12, 20, 21",165,58,"Control Input 27","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_27",826]
[1,"9, 11, 12, 20, 21",165,59,"Control Input 28","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_28",827]
[1,"9, 11, 12, 20, 21",165,60,"Control Input 29","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_29",828]
[1,"9, 11, 12, 20, 21",165,61,"Control Input 30","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_30",829]
[1,"9, 11, 12, 20, 21",165,62,"Control Input 31","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_31",830]
[1,"9, 11, 12, 20, 21",165,63,"Control Input 32","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_32",831]
[1,"1, 7, 9",165,64,"GOOSE VIP 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_1",832]
[1,"1, 7, 9",165,65,"GOOSE VIP 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_2",833]
[1,"1, 7, 9",165,66,"GOOSE VIP 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_3",834]
[1,"1, 7, 9",165,67,"GOOSE VIP 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_4",835]
[1,"1, 7, 9",165,68,"GOOSE VIP 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_5",836]
[1,"1, 7, 9",165,69,"GOOSE VIP 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_6",837]
[1,"1, 7, 9",165,70,"GOOSE VIP 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_7",838]
[1,"1, 7, 9",165,71,"GOOSE VIP 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_8",839]
[1,"1, 7, 9",165,72,"GOOSE VIP 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_9",840]
[1,"1, 7, 9",165,73,"GOOSE VIP 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_10",841]
[1,"1, 7, 9",165,74,"GOOSE VIP 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_11",842]
[1,"1, 7, 9",165,75,"GOOSE VIP 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_12",843]
[1,"1, 7, 9",165,76,"GOOSE VIP 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_13",844]
[1,"1, 7, 9",165,77,"GOOSE VIP 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_14",845]
[1,"1, 7, 9",165,78,"GOOSE VIP 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_15",846]
[1,"1, 7, 9",165,79,"GOOSE VIP 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_16",847]
[1,"1, 7, 9",165,80,"GOOSE VIP 17","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_17",848]
[1,"1, 7, 9",165,81,"GOOSE VIP 18","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_18",849]
[1,"1, 7, 9",165,82,"GOOSE VIP 19","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_19",850]
[1,"1, 7, 9",165,83,"GOOSE VIP 20","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_20",851]
[1,"1, 7, 9",165,84,"GOOSE VIP 21","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_21",852]
[1,"1, 7, 9",165,85,"GOOSE VIP 22","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_22",853]
[1,"1, 7, 9",165,86,"GOOSE VIP 23","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_23",854]
[1,"1, 7, 9",165,87,"GOOSE VIP 24","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_24",855]
[1,"1, 7, 9",165,88,"GOOSE VIP 25","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_25",856]
[1,"1, 7, 9",165,89,"GOOSE VIP 26","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_26",857]
[1,"1, 7, 9",165,90,"GOOSE VIP 27","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_27",858]
[1,"1, 7, 9",165,91,"GOOSE VIP 28","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_28",859]
[1,"1, 7, 9",165,92,"GOOSE VIP 29","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_29",860]
[1,"1, 7, 9",165,93,"GOOSE VIP 30","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_30",861]
[1,"1, 7, 9",165,94,"GOOSE VIP 31","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_31",862]
[1,"1, 7, 9",165,95,"GOOSE VIP 32","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEIN_32",863]
[1,"1, 7, 9",165,96,"GOOSE VOP 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_1",864]
[1,"1, 7, 9",165,97,"GOOSE VOP 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_2",865]
[1,"1, 7, 9",165,98,"GOOSE VOP 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_3",866]
[1,"1, 7, 9",165,99,"GOOSE VOP 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_4",867]
[1,"1, 7, 9",165,100,"GOOSE VOP 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_5",868]
[1,"1, 7, 9",165,101,"GOOSE VOP 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_6",869]
[1,"1, 7, 9",165,102,"GOOSE VOP 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_7",870]
[1,"1, 7, 9",165,103,"GOOSE VOP 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_8",871]
[1,"1, 7, 9",165,104,"GOOSE VOP 9","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_9",872]
[1,"1, 7, 9",165,105,"GOOSE VOP 10","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_10",873]
[1,"1, 7, 9",165,106,"GOOSE VOP 11","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_11",874]
[1,"1, 7, 9",165,107,"GOOSE VOP 12","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_12",875]
[1,"1, 7, 9",165,108,"GOOSE VOP 13","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_13",876]
[1,"1, 7, 9",165,109,"GOOSE VOP 14","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_14",877]
[1,"1, 7, 9",165,110,"GOOSE VOP 15","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_15",878]
[1,"1, 7, 9",165,111,"GOOSE VOP 16","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_16",879]
[1,"1, 7, 9",165,112,"GOOSE VOP 17","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_17",880]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[1,"1, 7, 9",165,113,"GOOSE VOP 18","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_18",881]
[1,"1, 7, 9",165,114,"GOOSE VOP 19","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_19",882]
[1,"1, 7, 9",165,115,"GOOSE VOP 20","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_20",883]
[1,"1, 7, 9",165,116,"GOOSE VOP 21","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_21",884]
[1,"1, 7, 9",165,117,"GOOSE VOP 22","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_22",885]
[1,"1, 7, 9",165,118,"GOOSE VOP 23","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_23",886]
[1,"1, 7, 9",165,119,"GOOSE VOP 24","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_24",887]
[1,"1, 7, 9",165,120,"GOOSE VOP 25","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_25",888]
[1,"1, 7, 9",165,121,"GOOSE VOP 26","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_26",889]
[1,"1, 7, 9",165,122,"GOOSE VOP 27","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_27",890]
[1,"1, 7, 9",165,123,"GOOSE VOP 28","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_28",891]
[1,"1, 7, 9",165,124,"GOOSE VOP 29","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_29",892]
[1,"1, 7, 9",165,125,"GOOSE VOP 30","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_30",893]
[1,"1, 7, 9",165,126,"GOOSE VOP 31","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_31",894]
[1,"1, 7, 9",165,127,"GOOSE VOP 32","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_GOOSEOUT_32",895]
[1,"1, 7, 9",165,128,"InterMiCOM in 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_1",896]
[1,"1, 7, 9",165,129,"InterMiCOM in 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_2",897]
[1,"1, 7, 9",165,130,"InterMiCOM in 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_3",898]
[1,"1, 7, 9",165,131,"InterMiCOM in 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_4",899]
[1,"1, 7, 9",165,132,"InterMiCOM in 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_5",900]
[1,"1, 7, 9",165,133,"InterMiCOM in 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_6",901]
[1,"1, 7, 9",165,134,"InterMiCOM in 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_7",902]
[1,"1, 7, 9",165,135,"InterMiCOM in 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTERIN_8",903]
[1,"1, 7, 9",165,136,"InterMiCOM out 1","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_1",904]
[1,"1, 7, 9",165,137,"InterMiCOM out 2","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_2",905]
[1,"1, 7, 9",165,138,"InterMiCOM out 3","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_3",906]
[1,"1, 7, 9",165,139,"InterMiCOM out 4","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_4",907]
[1,"1, 7, 9",165,140,"InterMiCOM out 5","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_5",908]
[1,"1, 7, 9",165,141,"InterMiCOM out 6","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_6",909]
[1,"1, 7, 9",165,142,"InterMiCOM out 7","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_7",910]
[1,"1, 7, 9",165,143,"InterMiCOM out 8","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_INTEROUT_8",911]
[null,null,165,144,{"$nulls":34},"DDB_UNUSED_912",912]
[null,null,165,145,{"$nulls":34},"DDB_UNUSED_913",913]
[null,null,165,146,{"$nulls":34},"DDB_UNUSED_914",914]
[null,null,165,147,{"$nulls":34},"DDB_UNUSED_915",915]
[null,null,165,148,{"$nulls":34},"DDB_UNUSED_916",916]
[null,null,165,149,{"$nulls":34},"DDB_UNUSED_917",917]
[null,null,165,150,{"$nulls":34},"DDB_UNUSED_918",918]
[null,null,165,151,{"$nulls":34},"DDB_UNUSED_919",919]
[null,null,165,152,{"$nulls":34},"DDB_UNUSED_920",920]
[null,null,165,153,{"$nulls":34},"DDB_UNUSED_921",921]
[null,null,165,154,{"$nulls":34},"DDB_RESERVED_DISTREC",922]
[null,null,165,155,"PSL Internal 001",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_1",923]
[null,null,165,156,"PSL Internal 002",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_2",924]
[null,null,165,157,"PSL Internal 003",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_3",925]
[null,null,165,158,"PSL Internal 004",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_4",926]
[null,null,165,159,"PSL Internal 005",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_5",927]
[null,null,165,160,"PSL Internal 006",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_6",928]
[null,null,165,161,"PSL Internal 007",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_7",929]
[null,null,165,162,"PSL Internal 008",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_8",930]
[null,null,165,163,"PSL Internal 009",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_9",931]
[null,null,165,164,"PSL Internal 010",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_10",932]
[null,null,165,165,"PSL Internal 011",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_11",933]
[null,null,165,166,"PSL Internal 012",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_12",934]
[null,null,165,167,"PSL Internal 013",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_13",935]
[null,null,165,168,"PSL Internal 014",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_14",936]
[null,null,165,169,"PSL Internal 015",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_15",937]
[null,null,165,170,"PSL Internal 016",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_16",938]
[null,null,165,171,"PSL Internal 017",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_17",939]
[null,null,165,172,"PSL Internal 018",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_18",940]
[null,null,165,173,"PSL Internal 019",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_19",941]
[null,null,165,174,"PSL Internal 020",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_20",942]
[null,null,165,175,"PSL Internal 021",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_21",943]
[null,null,165,176,"PSL Internal 022",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_22",944]
[null,null,165,177,"PSL Internal 023",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_23",945]
[null,null,165,178,"PSL Internal 024",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_24",946]
[null,null,165,179,"PSL Internal 025",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_25",947]
[null,null,165,180,"PSL Internal 026",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_26",948]
[null,null,165,181,"PSL Internal 027",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_27",949]
[null,null,165,182,"PSL Internal 028",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_28",950]
[null,null,165,183,"PSL Internal 029",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_29",951]
[null,null,165,184,"PSL Internal 030",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_30",952]
[null,null,165,185,"PSL Internal 031",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_31",953]
[null,null,165,186,"PSL Internal 032",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_32",954]
[null,null,165,187,"PSL Internal 033",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_33",955]
[null,null,165,188,"PSL Internal 034",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_34",956]
[null,null,165,189,"PSL Internal 035",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_35",957]
[null,null,165,190,"PSL Internal 036",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_36",958]
[null,null,165,191,"PSL Internal 037",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_37",959]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,165,192,"PSL Internal 038",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_38",960]
[null,null,165,193,"PSL Internal 039",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_39",961]
[null,null,165,194,"PSL Internal 040",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_40",962]
[null,null,165,195,"PSL Internal 041",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_41",963]
[null,null,165,196,"PSL Internal 042",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_42",964]
[null,null,165,197,"PSL Internal 043",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_43",965]
[null,null,165,198,"PSL Internal 044",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_44",966]
[null,null,165,199,"PSL Internal 045",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_45",967]
[null,null,165,200,"PSL Internal 046",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_46",968]
[null,null,165,201,"PSL Internal 047",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_47",969]
[null,null,165,202,"PSL Internal 048",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_48",970]
[null,null,165,203,"PSL Internal 049",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_49",971]
[null,null,165,204,"PSL Internal 050",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_50",972]
[null,null,165,205,"PSL Internal 051",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_51",973]
[null,null,165,206,"PSL Internal 052",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_52",974]
[null,null,165,207,"PSL Internal 053",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_53",975]
[null,null,165,208,"PSL Internal 054",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_54",976]
[null,null,165,209,"PSL Internal 055",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_55",977]
[null,null,165,210,"PSL Internal 056",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_56",978]
[null,null,165,211,"PSL Internal 057",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_57",979]
[null,null,165,212,"PSL Internal 058",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_58",980]
[null,null,165,213,"PSL Internal 059",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_59",981]
[null,null,165,214,"PSL Internal 060",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_60",982]
[null,null,165,215,"PSL Internal 061",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_61",983]
[null,null,165,216,"PSL Internal 062",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_62",984]
[null,null,165,217,"PSL Internal 063",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_63",985]
[null,null,165,218,"PSL Internal 064",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_64",986]
[null,null,165,219,"PSL Internal 065",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_65",987]
[null,null,165,220,"PSL Internal 066",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_66",988]
[null,null,165,221,"PSL Internal 067",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_67",989]
[null,null,165,222,"PSL Internal 068",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_68",990]
[null,null,165,223,"PSL Internal 069",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_69",991]
[null,null,165,224,"PSL Internal 070",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_70",992]
[null,null,165,225,"PSL Internal 071",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_71",993]
[null,null,165,226,"PSL Internal 072",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_72",994]
[null,null,165,227,"PSL Internal 073",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_73",995]
[null,null,165,228,"PSL Internal 074",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_74",996]
[null,null,165,229,"PSL Internal 075",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_75",997]
[null,null,165,230,"PSL Internal 076",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_76",998]
[null,null,165,231,"PSL Internal 077",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_77",999]
[null,null,165,232,"PSL Internal 078",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_78",1000]
[null,null,165,233,"PSL Internal 079",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_79",1001]
[null,null,165,234,"PSL Internal 080",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_80",1002]
[null,null,165,235,"PSL Internal 081",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_81",1003]
[null,null,165,236,"PSL Internal 082",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_82",1004]
[null,null,165,237,"PSL Internal 083",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_83",1005]
[null,null,165,238,"PSL Internal 084",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_84",1006]
[null,null,165,239,"PSL Internal 085",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_85",1007]
[null,null,165,240,"PSL Internal 086",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_86",1008]
[null,null,165,241,"PSL Internal 087",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_87",1009]
[null,null,165,242,"PSL Internal 088",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_88",1010]
[null,null,165,243,"PSL Internal 089",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_89",1011]
[null,null,165,244,"PSL Internal 090",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_90",1012]
[null,null,165,245,"PSL Internal 091",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_91",1013]
[null,null,165,246,"PSL Internal 092",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_92",1014]
[null,null,165,247,"PSL Internal 093",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_93",1015]
[null,null,165,248,"PSL Internal 094",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_94",1016]
[null,null,165,249,"PSL Internal 095",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_95",1017]
[null,null,165,250,"PSL Internal 096",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_96",1018]
[null,null,165,251,"PSL Internal 097",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_97",1019]
[null,null,165,252,"PSL Internal 098",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_98",1020]
[null,null,165,253,"PSL Internal 099",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_99",1021]
[null,null,165,254,"PSL Internal 100",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_PSLINT_100",1022]
[null,null,165,255,{"$nulls":34},"DDB_UNUSED_1023",1023]
[null,null,166,0,"Adv Freq Inh",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_ADV_FREQ_INHIBIT",1024]
[2,"1, 7, 9",166,1,"Stg1 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_F_T_START",1025]
[2,"1, 7",166,2,"Stg1 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_F_T_TRIP",1026]
[2,"1, 7",166,3,"Stg1 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_F_DFDT_TRIP",1027]
[2,"1, 7, 9",166,4,"Stg1 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_DFDT_T_START",1028]
[2,"1, 7",166,5,"Stg1 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_DFDT_T_TRIP",1029]
[2,"1, 7, 9",166,6,"Stg1 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_F_DELF_DELT_          START",1030]
[2,"1, 7",166,7,"Stg1 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_F_DELF_DELT_    TRIP",1031]
[null,null,166,8,"Stg1 Block",{"$nulls":33},"DDB_STG1_ADV_FREQ_     BLOCK",1032]
[null,null,166,9,{"$nulls":34},"DDB_UNUSED_1033",1033]
[null,null,166,10,{"$nulls":34},"DDB_UNUSED_1034",1034]
[2,"1, 7",166,11,"Stg1 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_RESTORE_CLOSE",1035]
[2,"1, 7, 9",166,12,"Stg1 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG1_RESTORE_START",1036]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,166,13,{"$nulls":34},"DDB_UNUSED_1037",1037]
[null,null,166,14,{"$nulls":34},"DDB_UNUSED_1038",1038]
[2,"1, 7, 9",166,15,"Stg2 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_F_T_START",1039]
[2,"1, 7",166,16,"Stg2 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_F_T_TRIP",1040]
[2,"1, 7",166,17,"Stg2 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_F_DFDT_TRIP",1041]
[2,"1, 7, 9",166,18,"Stg2 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_DFDT_T_START",1042]
[2,"1, 7",166,19,"Stg2 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_DFDT_T_TRIP",1043]
[2,"1, 7, 9",166,20,"Stg2 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_F_DELF_DELT_  START",1044]
[2,"1, 7",166,21,"Stg2 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_F_DELF_DELT_     TRIP",1045]
[null,null,166,22,"Stg2 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_ADV_FREQ_    BLOCK",1046]
[null,null,166,23,{"$nulls":34},"DDB_UNUSED_1047",1047]
[null,null,166,24,{"$nulls":34},"DDB_UNUSED_1048",1048]
[2,"1, 7",166,25,"Stg2 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_RESTORE_CLOSE",1049]
[2,"1, 7, 9",166,26,"Stg2 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG2_RESTORE_START",1050]
[null,null,166,27,{"$nulls":34},"DDB_UNUSED_1051",1051]
[null,null,166,28,{"$nulls":34},"DDB_UNUSED_1052",1052]
[2,"1, 7, 9",166,29,"Stg3 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_F_T_START",1053]
[2,"1, 7",166,30,"Stg3 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_F_T_TRIP",1054]
[2,"1, 7",166,31,"Stg3 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_F_DFDT_TRIP",1055]
[2,"1, 7, 9",166,32,"Stg3 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_DFDT_T_START",1056]
[2,"1, 7",166,33,"Stg3 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_DFDT_T_TRIP",1057]
[2,"1, 7, 9",166,34,"Stg3 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_F_DELF_DELT_         START",1058]
[2,"1, 7",166,35,"Stg3 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_F_DELF_DELT_      TRIP",1059]
[null,null,166,36,"Stg3 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_ADV_FREQ_       BLOCK",1060]
[null,null,166,37,{"$nulls":34},"DDB_UNUSED_1061",1061]
[null,null,166,38,{"$nulls":34},"DDB_UNUSED_1062",1062]
[2,"1, 7",166,39,"Stg3 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_RESTORE_CLOSE",1063]
[2,"1, 7, 9",166,40,"Stg3 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG3_RESTORE_START",1064]
[null,null,166,41,{"$nulls":34},"DDB_UNUSED_1065",1065]
[null,null,166,42,{"$nulls":34},"DDB_UNUSED_1066",1066]
[2,"1, 7, 9",166,43,"Stg4 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_F_T_START",1067]
[2,"1, 7",166,44,"Stg4 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_F_T_TRIP",1068]
[2,"1, 7",166,45,"Stg4 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_F_DFDT_TRIP",1069]
[2,"1, 7, 9",166,46,"Stg4 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_DFDT_T_START",1070]
[2,"1, 7",166,47,"Stg4 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_DFDT_T_TRIP",1071]
[2,"1, 7, 9",166,48,"Stg4 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_F_DELF_DELT_   START",1072]
[2,"1, 7",166,49,"Stg4 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_F_DELF_DELT_      TRIP",1073]
[null,null,166,50,"Stg4 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_ADV_FREQ_    BLOCK",1074]
[null,null,166,51,{"$nulls":34},"DDB_UNUSED_1075",1075]
[null,null,166,52,{"$nulls":34},"DDB_UNUSED_1076",1076]
[2,"1, 7",166,53,"Stg4 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_RESTORE_CLOSE",1077]
[2,"1, 7, 9",166,54,"Stg4 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG4_RESTORE_START",1078]
[null,null,166,55,{"$nulls":34},"DDB_UNUSED_1079",1079]
[null,null,166,56,{"$nulls":34},"DDB_UNUSED_1080",1080]
[2,"1, 7, 9",166,57,"Stg5 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_F_T_START",1081]
[2,"1, 7",166,58,"Stg5 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_F_T_TRIP",1082]
[2,"1, 7",166,59,"Stg5 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_F_DFDT_TRIP",1083]
[2,"1, 7, 9",166,60,"Stg5 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_DFDT_T_START",1084]
[2,"1, 7",166,61,"Stg5 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_DFDT_T_TRIP",1085]
[2,"1, 7, 9",166,62,"Stg5 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_F_DELF_DELT_     START",1086]
[2,"1, 7",166,63,"Stg5 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_F_DELF_DELT_   TRIP",1087]
[null,null,166,64,"Stg5 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_ADV_FREQ_      BLOCK",1088]
[null,null,166,65,{"$nulls":34},"DDB_UNUSED_1089",1089]
[null,null,166,66,{"$nulls":34},"DDB_UNUSED_1090",1090]
[2,"1, 7",166,67,"Stg5 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_RESTORE_CLOSE",1091]
[2,"1, 7, 9",166,68,"Stg5 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG5_RESTORE_START",1092]
[null,null,166,69,{"$nulls":34},"DDB_UNUSED_1093",1093]
[null,null,166,70,{"$nulls":34},"DDB_UNUSED_1094",1094]
[2,"1, 7, 9",166,71,"Stg6 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_F_T_START",1095]
[2,"1, 7",166,72,"Stg6 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_F_T_TRIP",1096]
[2,"1, 7",166,73,"Stg6 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_F_DFDT_TRIP",1097]
[2,"1, 7, 9",166,74,"Stg6 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_DFDT_T_START",1098]
[2,"1, 7",166,75,"Stg6 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_DFDT_T_TRIP",1099]
[2,"1, 7, 9",166,76,"Stg6 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_F_DELF_DELT_       START",1100]
[2,"1, 7",166,77,"Stg6 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_F_DELF_DELT_      TRIP",1101]
[null,null,166,78,"Stg6 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_ADV_FREQ_       BLOCK",1102]
[null,null,166,79,{"$nulls":34},"DDB_UNUSED_1103",1103]
[null,null,166,80,{"$nulls":34},"DDB_UNUSED_1104",1104]
[2,"1, 7",166,81,"Stg6 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_RESTORE_CLOSE",1105]
[2,"1, 7, 9",166,82,"Stg6 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG6_RESTORE_START",1106]
[null,null,166,83,{"$nulls":34},"DDB_UNUSED_1107",1107]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,166,84,{"$nulls":34},"DDB_UNUSED_1108",1108]
[2,"1, 7, 9",166,85,"Stg7 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_F_T_START",1109]
[2,"1, 7",166,86,"Stg7 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_F_T_TRIP",1110]
[2,"1, 7",166,87,"Stg7 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_F_DFDT_TRIP",1111]
[2,"1, 7, 9",166,88,"Stg7 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_DFDT_T_START",1112]
[2,"1, 7",166,89,"Stg7 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_DFDT_T_TRIP",1113]
[2,"1, 7, 9",166,90,"Stg7 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_F_DELF_DELT_     START",1114]
[2,"1, 7",166,91,"Stg7 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_F_DELF_DELT_   TRIP",1115]
[null,null,166,92,"Stg7 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_ADV_FREQ_     BLOCK",1116]
[null,null,166,93,{"$nulls":34},"DDB_UNUSED_1117",1117]
[null,null,166,94,{"$nulls":34},"DDB_UNUSED_1118",1118]
[2,"1, 7",166,95,"Stg7 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_RESTORE_CLOSE",1119]
[2,"1, 7, 9",166,96,"Stg7 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG7_RESTORE_START",1120]
[null,null,166,97,{"$nulls":34},"DDB_UNUSED_1121",1121]
[null,null,166,98,{"$nulls":34},"DDB_UNUSED_1122",1122]
[2,"1, 7, 9",166,99,"Stg8 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_F_T_START",1123]
[2,"1, 7",166,100,"Stg8 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_F_T_TRIP",1124]
[2,"1, 7",166,101,"Stg8 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_F_DFDT_TRIP",1125]
[2,"1, 7, 9",166,102,"Stg8 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_DFDT_T_START",1126]
[2,"1, 7",166,103,"Stg8 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_DFDT_T_TRIP",1127]
[2,"1, 7, 9",166,104,"Stg8 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_F_DELF_DELT_  START",1128]
[2,"1, 7",166,105,"Stg8 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_F_DELF_DELT_   TRIP",1129]
[null,null,166,106,"Stg8 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_ADV_FREQ_   BLOCK",1130]
[null,null,166,107,{"$nulls":34},"DDB_UNUSED_1131",1131]
[null,null,166,108,{"$nulls":34},"DDB_UNUSED_1132",1132]
[2,"1, 7",166,109,"Stg8 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_RESTORE_CLOSE",1133]
[2,"1, 7, 9",166,110,"Stg8 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG8_RESTORE_START",1134]
[null,null,166,111,{"$nulls":34},"DDB_UNUSED_1135",1135]
[null,null,166,112,{"$nulls":34},"DDB_UNUSED_1136",1136]
[2,"1, 7, 9",166,113,"Stg9 f+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_F_T_START",1137]
[2,"1, 7",166,114,"Stg9 f+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_F_T_TRIP",1138]
[2,"1, 7",166,115,"Stg9 f+df/dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_F_DFDT_TRIP",1139]
[2,"1, 7, 9",166,116,"Stg9 df/dt+t Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_DFDT_T_START",1140]
[2,"1, 7",166,117,"Stg9 df/dt+t Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_DFDT_T_TRIP",1141]
[2,"1, 7, 9",166,118,"Stg9 f+Df/Dt Sta","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_F_DELF_DELT_  START",1142]
[2,"1, 7",166,119,"Stg9 f+Df/Dt Trp",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_F_DELF_DELT_ TRIP",1143]
[null,null,166,120,"Stg9 Block",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_ADV_FREQ_   BLOCK",1144]
[null,null,166,121,{"$nulls":34},"DDB_UNUSED_1145",1145]
[null,null,166,122,{"$nulls":34},"DDB_UNUSED_1146",1146]
[2,"1, 7",166,123,"Stg9 Restore Cls",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_RESTORE_CLOSE",1147]
[2,"1, 7, 9",166,124,"Stg9 Restore Sta",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_STG9_RESTORE_START",1148]
[null,null,166,125,"Restore Reset",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_RESTORE_RESET",1149]
[null,null,166,126,"Reset Stats",{"$nulls":33},"DDB_RESET_STATISTICS",1150]
[null,null,166,127,{"$nulls":34},"DDB_UNUSED_1151",1151]
[null,null,166,128,{"$nulls":34},"DDB_UNUSED_1152",1152]
[null,null,166,129,{"$nulls":34},"DDB_UNUSED_1153",1153]
[null,null,166,130,{"$nulls":34},"DDB_UNUSED_1154",1154]
[null,null,166,131,{"$nulls":34},"DDB_UNUSED_1155",1155]
[null,null,166,132,{"$nulls":34},"DDB_UNUSED_1156",1156]
[null,null,166,133,{"$nulls":34},"DDB_UNUSED_1157",1157]
[null,null,166,134,{"$nulls":34},"DDB_UNUSED_1158",1158]
[null,null,166,135,{"$nulls":34},"DDB_UNUSED_1159",1159]
[null,null,166,136,{"$nulls":34},"DDB_UNUSED_1160",1160]
[null,null,166,137,{"$nulls":34},"DDB_UNUSED_1161",1161]
[null,null,166,138,{"$nulls":34},"DDB_UNUSED_1162",1162]
[null,null,166,139,{"$nulls":34},"DDB_UNUSED_1163",1163]
[null,null,166,140,{"$nulls":34},"DDB_UNUSED_1164",1164]
[null,null,166,141,{"$nulls":34},"DDB_UNUSED_1165",1165]
[null,null,166,142,{"$nulls":34},"DDB_UNUSED_1166",1166]
[null,null,166,143,{"$nulls":34},"DDB_UNUSED_1167",1167]
[null,null,166,144,{"$nulls":34},"DDB_UNUSED_1168",1168]
[null,null,166,145,{"$nulls":34},"DDB_UNUSED_1169",1169]
[null,null,166,146,{"$nulls":34},"DDB_UNUSED_1170",1170]
[null,null,166,147,{"$nulls":34},"DDB_UNUSED_1171",1171]
[null,null,166,148,{"$nulls":34},"DDB_UNUSED_1172",1172]
[null,null,166,149,{"$nulls":34},"DDB_UNUSED_1173",1173]
[null,null,166,150,{"$nulls":34},"DDB_UNUSED_1174",1174]
[null,null,166,151,{"$nulls":34},"DDB_UNUSED_1175",1175]
[null,null,166,152,{"$nulls":34},"DDB_UNUSED_1176",1176]
[null,null,166,153,{"$nulls":34},"DDB_UNUSED_1177",1177]
[null,null,166,154,{"$nulls":34},"DDB_UNUSED_1178",1178]
[null,null,166,155,{"$nulls":34},"DDB_UNUSED_1179",1179]
[null,null,166,156,{"$nulls":34},"DDB_UNUSED_1180",1180]
[null,null,166,157,{"$nulls":34},"DDB_UNUSED_1181",1181]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,166,158,{"$nulls":34},"DDB_UNUSED_1182",1182]
[null,null,166,159,{"$nulls":34},"DDB_UNUSED_1183",1183]
[null,null,166,160,{"$nulls":34},"DDB_UNUSED_1184",1184]
[null,null,166,161,{"$nulls":34},"DDB_UNUSED_1185",1185]
[null,null,166,162,{"$nulls":34},"DDB_UNUSED_1186",1186]
[null,null,166,163,{"$nulls":34},"DDB_UNUSED_1187",1187]
[null,null,166,164,{"$nulls":34},"DDB_UNUSED_1188",1188]
[null,null,166,165,{"$nulls":34},"DDB_UNUSED_1189",1189]
[null,null,166,166,{"$nulls":34},"DDB_UNUSED_1190",1190]
[null,null,166,167,{"$nulls":34},"DDB_UNUSED_1191",1191]
[null,null,166,168,{"$nulls":34},"DDB_UNUSED_1192",1192]
[null,null,166,169,{"$nulls":34},"DDB_UNUSED_1193",1193]
[null,null,166,170,{"$nulls":34},"DDB_UNUSED_1194",1194]
[null,null,166,171,{"$nulls":34},"DDB_UNUSED_1195",1195]
[null,null,166,172,{"$nulls":34},"DDB_UNUSED_1196",1196]
[null,null,166,173,{"$nulls":34},"DDB_UNUSED_1197",1197]
[null,null,166,174,{"$nulls":34},"DDB_UNUSED_1198",1198]
[null,null,166,175,{"$nulls":34},"DDB_UNUSED_1199",1199]
[null,null,166,176,{"$nulls":34},"DDB_UNUSED_1200",1200]
[null,null,166,177,{"$nulls":34},"DDB_UNUSED_1201",1201]
[null,null,166,178,{"$nulls":34},"DDB_UNUSED_1202",1202]
[null,null,166,179,{"$nulls":34},"DDB_UNUSED_1203",1203]
[null,null,166,180,{"$nulls":34},"DDB_UNUSED_1204",1204]
[null,null,166,181,{"$nulls":34},"DDB_UNUSED_1205",1205]
[null,null,166,182,{"$nulls":34},"DDB_UNUSED_1206",1206]
[null,null,166,183,{"$nulls":34},"DDB_UNUSED_1207",1207]
[null,null,166,184,{"$nulls":34},"DDB_UNUSED_1208",1208]
[null,null,166,185,{"$nulls":34},"DDB_UNUSED_1209",1209]
[null,null,166,186,{"$nulls":34},"DDB_UNUSED_1210",1210]
[null,null,166,187,{"$nulls":34},"DDB_UNUSED_1211",1211]
[null,null,166,188,{"$nulls":34},"DDB_UNUSED_1212",1212]
[null,null,166,189,{"$nulls":34},"DDB_UNUSED_1213",1213]
[null,null,166,190,{"$nulls":34},"DDB_UNUSED_1214",1214]
[null,null,166,191,{"$nulls":34},"DDB_UNUSED_1215",1215]
[null,null,166,192,{"$nulls":34},"DDB_UNUSED_1216",1216]
[null,null,166,193,{"$nulls":34},"DDB_UNUSED_1217",1217]
[null,null,166,194,{"$nulls":34},"DDB_UNUSED_1218",1218]
[null,null,166,195,{"$nulls":34},"DDB_UNUSED_1219",1219]
[null,null,166,196,{"$nulls":34},"DDB_UNUSED_1220",1220]
[null,null,166,197,{"$nulls":34},"DDB_UNUSED_1221",1221]
[null,null,166,198,{"$nulls":34},"DDB_UNUSED_1222",1222]
[null,null,166,199,{"$nulls":34},"DDB_UNUSED_1223",1223]
[null,null,166,200,{"$nulls":34},"DDB_UNUSED_1224",1224]
[null,null,166,201,{"$nulls":34},"DDB_UNUSED_1225",1225]
[null,null,166,202,{"$nulls":34},"DDB_UNUSED_1226",1226]
[null,null,166,203,{"$nulls":34},"DDB_UNUSED_1227",1227]
[null,null,166,204,{"$nulls":34},"DDB_UNUSED_1228",1228]
[null,null,166,205,{"$nulls":34},"DDB_UNUSED_1229",1229]
[null,null,166,206,{"$nulls":34},"DDB_UNUSED_1230",1230]
[null,null,166,207,{"$nulls":34},"DDB_UNUSED_1231",1231]
[null,null,166,208,{"$nulls":34},"DDB_UNUSED_1232",1232]
[null,null,166,209,{"$nulls":34},"DDB_UNUSED_1233",1233]
[null,null,166,210,{"$nulls":34},"DDB_UNUSED_1234",1234]
[null,null,166,211,{"$nulls":34},"DDB_UNUSED_1235",1235]
[null,null,166,212,{"$nulls":34},"DDB_UNUSED_1236",1236]
[null,null,166,213,{"$nulls":34},"DDB_UNUSED_1237",1237]
[null,null,166,214,{"$nulls":34},"DDB_UNUSED_1238",1238]
[null,null,166,215,{"$nulls":34},"DDB_UNUSED_1239",1239]
[null,null,166,216,{"$nulls":34},"DDB_UNUSED_1240",1240]
[null,null,166,217,{"$nulls":34},"DDB_UNUSED_1241",1241]
[null,null,166,218,{"$nulls":34},"DDB_UNUSED_1242",1242]
[null,null,166,219,{"$nulls":34},"DDB_UNUSED_1243",1243]
[null,null,166,220,{"$nulls":34},"DDB_UNUSED_1244",1244]
[null,null,166,221,{"$nulls":34},"DDB_UNUSED_1245",1245]
[null,null,166,222,{"$nulls":34},"DDB_UNUSED_1246",1246]
[null,null,166,223,{"$nulls":34},"DDB_UNUSED_1247",1247]
[null,null,166,224,{"$nulls":34},"DDB_UNUSED_1248",1248]
[null,null,166,225,{"$nulls":34},"DDB_UNUSED_1249",1249]
[null,null,166,226,{"$nulls":34},"DDB_UNUSED_1250",1250]
[null,null,166,227,{"$nulls":34},"DDB_UNUSED_1251",1251]
[null,null,166,228,{"$nulls":34},"DDB_UNUSED_1252",1252]
[null,null,166,229,{"$nulls":34},"DDB_UNUSED_1253",1253]
[null,null,166,230,{"$nulls":34},"DDB_UNUSED_1254",1254]
[null,null,166,231,{"$nulls":34},"DDB_UNUSED_1255",1255]
[null,null,166,232,{"$nulls":34},"DDB_UNUSED_1256",1256]
[null,null,166,233,{"$nulls":34},"DDB_UNUSED_1257",1257]
[null,null,166,234,{"$nulls":34},"DDB_UNUSED_1258",1258]
[null,null,166,235,{"$nulls":34},"DDB_UNUSED_1259",1259]
[null,null,166,236,{"$nulls":34},"DDB_UNUSED_1260",1260]
["ASDU TYPE","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[null,null,166,237,{"$nulls":34},"DDB_UNUSED_1261",1261]
[null,null,166,238,{"$nulls":34},"DDB_UNUSED_1262",1262]
[null,null,166,239,{"$nulls":34},"DDB_UNUSED_1263",1263]
[null,null,166,240,{"$nulls":34},"DDB_UNUSED_1264",1264]
[null,null,166,241,{"$nulls":34},"DDB_UNUSED_1265",1265]
[null,null,166,242,{"$nulls":34},"DDB_UNUSED_1266",1266]
[null,null,166,243,{"$nulls":34},"DDB_UNUSED_1267",1267]
[null,null,166,244,{"$nulls":34},"DDB_UNUSED_1268",1268]
[null,null,166,245,{"$nulls":34},"DDB_UNUSED_1269",1269]
[null,null,166,246,{"$nulls":34},"DDB_UNUSED_1270",1270]
[null,null,166,247,{"$nulls":34},"DDB_UNUSED_1271",1271]
[null,null,166,248,{"$nulls":34},"DDB_UNUSED_1272",1272]
[null,null,166,249,{"$nulls":34},"DDB_UNUSED_1273",1273]
[null,null,166,250,{"$nulls":34},"DDB_UNUSED_1274",1274]
[null,null,166,251,{"$nulls":34},"DDB_UNUSED_1275",1275]
[null,null,166,252,{"$nulls":34},"DDB_UNUSED_1276",1276]
[null,null,166,253,{"$nulls":34},"DDB_UNUSED_1277",1277]
[null,null,166,254,{"$nulls":34},"DDB_UNUSED_1278",1278]
[null,null,166,255,{"$nulls":34},"DDB_UNUSED_1279",1279]
[]
["Private Range Information Numbers in Control Direction"]
["ASDU Type","COT","FUN","Inf. No.","Display Text (English)","GI","Model Number",{"$nulls":31},"DDB Signal Description","DDB"]
[null,null,null,"No.",null,null,1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L",null,"Ordinal"]
[20,20,165,32,"Control Input 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_1",832]
[20,20,165,33,"Control Input 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_2",833]
[20,20,165,34,"Control Input 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_3",834]
[20,20,165,35,"Control Input 4",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_4",835]
[20,20,165,36,"Control Input 5",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_5",836]
[20,20,165,37,"Control Input 6",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_6",837]
[20,20,165,38,"Control Input 7",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_7",838]
[20,20,165,39,"Control Input 8",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_8",839]
[20,20,165,40,"Control Input 9",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_9",840]
[20,20,165,41,"Control Input 10",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_10",841]
[20,20,165,42,"Control Input 11",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_11",842]
[20,20,165,43,"Control Input 12",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_12",843]
[20,20,165,44,"Control Input 13",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_13",844]
[20,20,165,45,"Control Input 14",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_14",845]
[20,20,165,46,"Control Input 15",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_15",846]
[20,20,165,47,"Control Input 16",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_16",847]
[20,20,165,48,"Control Input 17",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_17",848]
[20,20,165,49,"Control Input 18",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_18",849]
[20,20,165,50,"Control Input 19",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_19",850]
[20,20,165,51,"Control Input 20",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_20",851]
[20,20,165,52,"Control Input 21",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_21",852]
[20,20,165,53,"Control Input 22",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_22",853]
[20,20,165,54,"Control Input 23",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_23",854]
[20,20,165,55,"Control Input 24",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_24",855]
[20,20,165,56,"Control Input 25",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_25",856]
[20,20,165,57,"Control Input 26",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_26",857]
[20,20,165,58,"Control Input 27",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_27",858]
[20,20,165,59,"Control Input 28",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_28",859]
[20,20,165,60,"Control Input 29",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_29",860]
[20,20,165,61,"Control Input 30",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_30",861]
[20,20,165,62,"Control Input 31",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_31",862]
[20,20,165,63,"Control Input 32",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","DDB_CONTROL_32",863]
[]
["Disturbance Data Actual Channel Identifiers"]
["ACC","Standard","Interpretation"]
[0,"Global","Null Channel"]
[1,"IL1","IA"]
[2,"IL2","IB"]
[3,"IL3","IC"]
[4,"IN","IN"]
[5,"VL1E","VAN"]
[6,"VL2E","VBN"]
[7,"VL3E","VCN"]
[8,"VCS/VN","VCS/VN",null,null,null,"P143/P144/P145 only"]
[64,"-","IN Sensitive"]
[72,"-","Frequency"]
[245,"-","SampleTime"]
[]
["Fault Record Data"]
["ASDU Type","COT","FUN","Inf. No.","Description",null,"Model Number",{"$nulls":31},"Valid When ..."]
[null,null,null,"No.",null,null,1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
[4,1,160,73,"Fault Location - Ohms",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Sufficient pre-fault sample data is available at the time of the fault."]
[4,1,170,0,"Active setting group",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,1,"Frequency",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Relay is correctly frequency tracking (40Hz - 70Hz)"]
[4,1,170,2,"Overall fault duration",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","The protection start time and undercurrent pickup times are valid:\nDur. = Undercurrent pickup time - start time"]
[4,1,170,3,"Circuit Breaker operating time",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","The protection trip time and undercurrent pickup times are valid:\nOp. Time = Undercurrent pickup time - trip time"]
[4,1,170,4,"Protection operating time",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","The protection trip time and start times are valid:\nOp. Time = Trip time - start time"]
[4,1,170,5,"Phase A fault current magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,6,"Phase B fault current magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,7,"Phase C fault current magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,8,"Residual Neutral current magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,9,"Residual Neutral current magnitude (derived)",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,10,"Sensitive Neutral current magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,11,"Phase A-B fault voltage magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,12,"Phase B-C fault voltage magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,13,"Phase C-A fault voltage magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,14,"Residual Neutral voltage magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,15,"Phase A fault voltage magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,16,"Phase B fault voltage magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,17,"Phase C fault voltage magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always valid."]
[4,1,170,18,"Restricted Earth Fault bias",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","SEF/REF Protection is Enabled. and the operating mode is either:\n    o. Lo Z REF Enabled.\n    o. Lo Z REF + SEF\n    o. Lo Z REF + Wattmetric"]
[4,1,170,19,"Restricted Earth Fault differential",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*"]
[4,1,170,255,"No more valid data",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Under normal circumstances this element will not be transmitted.  It is used to indicate there is no more valid data within the current fault record."]
["Notes: "]
["1.  The 'V' column indicates if the fault record element has to pass a validity check prior to being transmitted."]
["2.  The 'Valid When' column provides the criteria for the element to be classed as valid."]
["3.  Only valid elements will be transmitted."]
["4.  If an internal error occurs (i.e. No more valid data is found in the current fault record) an ASDU4 of FUN 166 INF 255 will be transmitted."]
["Generic Measurements added in software version 35C"]
["Generic Measurements",{"$nulls":5},"Model Number"]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
["The following commands can be used to access measurements.  The measurement quantities are given below:"]
["ASDU Type","COT","FUN","Inf. No.","Description"]
[null,null,null,"No."]
[21,42,254,240,"Get Courier column heading text",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","NOG = 0"]
[21,42,254,241,"Get Courier column heading data",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","NOG = 1,                                                GIN = Courier address of column,\nKOD = 10 for description"]
[21,42,254,243,"Get Courier Cell Data",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","NOG = 1,                                                            GIN = Courier address of cell,\nKOD = 0"]
["The data returned in response to a Get Courier Cell Data command is:"]
[null,"GIN Reference",null,null,"The Courier Column and Row"]
[null,"Description",null,null,"The Courier Text"]
[null,"Actual Value",null,null,"The value of the measurement"]
[null,"Dimension",null,null,"The units of the measurement"]
[null,"Is Read Only",null,null,"Always 1"]
[null,"Enumerated Text Array",null,null,"Used if a measurement is invalid"]
[null,"Enumerated Text Value",null,null,"Used if a measurement is invalid"]
[]
[null,null,"Generic Measurements - Derived from Datacells Sheet at Courier Columns [02xx], [03xx], [04xx]"]
[null,null,"GIN",null,"Description","Model Number","Model Number",{"$nulls":31},"Valid When ..."]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
[null,null,200,"0200","MEASUREMENTS 1",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0201",null,"IA Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0202",null,"IA Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0203",null,"IB Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0204",null,"IB Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0205",null,"IC Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0206",null,"IC Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0207",null,"IN Measured Mag",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0208",null,"IN Measured Ang",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0209",null,"IN Derived Mag",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"020A",null,"IN Derived Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"020B",null,"ISEF Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"020C",null,"ISEF Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0210",null,"IA RMS",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0211",null,"IB RMS",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0212",null,"IC RMS",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0214",null,"VAB Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0215",null,"VAB Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0216",null,"VBC Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0217",null,"VBC Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0218",null,"VCA Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0219",null,"VCA Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"021A",null,"VAN Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"021B",null,"VAN Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"021C",null,"VBN Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"021D",null,"VBN Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"021E",null,"VCN Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"021F",null,"VCN Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0222",null,"VN Derived Mag",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0222",null,"VN Measured Mag",{"$nulls":17},"*","*","*","*","*",{"$nulls":11},"Always Valid."]
[null,null,"0223",null,"VN Derived Ang",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0223",null,"VN Measured Ang",{"$nulls":17},"*","*","*","*","*",{"$nulls":11},"Always Valid."]
[null,null,"0227",null,"VAN RMS",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0228",null,"VBN RMS",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0229",null,"VCN RMS",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[{"$nulls":6},"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"022D",null,"Frequency",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Relay is Correctly Frequency Tracking (40Hz - 70Hz)."]
[null,null,"022E",null,"C/S Voltage Mag",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"022F",null,"C/S Voltage Ang",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0230",null,"C/S Bus-Line Ang",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","System Checks Enabled."]
[null,null,"0231",null,"Slip Frequency",{"$nulls":7},"*","*","*","*","*","*","*","*","*","*",{"$nulls":5},"*","*","*","*","*","*","*","*","*","*","*","System Checks Enabled."]
[null,null,"0240",null,"I1 Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0241",null,"I1 Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0242",null,"I2 Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0243",null,"I2 Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0244",null,"I0 Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0245",null,"I0 Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0246",null,"V1 Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0247",null,"V1 Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0248",null,"V2 Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0249",null,"V2 Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"024A",null,"V0 Magnitude",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"024B",null,"V0 Phase Angle",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0300",null,"MEASUREMENTS 2",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0301",null,"A Phase Watts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0302",null,"B Phase Watts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0303",null,"C Phase Watts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0304",null,"A Phase VArs",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0305",null,"B Phase VArs",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0306",null,"C Phase VArs",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0307",null,"A Phase VA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0308",null,"B Phase VA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0309",null,"C Phase VA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"030A",null,"3 Phase Watts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"030B",null,"3 Phase VArs",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"030C",null,"3 Phase VA",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"030E",null,"3Ph Power Factor",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"030F",null,"APh Power Factor",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0310",null,"BPh Power Factor",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0311",null,"CPh Power Factor",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0312",null,"3Ph WHours Fwd",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0313",null,"3Ph WHours Rev",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0314",null,"3Ph VArHours Fwd",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0315",null,"3Ph VArHours Rev",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0316",null,"3Ph W Fix Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0317",null,"3Ph VArs Fix Dem",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0318",null,"IA  Fixed Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"GIN",null,"Description","Model Number","Model Number",{"$nulls":31},"Valid When ..."]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
[null,null,"0319",null,"IB  Fixed Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"031A",null,"IC  Fixed Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"031B",null,"3 Ph W Roll Dem",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"031C",null,"3Ph VArs RollDem",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"031D",null,"IA Roll Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"031E",null,"IB Roll Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"031F",null,"IC Roll Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0320",null,"3Ph W Peak Dem",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0321",null,"3Ph VAr Peak Dem",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0322",null,"IA Peak Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0323",null,"IB Peak Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0324",null,"IC Peak Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[{"$nulls":6},"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0400",null,"MEASUREMENTS 3",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0401",null,"Highest Phase I  ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0402",null,"Thermal State",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Thermal Overload Enabled."]
[null,null,"0404",null,"IREF Diff",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Low Impedance E/F Enabled."]
[null,null,"0405",null,"IREF Bias",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Low Impedance E/F Enabled."]
[null,null,"0406",null,"Admittance SEF",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Admittance Protection Enabled."]
[null,null,"0407",null,"Conductance SEF",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Admittance Protection Enabled."]
[null,null,"0408",null,"Susceptance SEF",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Admittance Protection Enabled."]
[null,null,"0409",null,"Admittance E/F",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Admittance Protection Enabled."]
[null,null,"040A",null,"Conductance E/F",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Admittance Protection Enabled."]
[null,null,"040B",null,"Susceptance E/F",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Admittance Protection Enabled."]
[null,null,"040C",null,"I2/I1 Ratio",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"040D",null,"SEF Power",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","SEF Wattmetric Enabled."]
[null,null,"040E",null,"df/dt",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","ROCOF Protection Enabled."]
[null,null,"040F",null,"IA 2nd Harmonic",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0410",null,"IB 2nd Harmonic",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0411",null,"IC 2nd Harmonic",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Always Valid."]
[null,null,"0412",null,"Aph Sen Watts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Valid When [091C]&[4129]=Enabled."]
[null,null,"0413",null,"Aph Sen Vars",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Valid When [091C]&[4129]=Enabled."]
[null,null,"0414",null,"Aph Power Angle ",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Valid When [091C]&[4129]=Enabled."]
[null,null,"0500",null,"STAGE STATISTICS"]
[null,null,"0501",null,"Stg1 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,502,null,"Stg1 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,503,null,"Stg1 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,504,null,"Stg1 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,505,null,"Stg1 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,506,null,"Stg1 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,507,null,"Stg1 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,508,null,"Stg1 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"050A",null,"Stg2 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"050B",null,"Stg2 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"050C",null,"Stg2 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"050D",null,"Stg2 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"050E",null,"Stg2 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"050F",null,"Stg2 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0510",null,"Stg2 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0511",null,"Stg2 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0513",null,"Stg3 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0514",null,"Stg3 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0515",null,"Stg3 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0516",null,"Stg3 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0517",null,"Stg3 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0518",null,"Stg3 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0519",null,"Stg3 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"051A",null,"Stg3 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"051C",null,"Stg4 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"051D",null,"Stg4 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"051E",null,"Stg4 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"051F",null,"Stg4 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0520",null,"Stg4 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0521",null,"Stg4 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0522",null,"Stg4 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0523",null,"Stg4 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0525",null,"Stg5 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0526",null,"Stg5 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0527",null,"Stg5 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0528",null,"Stg5 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0529",null,"Stg5 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"052A",null,"Stg5 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"052B",null,"Stg5 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"052C",null,"Stg5 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"052E",null,"Stg6 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"052F",null,"Stg6 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0530",null,"Stg6 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0531",null,"Stg6 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0532",null,"Stg6 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"GIN",null,"Description","Model Number","Model Number",{"$nulls":31},"Valid When ..."]
[{"$nulls":6},1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
[null,null,"0533",null,"Stg6 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0534",null,"Stg6 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0535",null,"Stg6 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0537",null,"Stg7 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0538",null,"Stg7 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0539",null,"Stg7 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"053A",null,"Stg7 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"053B",null,"Stg7 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"053C",null,"Stg7 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"053D",null,"Stg7 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"053E",null,"Stg7 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0540",null,"Stg8 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0541",null,"Stg8 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0542",null,"Stg8 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0543",null,"Stg8 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0544",null,"Stg8 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0545",null,"Stg8 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0546",null,"Stg8 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0547",null,"Stg8 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0549",null,"Stg9 f+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"054A",null,"Stg9 f+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"054B",null,"Stg9 f+df/dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"054C",null,"Stg9 df/dt+t Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"054D",null,"Stg9 df/dt+t trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"054E",null,"Stg9 f+Df/Dt Starts",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"054F",null,"Stg9 f+Df/Dt trips",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[null,null,"0550",null,"Stg9 Revn Date",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Advanced Frequency Enabled."]
[]
["Generic Commands for Additional Generic Measurements"]
["ASDU Type","COT","FUN","Inf. No.","Description",null,"Model Number"]
[null,null,null,"No.",null,null,1,"2A","2B","2C","2D","2H","3A","3C","3D","3E","3F","3G","3H","3J","3K","3L","4A","4B","4C","4D","4H","5A","5B","5C","5D","5E","5F","5G","5H","5J","5K","5L"]
[20,20,249,129,"Reset Demand",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Resets Demand Measurements."]
[20,20,249,130,"Reset Thermal",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Resets Thermal Measurements."]
[20,20,249,131,"Reset Statistics",null,"*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","*","Resets Advanced Frequency Statistics."]