## Modbus File
Resi9 Energy Meter Wired
Modbus File
Resi9 Energy Meter Wired, Universal, 80A/160A/250A, 6 Channels
R9MUX6M-MdBs-EN-05
01/2025

## Safety Information
Safety Information
Important Information
Read these instructions carefully, and look at the equipment to become familiar with the device before trying to install, operate, service, or maintain it. The following special messages may appear throughout this documentation or on the equipment to warn of potential hazards or to call attention to information that clarifies or simplifies a procedure.
The addition of this symbol to a “Danger” or “Warning” safety label indicates that an electrical hazard exists which will result in personal injury if the instructions are not followed.
This is the safety alert symbol. It is used to alert you to potential personal injury hazards. Obey all safety messages that follow this symbol to avoid possible injury or death.
Safety Precautions
Cybersecurity Notice - Access control
The R9MUX6M Energy meter allows local access and the remote access based on Modbus-RTU. It is strongly recommended to secure the Energy meter by authorized users.
It is advisable that the R9MUX6M Energy meter is installed in a secure area in which access rules are implemented and managed (e.g., locked cabinet with keys). Also, always ensure physical protection on communication/connection ports and network cables.
For remote access based on Modbus RTU of the R9MUX6M Energy meter, it is advisable that in addition to local access control, the system that is able to access the Energy meter should deploy a defense-in-depth approach to limit such an access to authorized components in the system.

## About the File
About the File
Document Scope
The aim of this file is to provide users, installers, and maintenance personnel with the Modbus registers of: • Resi9 Energy Meter Wired, Universal, 80A/160A/250A, 6 Channels These registers provide metering (current, voltage, power, power factor, energy), relay output, alarm, SOE information.
Validity Note
This document applies to the following 3-phase Energy meter R9MUX6M. If you are using a 1-phase Energy meter R9M80X6M, please refer to the corresponding Modbus Register file. • This file is applicable for Energy meter with firmware version 1002 or greater, the firmware version can be read from the Modbus register "FW version" • Note: There are new registers available only for certain firmware versions. Please refer to the Register List tab for detailed information.
Convention
Resi9 Energy Meter Wired, Universal, 80A/160A/250A, 6 Channels is referred to as Energy meter or R9MUX6M﻿
Online Information
The information contained in this file is likely to be updated at any time. Schneider Electric strongly recommends that you have the most recent and up-todate version available on https://se.com/ww/en/download
The technical characteristics of the devices described in this file also appear online. To access the information online, go to the Schneider Electric home page at https://www.se.com
Related Documents
| Title of documentation | Reference number
| Energy meter - Instruction Sheet | Istruction Sheet HTML Link
| Energy meter - Configuration and User Manual | Configuration and User Manual
All documents in several languages can be found in the HTML link by clicking/taping on Globe icon:

## Register List
Category | Sub Cat 1 | Sub Cat 2 | Description | FD Meter | PDM Register | PDU Register | Units | Size (INT16) | Data Type | Access iMEXXX | Range | Default | User Notes | Applicable for Firmware Version
System Setup & Status
Product & Features
|  |  | Meter Name | Y | 31 | 30 |  | 20 | UTF8 | RW |  | "Energy Meter" |  | 1002 or greater
|  |  | Meter Model | Y | 51 | 50 |  | 20 | UTF8 | R |  | "R9MUX6M " |  | 1002 or greater
|  |  | Manufacturer | Y | 71 | 70 |  | 20 | UTF8 | R |  | "Schneider Electric" |  | 1002 or greater
|  |  | Product ID Number | Y | 91 | 90 |  | 1 | INT16U | R |  | 15901 |  | 1002 or greater
|  |  | Hardware Detected | Y | 92 | 91 |  | 11 | UTF8 | R |  | R9MUX6M = xxx.yyy.zzz |  | 1002 or greater
Option Slot A
|  |  | Installed Option – Slot A | Y | 403 | 402 |  | 1 | INT16U | R |  | 0xFFFF
|  |  | Serial Number | Y | 404 | 403 |  | 2 | INT32U | R |  |  |  | 1002 or greater
|  |  | Date of Manufacture | Y | 406 | 405 |  | 4 | DATETIME | R
|  |  | Hardware Revision | Y | 410 | 409 |  | 5 | UTF8 | R
|  |  | FW version | Y | 415 | 414 |  | 1 | INT16U | R |  |  |  | 1002 or greater
Timekeeping
Present Date & Time (4 register format)
|  |  | Year | Y | 1846 | 1845 |  | 1 | INT16U | RW | 0 – 99 | 0x0000 |  | 1002 or greater
|  |  | Month & Day | Y | 1847 | 1846 |  | 1 | INT16U | RW | 1 – 12, 1 – 31 | 0x0101 |  | 1002 or greater
|  |  | Hour & Minute | Y | 1848 | 1847 |  | 1 | INT16U | RW | 0 – 23, 0 – 59 | 0x0000 |  | 1002 or greater
Meter Setup & Status
Metering Setup
|  |  | VT Primary | Y | 2027 | 2026 | V | 2 | FLOAT32 | RW | 1 - 999999 | 220 |  | 1002 or greater
|  |  | VT Secondary | Y | 2029 | 2028 | V | 1 | INT16U | RW | 1 - 374 | 220 |  | 1002 or greater
|  |  | L1 Label | Y | 2031 | 2030 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L1 CT Rating | Y | 2039 | 2038 | A | 1 | INT16U | RW | 80、160、250 | 80 | 80 = 80A, 160 = 160A, 250 = 250A | 1002 or greater
|  |  | L1 Direction | Y | 2041 | 2040 |  | 1 | INT16U | RW | 0:Default 1:Reverse | 0 |  | 1002 or greater
|  |  | L2 Label | Y | 2045 | 2044 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L2 CT Rating | Y | 2053 | 2052 | A | 1 | INT16U | RW | 80、160、250 | 80 | 80 = 80A, 160 = 160A, 250 = 250A | 1002 or greater
|  |  | L2 Direction | Y | 2055 | 2054 |  | 1 | INT16U | RW | 0:Default 1:Reverse | 0 |  | 1002 or greater
|  |  | L3 Label | Y | 2059 | 2058 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L3 CT Rating | Y | 2067 | 2066 | A | 1 | INT16U | RW | 80、160、250 | 80 | 80 = 80A, 160 = 160A, 250 = 250A | 1002 or greater
|  |  | L3 Direction | Y | 2069 | 2068 |  | 1 | INT16U | RW | 0:Default 1:Reverse | 0 |  | 1002 or greater
|  |  | L4 Label | Y | 2073 | 2072 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L4 CT Rating | Y | 2081 | 2080 | A | 1 | INT16U | RW | 80、160、250 | 80 | 80 = 80A, 160 = 160A, 250 = 250A | 1002 or greater
|  |  | L4 Direction | Y | 2083 | 2082 |  | 1 | INT16U | RW | 0:Default 1:Reverse | 0 |  | 1002 or greater
|  |  | L5 Label | Y | 2087 | 2086 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L5 CT Rating | Y | 2095 | 2094 | A | 1 | INT16U | RW | 80、160、250 | 80 | 80 = 80A, 160 = 160A, 250 = 250A | 1002 or greater
|  |  | L5 Direction | Y | 2097 | 2096 |  | 1 | INT16U | RW | 0:Default 1:Reverse | 0 |  | 1002 or greater
|  |  | L6 Label | Y | 2101 | 2100 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L6 CT Rating | Y | 2109 | 2108 | A | 1 | INT16U | RW | 80、160、250 | 80 | 80 = 80A, 160 = 160A, 250 = 250A | 1002 or greater
|  |  | L6 Direction | Y | 2111 | 2110 |  | 1 | INT16U | RW | 0:Default 1:Reverse | 0 |  | 1002 or greater
|  |  | L1L2L3 Label | Y | 2117 | 2116 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L4L5L6 Label | Y | 2125 | 2124 |  | 8 | INT16U | RW | Cstring | 0 |  | 1002 or greater
|  |  | L1 Voltage Input | Y | 2133 | 2132 |  | 1 | INT16U | RW | 0：UL1，1：U1; 2:U2; 3:U3 | 0 |  | 1002 or greater
|  |  | L2 Voltage Input | Y | 2135 | 2134 |  | 1 | INT16U | RW | 0：UL2，1：U1; 2:U2; 3:U3 | 0 |  | 1002 or greater
|  |  | L3 Voltage Input | Y | 2137 | 2136 |  | 1 | INT16U | RW | 0：UL3，1：U1; 2:U2; 3:U3 | 0 |  | 1002 or greater
|  |  | L4 Voltage Input | Y | 2139 | 2138 |  | 1 | INT16U | RW | 0：UL1，1：U1; 2:U2; 3:U3 | 0 |  | 1002 or greater
|  |  | L5 Voltage Input | Y | 2141 | 2140 |  | 1 | INT16U | RW | 0：UL2，1：U1; 2:U2; 3:U3 | 0 |  | 1002 or greater
|  |  | L6 Voltage Input | Y | 2143 | 2142 |  | 1 | INT16U | RW | 0：UL3，1：U1; 2:U2; 3:U3 | 0 |  | 1002 or greater
Inputs & Outputs
Option Slots
Relay Outputs
|  |  | Relay Output Status | Y | 2201 | 2200 |  | 1 | BITMAP | R | 0x0000: DO1 Off, DO2 Off 0x0001: DO1 ON, DO2 Off 0x0010: DO1 Off, DO2 ON 0x0011: DO1 ON, DO2 ON |  | Bit00:DO1 Bit01:DO2
Relay Outputs Setup
Relay Output DO1
|  |  | Operation Mode | Y | 2203 | 2202 |  | 1 | INT16U | R | 2 | 2 | 2 = alarm | 1002 or greater
|  |  | Behavioral Mode(Level or Pulse) | Y | 2204 | 2203 |  | 1 | INT16U | RW | 0 – 1 | 0 | 0 = Normal 1 = Timed | 1002 or greater
|  |  | On Time For Timed Mode(Pulse width) | Y | 2205 | 2204 | 0.1seconds | 1 | INT16U | RW | 0-2000 | 10 | The time for the output to remain energized when the output is energized in timed mode. | 1002 or greater
Relay Output DO2
|  |  | Operation Mode | Y | 2212 | 2211 |  | 1 | INT16U | R | 2 | 2 | 2 = alarm | 1002 or greater
|  |  | Behavioral Mode(Level or Pulse) | Y | 2213 | 2212 |  | 1 | INT16U | RW | 0 – 1 | 0 | 0 = Normal 1 = Timed | 1002 or greater
|  |  | On Time For Timed Mode(Pulse width) | Y | 2214 | 2213 | 0.1seconds | 1 | INT16U | RW | 0-2000 | 10 | The time for the output to remain energized when the output is energized in timed mode. | 1002 or greater
Alarm
DO1 Alarm Bitmask
|  |  | DO1 Alarm Bit Mask 1 | Y | 2206 | 2205 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0001 | 0: Disable 1: Enable BIT0：Over Current L1 BIT1：Under Current L1 BIT2：Over Current L2 BIT3：Under Current L2 BIT4：Over Current L3 BIT5：Under Current L3 BIT6：Over Current L4 BIT7：Under Current L4 BIT8：Over Current L5 BIT9：Under Current L5 BIT10：Over Current L6 BIT11：Under Current L6 BIT12：Over Power, Active L1 BIT13：Under Power, Active L1 BIT14：Over Power, Active L2 BIT15：Under Power, Active L2 | 1002 or greater
|  |  | DO1 Alarm Bit Mask 2 | Y | 2207 | 2206 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Active L3 BIT1：Under Power, Active L3 BIT2：Over Power, Active L4 BIT3：Under Power, Active L4 BIT4：Over Power, Active L5 BIT5：Under Power, Active L5 BIT6：Over Power, Active L6 BIT7：Under Power, Active L6 BIT8：Over Power, Reactive L1 BIT9：Under Power, Reactive L1 BIT10：Over Power, Reactive L2 BIT11：Under Power, Reactive L2 BIT12：Over Power, Reactive L3 BIT13：Under Power, Reactive L3 BIT14：Over Power, Reactive L4 BIT15：Under Power, Reactive L4 | 1002 or greater
|  |  | DO1 Alarm Bit Mask 3 | Y | 2208 | 2207 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Reactive L5 BIT1：Under Power, Reactive L5 BIT2：Over Power, Reactive L6 BIT3：Under Power, Reactive L6 BIT4：Over Power, Apparent L1 BIT5：Under Power, Apparent L1 BIT6：Over Power, Apparent L2 BIT7：Under Power, Apparent L2 BIT8：Over Power, Apparent L3 BIT9：Under Power, Apparent L3 BIT10：Over Power, Apparent L4 BIT11：Under Power, Apparent L4 BIT12：Over Power, Apparent L5 BIT13：Under Power, Apparent L5 BIT14：Over Power, Apparent L6 BIT15：Under Power, Apparent L6 | 1002 or greater
|  |  | DO1 Alarm Bit Mask 4 | Y | 2209 | 2208 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Under Power Factor, True L1 BIT1：Under Power Factor, True L2 BIT2：Under Power Factor, True L3 BIT3：Under Power Factor, True L4 BIT4：Under Power Factor, True L5 BIT5：Under Power Factor, True L6 BIT6：Over Frequency BIT7：Under Frequency BIT8：Over Current L1 Total Harmonic Distortion BIT9：Over Current L2 Total Harmonic Distortion BIT10：Over Current L3 Total Harmonic Distortion BIT11：Over Current L4 Total Harmonic Distortion BIT12：Over Current L5 Total Harmonic Distortion BIT13：Over Current L6 Total Harmonic Distortion BIT14：Over Voltage 1 BIT15：Under Voltage 1 | 1002 or greater
|  |  | DO1 Alarm Bit Mask 5 | Y | 2210 | 2209 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Voltage 2 BIT1：Under Voltage 2 BIT2：Over Voltage 3 BIT3：Under Voltage 3 BIT4：Over Current L1-L3 BIT5：Under Current L1-L3 BIT6：Over Current L4-L6 BIT7：Under Current L4-L6 BIT8：Over Power, Active L1-L3 BIT9：Under Power, Active L1-L3 BIT10：Over Power, Active L4-L6 BIT11：Under Power, Active L4-L6 BIT12：Over Power, Reactive L1-L3 BIT13：Under Power, Reactive L1-L3 BIT14：Over Power, Reactive L4-L6 BIT15：Under Power, Reactive L4-L6 | 1002 or greater
|  |  | DO1 Alarm Bit Mask 6 | Y | 2211 | 2210 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Apparent L1-L3 BIT1：Under Power, Apparent L1-L3 BIT2：Over Power, Apparent L4-L6 BIT3：Under Power, Apparent L4-L6 BIT4：Under Power Factor, True L1-L3 BIT5：Under Power Factor, True L4-L6 BIT6：Over Voltage Total Harmonic Distortion 1 BIT7：Over Voltage Total Harmonic Distortion 2 BIT8：Over Voltage Total Harmonic Distortion 3 BIT9：Over Voltage Unbalance BIT10：Over Current Unbalance 1 BIT11：Over Current Unbalance 2 | 1002 or greater
DO2 Alarm Bitmask
|  |  | DO2 Alarm Bit Mask 1 | Y | 2215 | 2214 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0001 | 0: Disable 1: Enable BIT0：Over Current L1 BIT1：Under Current L1 BIT2：Over Current L2 BIT3：Under Current L2 BIT4：Over Current L3 BIT5：Under Current L3 BIT6：Over Current L4 BIT7：Under Current L4 BIT8：Over Current L5 BIT9：Under Current L5 BIT10：Over Current L6 BIT11：Under Current L6 BIT12：Over Power, Active L1 BIT13：Under Power, Active L1 BIT14：Over Power, Active L2 BIT15：Under Power, Active L2 | 1002 or greater
|  |  | DO2 Alarm Bit Mask 2 | Y | 2216 | 2215 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Active L3 BIT1：Under Power, Active L3 BIT2：Over Power, Active L4 BIT3：Under Power, Active L4 BIT4：Over Power, Active L5 BIT5：Under Power, Active L5 BIT6：Over Power, Active L6 BIT7：Under Power, Active L6 BIT8：Over Power, Reactive L1 BIT9：Under Power, Reactive L1 BIT10：Over Power, Reactive L2 BIT11：Under Power, Reactive L2 BIT12：Over Power, Reactive L3 BIT13：Under Power, Reactive L3 BIT14：Over Power, Reactive L4 BIT15：Under Power, Reactive L4 | 1002 or greater
|  |  | DO2 Alarm Bit Mask 3 | Y | 2217 | 2216 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Reactive L5 BIT1：Under Power, Reactive L5 BIT2：Over Power, Reactive L6 BIT3：Under Power, Reactive L6 BIT4：Over Power, Apparent L1 BIT5：Under Power, Apparent L1 BIT6：Over Power, Apparent L2 BIT7：Under Power, Apparent L2 BIT8：Over Power, Apparent L3 BIT9：Under Power, Apparent L3 BIT10：Over Power, Apparent L4 BIT11：Under Power, Apparent L4 BIT12：Over Power, Apparent L5 BIT13：Under Power, Apparent L5 BIT14：Over Power, Apparent L6 BIT15：Under Power, Apparent L6 | 1002 or greater
|  |  | DO2 Alarm Bit Mask 4 | Y | 2218 | 2217 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Under Power Factor, True L1 BIT1：Under Power Factor, True L2 BIT2：Under Power Factor, True L3 BIT3：Under Power Factor, True L4 BIT4：Under Power Factor, True L5 BIT5：Under Power Factor, True L6 BIT6：Over Frequency BIT7：Under Frequency BIT8：Over Current L1 Total Harmonic Distortion BIT9：Over Current L2 Total Harmonic Distortion BIT10：Over Current L3 Total Harmonic Distortion BIT11：Over Current L4 Total Harmonic Distortion BIT12：Over Current L5 Total Harmonic Distortion BIT13：Over Current L6 Total Harmonic Distortion BIT14：Over Voltage 1 BIT15：Under Voltage 1 | 1002 or greater
|  |  | DO2 Alarm Bit Mask 5 | Y | 2219 | 2218 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Voltage 2 BIT1：Under Voltage 2 BIT2：Over Voltage 3 BIT3：Under Voltage 3 BIT4：Over Current L1-L3 BIT5：Under Current L1-L3 BIT6：Over Current L4-L6 BIT7：Under Current L4-L6 BIT8：Over Power, Active L1-L3 BIT9：Under Power, Active L1-L3 BIT10：Over Power, Active L4-L6 BIT11：Under Power, Active L4-L6 BIT12：Over Power, Reactive L1-L3 BIT13：Under Power, Reactive L1-L3 BIT14：Over Power, Reactive L4-L6 BIT15：Under Power, Reactive L4-L6 | 1002 or greater
|  |  | DO2 Alarm Bit Mask 6 | Y | 2220 | 2219 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Apparent L1-L3 BIT1：Under Power, Apparent L1-L3 BIT2：Over Power, Apparent L4-L6 BIT3：Under Power, Apparent L4-L6 BIT4：Under Power Factor, True L1-L3 BIT5：Under Power Factor, True L4-L6 BIT6：Over Voltage Total Harmonic Distortion 1 BIT7：Over Voltage Total Harmonic Distortion 2 BIT8：Over Voltage Total Harmonic Distortion 3 BIT9：Over Voltage Unbalance BIT10：Over Current Unbalance 1 BIT11：Over Current Unbalance 2 | 1002 or greater
Alarm Status
|  |  | Alarm Status Bit Mask 1 | Y | 11501 | 11500 |  | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000 | 0 = No Alarm 1 = Alarm BIT0：Over Current L1 BIT1：Under Current L1 BIT2：Over Current L2 BIT3：Under Current L2 BIT4：Over Current L3 BIT5：Under Current L3 BIT6：Over Current L4 BIT7：Under Current L4 BIT8：Over Current L5 BIT9：Under Current L5 BIT10：Over Current L6 BIT11：Under Current L6 BIT12：Over Current L1-L3 BIT13：Under Current L1-L3 BIT14：Over Current L4-L6 BIT15：Under Current L4-L6 | 1005 or greater
|  |  | Alarm Status Bit Mask 2 | Y | 11502 | 11501 |  | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000 | 0 = No Alarm 1 = Alarm BIT0：Over Power, Active L1 BIT1：Under Power, Active L1 BIT2：Over Power, Active L2 BIT3：Under Power, Active L2 BIT4：Over Power, Active L3 BIT5：Under Power, Active L3 BIT6：Over Power, Active L4 BIT7：Under Power, Active L4 BIT8：Over Power, Active L5 BIT9：Under Power, Active L5 BIT10：Over Power, Active L6 BIT11：Under Power, Active L6 BIT12：Over Power, Active L1-L3 BIT13：Under Power, Active L1-L3 BIT14：Over Power, Active L4-L6 BIT15：Under Power, Active L4-L6 | 1005 or greater
|  |  | Alarm Status Bit Mask 3 | Y | 11503 | 11502 |  | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000 | 0 = No Alarm 1 = Alarm BIT0：Over Frequency BIT1：Under Frequency BIT2：Over Voltage 1 BIT3：Under Voltage 1 BIT4：Over Voltage 2 BIT5：Under Voltage 2 BIT6：Over Voltage 3 BIT7：Under Voltage 3 BIT8：Under Power Factor, True L1 BIT9：Under Power Factor, True L2 BIT10：Under Power Factor, True L3 BIT11：Under Power Factor, True L4 BIT12：Under Power Factor, True L5 BIT13：Under Power Factor, True L6 BIT14：Under Power Factor, True L1-L3 BIT15：Under Power Factor, True L4-L6 | 1005 or greater
Meter Data (Basic)
1s Metering (50/60 Cycles)
Current
|  |  | Current L1 | Y | 3001 | 3000 | A | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Current L2 | Y | 3003 | 3002 | A | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Current L3 | Y | 3005 | 3004 | A | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Current L4 | Y | 3007 | 3006 | A | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Current L5 | Y | 3009 | 3008 | A | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Current L6 | Y | 3011 | 3010 | A | 2 | FLOAT32 | R |  |  |  | 1002 or greater
Voltage
|  |  | Voltage L1-N | Y | 3021 | 3020 | V | 2 | FLOAT32 | R |  |  | Phase Voltage L1 | 1002 or greater
|  |  | Voltage L2-N | Y | 3023 | 3022 | V | 2 | FLOAT32 | R |  |  | Phase Voltage L2 | 1002 or greater
|  |  | Voltage L3-N | Y | 3025 | 3024 | V | 2 | FLOAT32 | R |  |  | Phase Voltage L2 | 1002 or greater
|  |  | Voltage L1-L2 | Y | 3027 | 3026 | V | 2 | FLOAT32 | R |  |  | Line Voltage L1-L2 | 1002 or greater
|  |  | Voltage L2-L3 | Y | 3029 | 3028 | V | 2 | FLOAT32 | R |  |  | Line Voltage L2-L3 | 1002 or greater
|  |  | Voltage L3-L1 | Y | 3031 | 3030 | V | 2 | FLOAT32 | R |  |  | Line Voltage L3-L1 | 1002 or greater
|  | Voltage Unbalance |  | Y | 3033 | 3032 | % | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  | Current Unbalance 1 |  | Y | 3035 | 3034 | % | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  | Current Unbalance 2 |  | Y | 3037 | 3036 | % | 2 | FLOAT32 | R |  |  |  | 1002 or greater
Power
|  |  | Active Power L1 | Y | 3055 | 3054 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Power L2 | Y | 3057 | 3056 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Power L3 | Y | 3059 | 3058 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Power L4 | Y | 3061 | 3060 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Power L5 | Y | 3063 | 3062 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Power L6 | Y | 3065 | 3064 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Power Total L1L2L3 | Y | 3301 | 3300 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Power Total L4L5L6 | Y | 3303 | 3302 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
Power Factor
|  |  | Power Factor L1 | Y | 3098 | 3097 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
|  |  | Power Factor L2 | Y | 3100 | 3099 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
|  |  | Power Factor L3 | Y | 3102 | 3101 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
|  |  | Power Factor L4 | Y | 3104 | 3103 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
|  |  | Power Factor L5 | Y | 3106 | 3105 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
|  |  | Power Factor L6 | Y | 3108 | 3107 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
|  |  | Power Factor Total L1L2L3 | Y | 3313 | 3312 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
|  |  | Power Factor Total L4L5L6 | Y | 3315 | 3314 |  | 2 | FLOAT32 | R | +/- 0.0 – 2.0 |  |  | 1002 or greater
Frequency
|  |  | Frequency | Y | 3127 | 3126 | Hz | 2 | FLOAT32 | R | 45 – 65 |  |  | 1002 or greater
Power Factor, Alternate Format
|  |  | Power Factor L1 | Y | 3131 | 3130 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
|  |  | Power Factor L2 | Y | 3133 | 3132 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
|  |  | Power Factor L3 | Y | 3135 | 3134 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
|  |  | Power Factor L4 | Y | 3137 | 3136 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
|  |  | Power Factor L5 | Y | 3139 | 3138 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
|  |  | Power Factor L6 | Y | 3141 | 3140 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
|  |  | Power Factor Total L1L2L3 | Y | 3317 | 3316 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
|  |  | Power Factor Total L4L5L6 | Y | 3319 | 3318 |  | 2 | FLOAT32 | R | +/- 0.0 – 1.0 |  |  | 1002 or greater
TurboPulse Registers (for prosumer use)
Voltage
|  |  | Voltage L1-N-100ms | N |  | 3200 | V | 2 | FLOAT32 | R |  |  | Phase Voltage L1 | 1005 or greater
|  |  | Voltage L2-N -100ms | Y |  | 3238 | V |  | FLOAT32 | R |  |  | Phase Voltage L2 | 1005 or greater
|  |  | Voltage L3-N -100ms | Y |  | 3240 | V |  | FLOAT32 | R |  |  | Phase Voltage L2 | 1005 or greater
Current
|  |  | Current L1-100ms | N |  | 3202 | A | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Current L2-100ms | N |  | 3204 | A | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Current L3-100ms | N |  | 3206 | A | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Current L4-100ms | N |  | 3208 | A | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Current L5-100ms | N |  | 3210 | A | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Current L6-100ms | N |  | 3212 | A | 2 | FLOAT32 | R |  |  |  | 1005 or greater
Power
|  |  | Active Power L1-100ms | N |  | 3214 | kW | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Active Power L2-100ms | N |  | 3216 | kW | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Active Power L3-100ms | N |  | 3218 | kW | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Active Power L4-100ms | N |  | 3220 | kW | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Active Power L5-100ms | N |  | 3222 | kW | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Active Power L6-100ms | N |  | 3224 | kW | 2 | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Active Power L1L2L3-100ms | Y |  | 3242 | kW |  | FLOAT32 | R |  |  |  | 1005 or greater
|  |  | Active Power L4L5L6-100ms | Y |  | 3244 | kW |  | FLOAT32 | R |  |  |  | 1005 or greater
Energy
Accumulated Energy -32 bit floating point values
|  |  | L1 Active Energy Delivered | Y | 3589 | 3588 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L2 Active Energy Delivered | Y | 3593 | 3592 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L3 Active Energy Delivered | Y | 3597 | 3596 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L4 Active Energy Delivered | Y | 3601 | 3600 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L5 Active Energy Delivered | Y | 3605 | 3604 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L6 Active Energy Delivered | Y | 3609 | 3608 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Energy Delivered Total L1L2L3 | Y | 4175 | 4174 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Energy Delivered Total L4L5L6 | Y | 4177 | 4176 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L1 Active Energy Received | Y | 3661 | 3660 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L2 Active Energy Received | Y | 3665 | 3664 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L3 Active Energy Received | Y | 3669 | 3668 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L4 Active Energy Received | Y | 3673 | 3672 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L5 Active Energy Received | Y | 3677 | 3676 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | L6 Active Energy Received | Y | 3681 | 3680 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Energy Received Total L1L2L3 | Y | 4187 | 4186 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Active Energy Received Total L4L5L6 | Y | 4189 | 4188 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
Partial Accumulated Energy -32 bit floating point values
|  |  | Partial Reset date and time | Y | 3733 | 3732 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
|  |  | Partial L1 Active Energy Delivered | Y | 4199 | 4198 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L2 Active Energy Delivered | Y | 4201 | 4200 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L3 Active Energy Delivered | Y | 4203 | 4202 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial Active Energy Delivered Total L1L2L3 | Y | 4205 | 4204 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L4 Active Energy Delivered | Y | 4207 | 4206 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L5 Active Energy Delivered | Y | 4209 | 4208 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L6 Active Energy Delivered | Y | 4211 | 4210 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial Active Energy Delivered Total L4L5L6 | Y | 4213 | 4212 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L1 Active Energy Received | Y | 4247 | 4246 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L2 Active Energy Received | Y | 4249 | 4248 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L3 Active Energy Received | Y | 4251 | 4250 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial Active Energy Received Total L1L2L3 | Y | 4253 | 4252 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L4 Active Energy Received | Y | 4255 | 4254 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L5 Active Energy Received | Y | 4257 | 4256 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial L6 Active Energy Received | Y | 4259 | 4258 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Partial Active Energy Received Total L4L5L6 | Y | 4261 | 4260 | kWh | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Clear command parameter | Y | 4295 | 4294 |  | 1 | BITMAP | RW | 0x0000-0x003F | 0x003F | Bit00:CH1 Bit01:CH2 Bit02:CH3 Bit03:CH4 Bit04:CH5 Bit05:CH6 CH1-CH6: set the bit to 1 means the command will take effect on this channel, more than one channels can be selected at once | 1002 or greater
Accumulated Energy - 64 bit integer values
|  |  | L1 Active Energy Delivered | Y | 3321 | 3320 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L2 Active Energy Delivered | Y | 3325 | 3324 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L3 Active Energy Delivered | Y | 3329 | 3328 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L4 Active Energy Delivered | Y | 3333 | 3332 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L5 Active Energy Delivered | Y | 3337 | 3336 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L6 Active Energy Delivered | Y | 3341 | 3340 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L1 Active Energy Received | Y | 3345 | 3344 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L2 Active Energy Received | Y | 3349 | 3348 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L3 Active Energy Received | Y | 3353 | 3352 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L4 Active Energy Received | Y | 3357 | 3356 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L5 Active Energy Received | Y | 3361 | 3360 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | L6 Active Energy Received | Y | 3365 | 3364 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Active Energy Delivered Total L1L2L3 | Y | 3369 | 3368 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Active Energy Delivered Total L4L5L6 | Y | 3373 | 3372 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Active Energy Received Total L1L2L3 | Y | 3377 | 3376 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Active Energy Received Total L4L5L6 | Y | 3381 | 3380 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
Partial accumulated Energy - 64 bit integer values
|  |  | Partial L1 Active Energy Delivered | Y | 3385 | 3384 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L1 Active Energy Received | Y | 3389 | 3388 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L2 Active Energy Delivered | Y | 3393 | 3392 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L2 Active Energy Received | Y | 3397 | 3396 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L3 Active Energy Delivered | Y | 3401 | 3400 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L3 Active Energy Received | Y | 3405 | 3404 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L4 Active Energy Delivered | Y | 3409 | 3408 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L4 Active Energy Received | Y | 3413 | 3412 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L5 Active Energy Delivered | Y | 3417 | 3416 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L5 Active Energy Received | Y | 3421 | 3420 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L6 Active Energy Delivered | Y | 3425 | 3424 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial L6 Active Energy Received | Y | 3429 | 3428 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial Active Energy Delivered Total L1L2L3 | Y | 3433 | 3432 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial Active Energy Delivered Total L4L5L6 | Y | 3437 | 3436 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial Active Energy Received Total L1L2L3 | Y | 3441 | 3440 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
|  |  | Partial Active Energy Received Total L4L5L6 | Y | 3445 | 3444 | Wh | 4 | INT64 | R |  |  |  | 1006 or greater
Demand
Demand System 1 (Power)
|  |  | Power Demand Subinterval Duration | Y | 3802 | 3801 | minutes | 1 | INT16U | RW | 1 – 60 | 15 | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration. | 1002 or greater
|  |  | Power Demand Interval Duration | Y | 3803 | 3802 | minutes | 1 | INT16U | RW | 1/5/15/30/60 | 15 |  | 1002 or greater
|  |  | Power Demand Peak Reset Date/Time | Y | 3804 | 3803 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 1 (Active Power L1)
|  |  | Present Demand | Y | 3811 | 3810 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 3815 | 3814 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 3817 | 3816 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 2 (Active Power L2)
|  |  | Present Demand | Y | 3823 | 3822 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 3827 | 3826 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 3829 | 3828 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 3 (Active Power L3)
|  |  | Present Demand | Y | 3835 | 3834 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 3839 | 3838 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 3841 | 3840 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 4 (Active Power L4)
|  |  | Present Demand | Y | 3847 | 3846 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 3851 | 3850 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 3853 | 3852 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 5 (Active Power L5)
|  |  | Present Demand | Y | 3859 | 3858 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 3863 | 3862 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 3865 | 3864 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 6 (Active Power L6)
|  |  | Present Demand | Y | 3871 | 3870 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 3875 | 3874 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 3877 | 3876 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 25 (Active Power Total L1L2L3)
|  |  | Present Demand | Y | 4105 | 4104 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 4109 | 4108 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 4111 | 4110 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Demand Channel 26 (Active Power Total L4L5L6)
|  |  | Present Demand | Y | 4117 | 4116 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand | Y | 4121 | 4120 | kW | 2 | FLOAT32 | R |  |  |  | 1002 or greater
|  |  | Peak Demand DateTime | Y | 4123 | 4122 |  | 4 | DATETIME | R |  |  |  | 1002 or greater
Communications
RS-485 Base
RS-485 Base Port 1 Settings
|  |  | RS-485 Comm Port (M/S) Address | Y | 6501 | 6500 |  | 1 | INT16U | RW | 1 – 247 | 1 | Valid Addresses: Modbus: 1 – 247 | 1002 or greater
|  |  | RS-485 Comm Port (M/S) Baud Rate | Y | 6502 | 6501 |  | 1 | INT16U | RW | 0 – 5 | 4 | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 | 1002 or greater
|  |  | RS-485 Comm Port (M/S) Parity | Y | 6503 | 6502 |  | 1 | INT16U | RW | 0 – 3 | 1 | 0 = N81 1 = E81 2 = O81 3 = N82 parity – ‘E’ven, ‘O’dd or ‘N’one bytesize – Number of bits per byte 8 stopbits – Number of stop bits 1, 2 | 1002 or greater
SOE
SOE numbers
|  |  | Total SOE numbers | Y | 9739 | 9738 |  | 1 | INT16U | R | 0-65535 |  |  | 1002 or greater
|  |  | SOE numbers can reads | Y | 9740 | 9739 |  | 1 | INT16U | R | 0-128 |  |  | 1002 or greater
Last 1
|  |  | SOE Type | Y | 9741 | 9740 |  | 1 | INT16U | R |  |  | Bit15: Alarm Status, 1 = Active, 0 = Inactive; Bit8-Bit14: Reserved; Bit0-Bit7: SOE Type, defined as belows: 1、power on 2、power off 3、set parameter 4、clear energy 5、clear SOE 6、clear extremum 7、Over Current L1 8、Under Current L1 9、Over Current L2 10、Under Current L2 11、Over Current L3 12、Under Current L3 13、Over Current L4 14、Under Current L4 15、Over Current L5 16、Under Current L5 17、Over Current L6 18、Under Current L6 19、Over Power, Active L1 20、Under Power, Active L1 21、Over Power, Active L2 22、Under Power, Active L2 23、Over Power, Active L3 24、Under Power, Active L3 25、Over Power, Active L4 26、Under Power, Active L4 27、Over Power, Active L5 28、Under Power, Active L5 29、Over Power, Active L6 30、Under Power, Active L6 31、Over Power, Reactive L1 32、Under Power, Reactive L1 33、Over Power, Reactive L2 34、Under Power, Reactive L2 35、Over Power, Reactive L3 36、Under Power, Reactive L3 37、Over Power, Reactive L4 38、Under Power, Reactive L4 39、Over Power, Reactive L5 40、Under Power, Reactive L5 41、Over Power, Reactive L6 42、Under Power, Reactive L6 43、Over Power, Apparent L1 44、Under Power, Apparent L1 45、Over Power, Apparent L2 46、Under Power, Apparent L2 47、Over Power, Apparent L3 48、Under Power, Apparent L3 49、Over Power, Apparent L4 50、Under Power, Apparent L4 51、Over Power, Apparent L5 52、Under Power, Apparent L5 53、Over Power, Apparent L6 54、Under Power, Apparent L6 55、Under Power Factor, True L1 56、Under Power Factor, True L2 57、Under Power Factor, True L3 58、Under Power Factor, True L4 59、Under Power Factor, True L5 60、Under Power Factor, True L6 61、Over Frequency 62、Under Frequency 63、Over Current L1 Total Harmonic Distortion 64、Over Current L2 Total Harmonic Distortion 65、Over Current L3 Total Harmonic Distortion 66、Over Current L4 Total Harmonic Distortion 67、Over Current L5 Total Harmonic Distortion 68、Over Current L6 Total Harmonic Distortion 69、Over Voltage 1 70、Under Voltage 1 71、Over Voltage 2 72、Under Voltage 2 73、Over Voltage 3 74、Under Voltage 3 75、Over Current L1L2L3 76、Under Current L1L2L3 77、Over Current L4L5L6 78、Under Current L4L5L6 79、Over Power, Active L1L2L3 80、Under Power, Active L1L2L3 81、Over Power, Active L4L5L6 82、Under Power, Active L4L5L6 83、Over Power, Reactive L1L2L3 84、Under Power, Reactive L1L2L3 85、Over Power, Reactive L4L5L6 86、Under Power, Reactive L4L5L6 87、Over Power, Apparent L1L2L3 88、Under Power, Apparent L1L2L3 89、Over Power, Apparent L4L5L6 90、Under Power, Apparent L4L5L6 91、Under Power Factor, True L1L2L3 92、Under Power Factor, True L4L5L6 93、Over Voltage Total Harmonic Distortion 1 94、Over Voltage Total Harmonic Distortion 2 95、Over Voltage Total Harmonic Distortion 3 96、Over Voltage Unbalance 97、Over Current Unbalance 1 98、Over Current Unbalance 2 99、clear demand Same below. | 1005 or greater
|  |  | Date/Time | Y | 9743 | 9742 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 2
|  |  | SOE Type | Y | 9747 | 9746 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9749 | 9748 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 3
|  |  | SOE Type | Y | 9753 | 9752 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9755 | 9754 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 4
|  |  | SOE Type | Y | 9759 | 9758 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9761 | 9760 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 5
|  |  | SOE Type | Y | 9765 | 9764 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9767 | 9766 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 6
|  |  | SOE Type | Y | 9771 | 9770 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9773 | 9772 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 7
|  |  | SOE Type | Y | 9777 | 9776 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9779 | 9778 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 8
|  |  | SOE Type | Y | 9783 | 9782 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9785 | 9784 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 9
|  |  | SOE Type | Y | 9789 | 9788 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9791 | 9790 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 10
|  |  | SOE Type | Y | 9795 | 9794 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9797 | 9796 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 11
|  |  | SOE Type | Y | 9801 | 9800 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9803 | 9802 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 12
|  |  | SOE Type | Y | 9807 | 9806 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9809 | 9808 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 13
|  |  | SOE Type | Y | 9813 | 9812 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9815 | 9814 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 14
|  |  | SOE Type | Y | 9819 | 9818 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9821 | 9820 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 15
|  |  | SOE Type | Y | 9825 | 9824 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9827 | 9826 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 16
|  |  | SOE Type | Y | 9831 | 9830 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9833 | 9832 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 17
|  |  | SOE Type | Y | 9837 | 9836 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9839 | 9838 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 18
|  |  | SOE Type | Y | 9843 | 9842 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9845 | 9844 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 19
|  |  | SOE Type | Y | 9849 | 9848 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9851 | 9850 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 20
|  |  | SOE Type | Y | 9855 | 9854 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9857 | 9856 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 21
|  |  | SOE Type | Y | 9861 | 9860 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9863 | 9862 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 22
|  |  | SOE Type | Y | 9867 | 9866 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9869 | 9868 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 23
|  |  | SOE Type | Y | 9873 | 9872 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9875 | 9874 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 24
|  |  | SOE Type | Y | 9879 | 9878 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9881 | 9880 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 25
|  |  | SOE Type | Y | 9885 | 9884 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9887 | 9886 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 26
|  |  | SOE Type | Y | 9891 | 9890 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9893 | 9892 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 27
|  |  | SOE Type | Y | 9897 | 9896 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9899 | 9898 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 28
|  |  | SOE Type | Y | 9903 | 9902 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9905 | 9904 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 29
|  |  | SOE Type | Y | 9909 | 9908 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9911 | 9910 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 30
|  |  | SOE Type | Y | 9915 | 9914 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9917 | 9916 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 31
|  |  | SOE Type | Y | 9921 | 9920 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9923 | 9922 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 32
|  |  | SOE Type | Y | 9927 | 9926 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9929 | 9928 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 33
|  |  | SOE Type | Y | 9933 | 9932 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9935 | 9934 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 34
|  |  | SOE Type | Y | 9939 | 9938 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9941 | 9940 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 35
|  |  | SOE Type | Y | 9945 | 9944 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9947 | 9946 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 36
|  |  | SOE Type | Y | 9951 | 9950 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9953 | 9952 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 37
|  |  | SOE Type | Y | 9957 | 9956 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9959 | 9958 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 38
|  |  | SOE Type | Y | 9963 | 9962 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9965 | 9964 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 39
|  |  | SOE Type | Y | 9969 | 9968 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9971 | 9970 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 40
|  |  | SOE Type | Y | 9975 | 9974 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9977 | 9976 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 41
|  |  | SOE Type | Y | 9981 | 9980 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9983 | 9982 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 42
|  |  | SOE Type | Y | 9987 | 9986 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9989 | 9988 |  | 1 | DATETIME | R |  |  |  | 1005 or greater
Last 43
|  |  | SOE Type | Y | 9993 | 9992 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 9995 | 9994 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 44
|  |  | SOE Type | Y | 9999 | 9998 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10001 | 10000 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 45
|  |  | SOE Type | Y | 10005 | 10004 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10007 | 10006 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 46
|  |  | SOE Type | Y | 10011 | 10010 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10013 | 10012 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 47
|  |  | SOE Type | Y | 10017 | 10016 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10019 | 10018 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 48
|  |  | SOE Type | Y | 10023 | 10022 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10025 | 10024 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 49
|  |  | SOE Type | Y | 10029 | 10028 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10031 | 10030 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 50
|  |  | SOE Type | Y | 10035 | 10034 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10037 | 10036 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 51
|  |  | SOE Type | Y | 10041 | 10040 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10043 | 10042 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 52
|  |  | SOE Type | Y | 10047 | 10046 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10049 | 10048 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 53
|  |  | SOE Type | Y | 10053 | 10052 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10055 | 10054 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 54
|  |  | SOE Type | Y | 10059 | 10058 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10061 | 10060 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 55
|  |  | SOE Type | Y | 10065 | 10064 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10067 | 10066 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 56
|  |  | SOE Type | Y | 10071 | 10070 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10073 | 10072 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 57
|  |  | SOE Type | Y | 10077 | 10076 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10079 | 10078 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 58
|  |  | SOE Type | Y | 10083 | 10082 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10085 | 10084 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 59
|  |  | SOE Type | Y | 10089 | 10088 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10091 | 10090 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 60
|  |  | SOE Type | Y | 10095 | 10094 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10097 | 10096 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 61
|  |  | SOE Type | Y | 10101 | 10100 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10103 | 10102 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 62
|  |  | SOE Type | Y | 10107 | 10106 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10109 | 10108 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 63
|  |  | SOE Type | Y | 10113 | 10112 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10115 | 10114 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 64
|  |  | SOE Type | Y | 10119 | 10118 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10121 | 10120 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 65
|  |  | SOE Type | Y | 10125 | 10124 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10127 | 10126 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 66
|  |  | SOE Type | Y | 10131 | 10130 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10133 | 10132 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 67
|  |  | SOE Type | Y | 10137 | 10136 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10139 | 10138 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 68
|  |  | SOE Type | Y | 10143 | 10142 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10145 | 10144 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 69
|  |  | SOE Type | Y | 10149 | 10148 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10151 | 10150 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 70
|  |  | SOE Type | Y | 10155 | 10154 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10157 | 10156 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 71
|  |  | SOE Type | Y | 10161 | 10160 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10163 | 10162 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 72
|  |  | SOE Type | Y | 10167 | 10166 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10169 | 10168 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 73
|  |  | SOE Type | Y | 10173 | 10172 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10175 | 10174 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 74
|  |  | SOE Type | Y | 10179 | 10178 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10181 | 10180 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 75
|  |  | SOE Type | Y | 10185 | 10184 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10187 | 10186 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 76
|  |  | SOE Type | Y | 10191 | 10190 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10193 | 10192 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 77
|  |  | SOE Type | Y | 10197 | 10196 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10199 | 10198 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 78
|  |  | SOE Type | Y | 10203 | 10202 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10205 | 10204 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 79
|  |  | SOE Type | Y | 10209 | 10208 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10211 | 10210 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 80
|  |  | SOE Type | Y | 10215 | 10214 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10217 | 10216 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 81
|  |  | SOE Type | Y | 10221 | 10220 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10223 | 10222 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 82
|  |  | SOE Type | Y | 10227 | 10226 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10229 | 10228 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 83
|  |  | SOE Type | Y | 10233 | 10232 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10235 | 10234 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 84
|  |  | SOE Type | Y | 10239 | 10238 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10241 | 10240 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 85
|  |  | SOE Type | Y | 10245 | 10244 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10247 | 10246 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 86
|  |  | SOE Type | Y | 10251 | 10250 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10253 | 10252 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 87
|  |  | SOE Type | Y | 10257 | 10256 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10259 | 10258 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 88
|  |  | SOE Type | Y | 10263 | 10262 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10265 | 10264 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 89
|  |  | SOE Type | Y | 10269 | 10268 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10271 | 10270 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 90
|  |  | SOE Type | Y | 10275 | 10274 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10277 | 10276 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 91
|  |  | SOE Type | Y | 10281 | 10280 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10283 | 10282 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 92
|  |  | SOE Type | Y | 10287 | 10286 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10289 | 10288 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 93
|  |  | SOE Type | Y | 10293 | 10292 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10295 | 10294 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 94
|  |  | SOE Type | Y | 10299 | 10298 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10301 | 10300 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 95
|  |  | SOE Type | Y | 10305 | 10304 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10307 | 10306 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 96
|  |  | SOE Type | Y | 10311 | 10310 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10313 | 10312 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 97
|  |  | SOE Type | Y | 10317 | 10316 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10319 | 10318 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 98
|  |  | SOE Type | Y | 10323 | 10322 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10325 | 10324 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 99
|  |  | SOE Type | Y | 10329 | 10328 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10331 | 10330 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 100
|  |  | SOE Type | Y | 10335 | 10334 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10337 | 10336 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 101
|  |  | SOE Type | Y | 10341 | 10340 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10343 | 10342 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 102
|  |  | SOE Type | Y | 10347 | 10346 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10349 | 10348 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 103
|  |  | SOE Type | Y | 10353 | 10352 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10355 | 10354 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 104
|  |  | SOE Type | Y | 10359 | 10358 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10361 | 10360 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 105
|  |  | SOE Type | Y | 10365 | 10364 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10367 | 10366 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 106
|  |  | SOE Type | Y | 10371 | 10370 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10373 | 10372 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 107
|  |  | SOE Type | Y | 10377 | 10376 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10379 | 10378 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 108
|  |  | SOE Type | Y | 10383 | 10382 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10385 | 10384 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 109
|  |  | SOE Type | Y | 10389 | 10388 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10391 | 10390 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 110
|  |  | SOE Type | Y | 10395 | 10394 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10397 | 10396 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 111
|  |  | SOE Type | Y | 10401 | 10400 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10403 | 10402 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 112
|  |  | SOE Type | Y | 10407 | 10406 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10409 | 10408 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 113
|  |  | SOE Type | Y | 10413 | 10412 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10415 | 10414 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 114
|  |  | SOE Type | Y | 10419 | 10418 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10421 | 10420 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 115
|  |  | SOE Type | Y | 10425 | 10424 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10427 | 10426 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 116
|  |  | SOE Type | Y | 10431 | 10430 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10433 | 10432 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 117
|  |  | SOE Type | Y | 10437 | 10436 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10439 | 10438 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 118
|  |  | SOE Type | Y | 10443 | 10442 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10445 | 10444 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 119
|  |  | SOE Type | Y | 10449 | 10448 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10451 | 10450 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 120
|  |  | SOE Type | Y | 10455 | 10454 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10457 | 10456 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 121
|  |  | SOE Type | Y | 10461 | 10460 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10463 | 10462 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 122
|  |  | SOE Type | Y | 10467 | 10466 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10469 | 10468 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 123
|  |  | SOE Type | Y | 10473 | 10472 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10475 | 10474 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 124
|  |  | SOE Type | Y | 10479 | 10478 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10481 | 10480 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 125
|  |  | SOE Type | Y | 10485 | 10484 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10487 | 10486 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 126
|  |  | SOE Type | Y | 10491 | 10490 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10493 | 10492 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 127
|  |  | SOE Type | Y | 10497 | 10496 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10499 | 10498 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
Last 128
|  |  | SOE Type | Y | 10503 | 10502 |  | 1 | INT16U | R |  |  |  | 1005 or greater
|  |  | Date/Time | Y | 10505 | 10504 |  | 4 | DATETIME | R |  |  |  | 1005 or greater
SOE Alarm Threshold
Over Current, L1
|  |  | Pickup Setpoint | Y | 11009 | 11008 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11011 | 11010 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, L1
|  |  | Pickup Setpoint | Y | 11013 | 11012 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11015 | 11014 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Current, L2
|  |  | Pickup Setpoint | Y | 11017 | 11016 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11019 | 11018 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, L2
|  |  | Pickup Setpoint | Y | 11021 | 11020 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11023 | 11022 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Current, L3
|  |  | Pickup Setpoint | Y | 11025 | 11024 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11027 | 11026 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, L3
|  |  | Pickup Setpoint | Y | 11029 | 11028 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11031 | 11030 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Current, L4
|  |  | Pickup Setpoint | Y | 11033 | 11032 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11035 | 11034 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, L4
|  |  | Pickup Setpoint | Y | 11037 | 11036 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11039 | 11038 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Current, Phase5
|  |  | Pickup Setpoint | Y | 11041 | 11040 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11043 | 11042 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, Phase5
|  |  | Pickup Setpoint | Y | 11045 | 11044 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11047 | 11046 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Current, Phase6
|  |  | Pickup Setpoint | Y | 11049 | 11048 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11051 | 11050 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, Phase6
|  |  | Pickup Setpoint | Y | 11053 | 11052 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11055 | 11054 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active1
|  |  | Pickup Setpoint | Y | 11057 | 11056 | kW | 2 | FLOAT32 | RW | 0-110 | 21.12 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11059 | 11058 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active1
|  |  | Pickup Setpoint | Y | 11061 | 11060 | kW | 2 | FLOAT32 | RW | 0-110 | 14.08 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11063 | 11062 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active2
|  |  | Pickup Setpoint | Y | 11065 | 11064 | kW | 2 | FLOAT32 | RW | 0-110 | 21.12 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11067 | 11066 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active2
|  |  | Pickup Setpoint | Y | 11069 | 11068 | kW | 2 | FLOAT32 | RW | 0-110 | 14.08 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11071 | 11070 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active3
|  |  | Pickup Setpoint | Y | 11073 | 11072 | kW | 2 | FLOAT32 | RW | 0-110 | 21.12 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11075 | 11074 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active3
|  |  | Pickup Setpoint | Y | 11077 | 11076 | kW | 2 | FLOAT32 | RW | 0-110 | 14.08 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11079 | 11078 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active4
|  |  | Pickup Setpoint | Y | 11081 | 11080 | kW | 2 | FLOAT32 | RW | 0-110 | 21.12 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11083 | 11082 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active4
|  |  | Pickup Setpoint | Y | 11085 | 11084 | kW | 2 | FLOAT32 | RW | 0-110 | 14.08 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11087 | 11086 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active5
|  |  | Pickup Setpoint | Y | 11089 | 11088 | kW | 2 | FLOAT32 | RW | 0-110 | 21.12 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11091 | 11090 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active5
|  |  | Pickup Setpoint | Y | 11093 | 11092 | kW | 2 | FLOAT32 | RW | 0-110 | 14.08 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11095 | 11094 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active6
|  |  | Pickup Setpoint | Y | 11097 | 11096 | kW | 2 | FLOAT32 | RW | 0-110 | 21.12 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11099 | 11098 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active6
|  |  | Pickup Setpoint | Y | 11101 | 11100 | kW | 2 | FLOAT32 | RW | 0-110 | 14.08 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11103 | 11102 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L1
|  |  | Pickup Setpoint | Y | 11201 | 11200 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11203 | 11202 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L2
|  |  | Pickup Setpoint | Y | 11205 | 11204 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11207 | 11206 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L3
|  |  | Pickup Setpoint | Y | 11209 | 11208 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11211 | 11210 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L4
|  |  | Pickup Setpoint | Y | 11213 | 11212 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11215 | 11214 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L5
|  |  | Pickup Setpoint | Y | 11217 | 11216 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11219 | 11218 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L6
|  |  | Pickup Setpoint | Y | 11221 | 11220 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11223 | 11222 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Frequency
|  |  | Pickup Setpoint | Y | 11225 | 11224 | Hz | 2 | FLOAT32 | RW | 45-65 | 65 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11227 | 11226 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Frequency
|  |  | Pickup Setpoint | Y | 11229 | 11228 | Hz | 2 | FLOAT32 | RW | 45-65 | 45 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11231 | 11230 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Voltage1
|  |  | Pickup Setpoint | Y | 11311 | 11310 | V | 2 | FLOAT32 | RW | 0-440 | 264 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11313 | 11312 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Voltage1
|  |  | Pickup Setpoint | Y | 11315 | 11314 | V | 2 | FLOAT32 | RW | 0-440 | 176 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11317 | 11316 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Voltage2
|  |  | Pickup Setpoint | Y | 11319 | 11318 | V | 2 | FLOAT32 | RW | 0-440 | 264 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11321 | 11320 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Voltage2
|  |  | Pickup Setpoint | Y | 11323 | 11322 | V | 2 | FLOAT32 | RW | 0-440 | 176 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11325 | 11324 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Voltage3
|  |  | Pickup Setpoint | Y | 11327 | 11326 | V | 2 | FLOAT32 | RW | 0-440 | 264 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11329 | 11328 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Voltage3
|  |  | Pickup Setpoint | Y | 11331 | 11330 | V | 2 | FLOAT32 | RW | 0-440 | 176 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11333 | 11332 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Current, L1L2L3
|  |  | Pickup Setpoint | Y | 11335 | 11334 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11337 | 11336 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, L1L2L3
|  |  | Pickup Setpoint | Y | 11339 | 11338 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11341 | 11340 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Current, L4L5L6
|  |  | Pickup Setpoint | Y | 11343 | 11342 | A | 2 | FLOAT32 | RW | 0-500 | 96 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11345 | 11344 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Current, L4L5L6
|  |  | Pickup Setpoint | Y | 11347 | 11346 | A | 2 | FLOAT32 | RW | 0-500 | 64 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11349 | 11348 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active L1L2L3
|  |  | Pickup Setpoint | Y | 11351 | 11350 | kW | 2 | FLOAT32 | RW | 0-330 | 63.36 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11353 | 11352 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active L1L2L3
|  |  | Pickup Setpoint | Y | 11355 | 11354 | kW | 2 | FLOAT32 | RW | 0-110 | 42.24 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11357 | 11356 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Power, Active L4L5L6
|  |  | Pickup Setpoint | Y | 11359 | 11358 | kW | 2 | FLOAT32 | RW | 0-330 | 63.36 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11361 | 11360 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power, Active L4L5L6
|  |  | Pickup Setpoint | Y | 11363 | 11362 | kW | 2 | FLOAT32 | RW | 0-110 | 42.24 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11365 | 11364 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L1L2L3
|  |  | Pickup Setpoint | Y | 11399 | 11398 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11401 | 11400 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Under Power Factor L4L5L6
|  |  | Pickup Setpoint | Y | 11403 | 11402 |  | 2 | FLOAT32 | RW | 0-2 | 0.8 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11405 | 11404 | seconds | 1 | INT16U | RW | 0-60 | 5 |  | 1002 or greater
Over Voltage Unbalance
|  |  | Pickup Setpoint | Y | 11419 | 11418 | % | 2 | FLOAT32 | RW | 0 – 100 | 25 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11421 | 11420 | seconds | 1 | INT16U | RW | 0 – 60 | 5 |  | 1002 or greater
Over Current Unbalance
|  |  | Pickup Setpoint | Y | 11423 | 11422 | % | 2 | FLOAT32 | RW | 0 – 100 | 25 |  | 1002 or greater
|  |  | Pickup Time Delay | Y | 11425 | 11424 | seconds | 1 | INT16U | RW | 0 – 60 | 5 |  | 1002 or greater
SOE Bitmask
|  |  | SOE Bit Mask 1 | Y | 11301 | 11300 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0040 | 0: Disable 1: Enable BIT0：power on BIT1：power off BIT2：set parameter BIT3：clear energy## BIT4：clear SOE BIT5：clear extremum BIT6：Over Current L1 BIT7：Under Current L1 BIT8：Over Current L2 BIT9：Under Current L2 BIT10：Over Current L3 BIT11：Under Current L3 BIT12：Over Current L4 BIT13：Under Current L4 BIT14：Over Current L5 BIT15：Under Current L5 | 1002 or greater
|  |  | SOE Bit Mask 2 | Y | 11302 | 11301 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Current L6 BIT1：Under Current L6 BIT2：Over Power, Active L1 BIT3：Under Power, Active L1 BIT4：Over Power, Active L2 BIT5：Under Power, Active L2 BIT6：Over Power, Active L3 BIT7：Under Power, Active L3 BIT8：Over Power, Active L4 BIT9：Under Power, Active L4 BIT10：Over Power, Active L5 BIT11：Under Power, Active L5 BIT12：Over Power, Active L6 BIT13：Under Power, Active L6 BIT14：Over Power, Reactive L1 BIT15：Under Power, Reactive L1 | 1002 or greater
|  |  | SOE Bit Mask 3 | Y | 11303 | 11302 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Reactive L2 BIT1：Under Power, Reactive L2 BIT2：Over Power, Reactive L3 BIT3：Under Power, Reactive L3 BIT4：Over Power, Reactive L4 BIT5：Under Power, Reactive L4 BIT6：Over Power, Reactive L5 BIT7：Under Power, Reactive L5 BIT8：Over Power, Reactive L6 BIT9：Under Power, Reactive L6 BIT10：Over Power, Apparent L1 BIT11：Under Power, Apparent L1 BIT12：Over Power, Apparent L2 BIT13：Under Power, Apparent L2 BIT14：Over Power, Apparent L3 BIT15：Under Power, Apparent L3 | 1002 or greater
|  |  | SOE Bit Mask 4 | Y | 11304 | 11303 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Apparent L4 BIT1：Under Power, Apparent L4 BIT2：Over Power, Apparent L5 BIT3：Under Power, Apparent L5 BIT4：Over Power, Apparent L6 BIT5：Under Power, Apparent L6 BIT6：Under Power Factor, True L1 BIT7：Under Power Factor, True L2 BIT8：Under Power Factor, True L3 BIT9：Under Power Factor, True L4 BIT10：Under Power Factor, True L5 BIT11：Under Power Factor, True L6 BIT12：Over Frequency BIT13：Under Frequency BIT14：Over Current L1 Total Harmonic Distortion BIT15：Over Current L2 Total Harmonic Distortion | 1002 or greater
|  |  | SOE Bit Mask 5 | Y | 11305 | 11304 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Current L3 Total Harmonic Distortion BIT1：Over Current L4 Total Harmonic Distortion BIT2：Over Current L5 Total Harmonic Distortion BIT3：Over Current L6 Total Harmonic Distortion BIT4：Over Voltage 1 BIT5：Under Voltage 1 BIT6：Over Voltage 2 BIT7：Under Voltage 2 BIT8：Over Voltage 3 BIT9：Under Voltage 3 BIT10：Over Current L1L2L3 BIT11：Under Current L1L2L3 BIT12：Over Current L4L5L6 BIT13：Under Current L4L5L6 BIT14：Over Power, Active L1L2L3 BIT15：Under Power, Active L1L2L3 | 1002 or greater
|  |  | SOE Bit Mask 6 | Y | 11306 | 11305 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Power, Active L4L5L6 BIT1：Under Power, Active L4L5L6 BIT2：Over Power, Reactive L1L2L3 BIT3：Under Power, Reactive L1L2L3 BIT4：Over Power, Reactive L4L5L6 BIT5：Under Power, Reactive L4L5L6 BIT6：Over Power, Apparent L1L2L3 BIT7：Under Power, Apparent L1L2L3 BIT8：Over Power, Apparent L4L5L6 BIT9：Under Power, Apparent L4L5L6 BIT10：Under Power Factor, True L1L2L3 BIT11：Under Power Factor, True L4L5L6 BIT12：Over Voltage Total Harmonic Distortion 1 BIT13：Over Voltage Total Harmonic Distortion 2 BIT14：Over Voltage Total Harmonic Distortion 3 BIT15：Over Voltage Unbalance | 1002 or greater
|  |  | SOE Bit Mask 7 | Y | 11307 | 11306 |  | 1 | BITMAP | RW | 0x0000 – 0xFFFF | 0x0000 | 0: Disable 1: Enable BIT0：Over Current Unbalance 1 BIT1：Over Current Unbalance 2 BIT2：clear demand | 1002 or greater
Clear Command
|  |  | Clear Energy | Y | 60001 | 60000 |  | 1 | INT16U | W |  | 0x55A0 |  | 1002 or greater
|  |  | Clear Demand | Y | 60003 | 60002 |  | 1 | INT16U | W |  | 0x55A2 |  | 1002 or greater
|  |  | Clear SOE | Y | 60004 | 60003 |  | 1 | INT16U | W |  | 0x55A4 |  | 1002 or greater

## Data Types
Data Type | Description | Native Range | N/A Value | Notes
UTF8 | Alphanumeric | 0-3 bytes | 0x00
INT16 | Signed Integer, 16 bits | -32,768 - 32,767 | 0x8000
INT16U | Unsigned Integer, 16 bits | 0 - 65,535 | 0xFFFF
INT32 | Signed Integer, 32 bits | -2,147,483,648 – 2,147,483,647 | 0x80000000
INT32U | Unsigned Integer, 32 bits | 0 - 4,294,967,295 | 0xFFFFFFFF
INT64 | Signed Integer, 64 bits |  | 0x8000000000000000
FLOAT32 | Floating Point, 32 bits | +/- 1*10^38 | 0xFFC00000
FLOAT64 | Floating Point, 64 bits | +/-1.798*10^308 | 0xFFF8000000000000
BITMAP |  |  | 0x8000 Example for a status bitmap 1 register long. | For status bitmaps that are multiple registers long, the most significant bit will be set to indicate the entire bitmap is N/A.This does not apply to configuration bitmaps. So, in setup commands that include a bitmap as a parameter, the user must always include the desired value for these bitmaps.
DATETIME | DateTime | 1/1/2000 – 12/31/2127 | 0xFFFFFFFFFFFFFFFF | DateTime coding format using 4 words as per IEC 870-5-4 Word 1 b0-b6: Year (0 - 127) b7-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved Word 3 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 4 b0-b15: Millisecond (0 - 59999)
DATE | Date |  | 0xFFFFFFFF | Word 1 b0-b7: Year (0 - 99) b8-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved
TIME | Time |  | 0xFFFFFFFF | Word 1 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 2 b0-b15: Millisecond (0 - 59999)
4Q FP PF | Four Quadrant Floating Point Power Factor | -2 - 2 | 0xFFC00000 | Power factor values are specially encoded floating point values. Angle of complex power = power factor register value 0° = 1 90° = 0 180° = -1 270° = 2 Q1: 0 < x < 1 Q2: -2 < x < -1 Q3: -1 < x < 0 Q4: 1 < x < 2 Pseudo code to decode PF Value if (rigVal > 1) { PF_Val = 2 - regVal; PF is leading } else if (regVal < -1) { PF_Val = -2-regVal PF is leading } else if ( abs(regVal) equals 1 ) { PF_Val = regVal PF is at unity } else { PF_Val = regVal PF is lagging }
SOE Type | Sequence of event type |  |  | 01 = power on 02 = power off 03 = set parameter 04 = clear energy## 05 = clear SOE 06 = clear extremum 07 = Over Voltage 08 = Under Voltage 09 = Over Current L1 10 = Under Current L1 11 = Over Current L2 12 = Under Current L2 13 = Over Current L3 14 = Under Current L3 15 = Over Current L4 16 = Under Current L4 17 = Over Current L5 18 = Under Current L5 19 = Over Current L6 20 = Under Current L6 21 = Over Power, Active L1 22 = Under Power, Active L1 23 = Over Power, Active L2 24 = Under Power, Active L2 25 = Over Power, Active L3 26 = Under Power, Active L3 27 = Over Power, Active L4 28 = Under Power, Active L4 29 = Over Power, Active L5 30 = Under Power, Active L5 31 = Over Power, Active L6 32 = Under Power, Active L6 33 = Over Power, Reactive L1 34 = Under Power, Reactive L1 35 = Over Power, Reactive L2 36 = Under Power, Reactive L2 37 = Over Power, Reactive L3 38 = Under Power, Reactive L3 39 = Over Power, Reactive L4 40 = Under Power, Reactive L4 41 = Over Power, Reactive L5 42 = Under Power, Reactive L5 43 = Over Power, Reactive L6 44 = Under Power, Reactive L6 45 = Over Power, Apparent L1 46 = Under Power, Apparent L1 47 = Over Power, Apparent L2 48 = Under Power, Apparent L2 49 = Over Power, Apparent L3 50 = Under Power, Apparent L3 51 = Over Power, Apparent L4 52 = Under Power, Apparent L4 53 = Over Power, Apparent L5 54 = Under Power, Apparent L5 55 = Over Power, Apparent L6 56 = Under Power, Apparent L6 57 = Under Power Factor, True L1 58 = Under Power Factor, True L2 59 = Under Power Factor, True L3 60 = Under Power Factor, True L4 61 = Under Power Factor, True L5 62 = Under Power Factor, True L6 63 = Over Frequency 64 = Under Frequency 65 = Over Voltage Total Harmonic Distortion 66 = Over Current L1 Total Harmonic Distortion 67 = Over Current L2 Total Harmonic Distortion 68 = Over Current L3 Total Harmonic Distortion 69 = Over Current L4 Total Harmonic Distortion 70 = Over Current L5 Total Harmonic Distortion 71 = Over Current L6 Total Harmonic Distortion 73 = clear demand 74 = Upgrade

## References
References
Y | Yes, data item is supported as standard feature
O | Yes, item is supported as an option
P | Data item is supported but is private
R | An R in the Access column means the register may be read.
W | A W in the Access column means the register may be written.
C | A C in the Access column means the register may only be written via a setup command.
ASCII Characters | 0 1 2 3 4 5 6 7 8 9 A B C D E F
0 NUL SOH STX ETX EOT ENQ ACK BEL BS HT LF VT FF CR SO SI
1 DLE DC1 DC2 DC3 DC4 NAK SYN ETB CAN EM SUB ESC FS GS RS US
2 SP ! " # $ % & ' ( ) * + , – . /
3 0 1 2 3 4 5 6 7 8 9 : ; < = > ?
4 @ A B C D E F G H I J K L M N O
5 P Q R S T U V W X Y Z [ \ ] ^ _
6 ` a b c d e f g h i j k l m n o
7 p q r s t u v w x y z { ¦ } ~ DEL
Abbreviations | PRODUCTION_HISTORY - PROD_HIST
APPLIED – APLY
READING – READ
SHIFT – SFT
PRESENT – PRES
PREVIOUS – PREV
DURATION – DUR
NOMINAL – NOM
PRIMARY – PRI
SECONDARY – SEC
WIRECORRECT – SWC
FIELD_CAL_CT_RATIO_PH_A - FLD_CAL_CT_A
FIELD_CAL_VT_RATIO_PH_A - FLD_CAL_VT_A
R_METER_SETUP_ENERGY_OUT_PW01 - R_METER_SETUP_ENERGY_ PW01
R_METER_SETUP_ENERGY_OUT_DIGOUT_01 - R_METER_SETUP_ENERGY_DO_01
RS485 – 485
DIAG – DIA
DIAGNOSTIC – DIA
BEHAVIORAL – BEH
REGISTER – REG
OVER – OVR
UNDER – UND
CURRENT – CUR
VOLTAGE – VOLT
LEVEL – LVL
TYPE – TYP
ENABLE_PRI – EP
VOLT_LL – VLL
VOLT_LN – VLN
DATALOG – DLG
LEADING_PF_TRUE – LEDPFT
LAGGING_PF_TRUE – LAGPGT
LEADING_PF_DISP – LEDPFD
LAGGING_PF_DISP – LAGPGD
DEMAND – DEM
1S_STD – 1ST
TYPE_LEVEL – TL
UNBALANCE – UNB
ENERGY_ACCUM – ENG_ACC
ENERGY – ENG
INTERVAL - INT
Passwords shall be 4 alphanumeric characters long.
Passwords shall always be entered and setup left-to-right.
Characters shall be selected from the following subset of US ASCII printable characters:
Character Decimal Description
# 35 NUMBER SIGN
$ 36 DOLLAR SIGN
% 37 PERCENT SIGN
& 38 AMPERSAND
* 42 ASTERISK
+ 43 PLUS SIGN
- 45 MINUS SIGN
/ 47 SLASH
0 48 DIGIT ZERO
1 49 DIGIT ONE
2 50 DIGIT TWO
3 51 DIGIT THREE
4 52 DIGIT FOUR
5 53 DIGIT FIVE
6 54 DIGIT SIX
7 55 DIGIT SEVEN
8 56 DIGIT EIGHT
9 57 DIGIT NINE
? 63 QUESTION MARK
@ 64 COMMERCIAL AT SIGN
A 65 CAPITAL LETTER A
B 66 CAPITAL LETTER B
C 67 CAPITAL LETTER C
D 68 CAPITAL LETTER D
E 69 CAPITAL LETTER E
F 70 CAPITAL LETTER F
G 71 CAPITAL LETTER G
H 72 CAPITAL LETTER H
I 73 CAPITAL LETTER I
J 74 CAPITAL LETTER J
K 75 CAPITAL LETTER K
L 76 CAPITAL LETTER L
M 77 CAPITAL LETTER M
N 78 CAPITAL LETTER N
O 79 CAPITAL LETTER O
P 80 CAPITAL LETTER P
Q 81 CAPITAL LETTER Q
R 82 CAPITAL LETTER R
S 83 CAPITAL LETTER S
T 84 CAPITAL LETTER T
U 85 CAPITAL LETTER U
V 86 CAPITAL LETTER V
W 87 CAPITAL LETTER W
X 88 CAPITAL LETTER X
Y 89 CAPITAL LETTER Y
Z 90 CAPITAL LETTER Z
a 97 SMALL LETTER a
b 98 SMALL LETTER b
c 99 SMALL LETTER c
d 100 SMALL LETTER d
e 101 SMALL LETTER e
f 102 SMALL LETTER f
g 103 SMALL LETTER g
h 104 SMALL LETTER h
i 105 SMALL LETTER i
j 106 SMALL LETTER j
k 107 SMALL LETTER k
l 108 SMALL LETTER l
m 109 SMALL LETTER m
n 110 SMALL LETTER n
o 111 SMALL LETTER o
p 112 SMALL LETTER p
q 113 SMALL LETTER q
r 114 SMALL LETTER r
s 115 SMALL LETTER s
t 116 SMALL LETTER t
u 117 SMALL LETTER u
v 118 SMALL LETTER v
w 119 SMALL LETTER w
x 120 SMALL LETTER x
y 121 SMALL LETTER y
z 122 SMALL LETTER z

## Legal Information
Legal Information
The information provided in this document contains general descriptions, technical characteristics and/or recommendations related to products/solutions. This document is not intended as a substitute for a detailed study or operational and site-specific development or schematic plan. It is not to be used for determining suitability or reliability of the products/solutions for specific user applications. It is the duty of any such user to perform or have any professional expert of its choice (integrator, specifier or the like) perform the appropriate and comprehensive risk analysis, evaluation and testing of the products/solutions with respect to the relevant specific application or use thereof. The Schneider Electric brand and any trademarks of Schneider Electric SE and its subsidiaries referred to in this document are the property of Schneider Electric SE or its subsidiaries. All other brands may be trademarks of their respective owner. This document and its content are protected under applicable copyright laws and provided for informative use only. No part of this document may be reproduced or transmitted in any form or by any means (electronic, mechanical, photocopying, recording, or otherwise), for any purpose, without the prior written permission of Schneider Electric. Schneider Electric does not grant any right or license for commercial use of the document or its content, except for a non-exclusive and personal license to consult it on an "as is" basis. Schneider Electric reserves the right to make changes or updates with respect to or in the content of this document or the format thereof, at any time without notice. To the extent permitted by applicable law, no responsibility or liability is assumed by Schneider Electric and its subsidiaries for any errors or omissions in the informational content of this document, as well as any non-intended use or misuse of the content thereof.