## Vigilohm IM400 Mapping Sheet
Vigilohm IM400 Translator Details
PC -Logging | Log Interval | ManagerLabel | ModuleLabel | RegisterLabel | Name | IM400N/IM400/IM400C/IM400L | IM400THRN/IM400THR/ IM400LTHR | ModbusAddress | Format | IONHandle | RequestType | Mask | Scale | Multiplier | EnumName | NumberOfRegisters
|  | Factory Information | Factory 1 | FAC1 DeviceType | FAC1 DeviceType | Y | Y | 400101 | UINT16 | 4864 | R
|  | Factory Information | Factory 1 | FAC1 Compliance |  | Y | Y |  |  | 4865 | R
|  | Factory Information | Factory 1 | FAC1 Options |  | Y | Y |  |  | 4866 | R
|  | Factory Information | Factory 1 | FAC1 Revision |  | Y | Y |  |  | 4867 | R
|  | Factory Information | Factory 1 | FAC1 SerialNum | FAC1 SerialNum | Y | Y | 400209 | ASCII | 4868 | R |  |  |  |  | 5
|  | Factory Information | Factory 1 | FAC1 ION Version |  | Y | Y |  |  | 30510 | R
|  | Factory Information | Factory 1 | FAC1 Template |  | Y | Y |  |  | 4989 | R
|  | Factory Information | Factory 1 | FAC1 Device Name | FAC1 Device Name | Y | Y | 400141 | ASCII | 22340 | R |  |  |  |  | 20
|  | Factory Information | Factory 1 | FAC1 FW Rev RS | FAC1 FW Rev RS | Y | Y | 400551 | ASCII | 30131 | R |  |  |  |  | 6
|  | Clocks | Clock | CL1 Universal Time | CL1 Universal Time | Y | Y | 400308 | DateTime3_IEC870 | 159383809 | R |  |  |  |  | 4
|  | Clocks | Clock | CL1 Local Time | CL1 Local Time | Y | Y | 400308 | DateTime3_IEC870 | 159383810 | R |  |  |  |  | 4
|  | Clocks | Clock | CL1 Year | CL1 Year | Y | Y | 400301 | UINT16 | 159383811 | R |  |  |  |  | 1
|  | Clocks | Clock | CL1 Month | CL1 Month | Y | Y | 400302 | UINT16 | 159383812 | R |  |  |  |  | 1
|  | Clocks | Clock | CL1 Day | CL1 Day | Y | Y | 400303 | UINT16 | 159383813 | R |  |  |  |  | 1
|  | Clocks | Clock | CL1 Hour | CL1 Hour | Y | Y | 400304 | UINT16 | 159383814 | R |  |  |  |  | 1
|  | Clocks | Clock | CL1 Minute | CL1 Minute | Y | Y | 400305 | UINT16 | 159383815 | R |  |  |  |  | 1
|  | Clocks | Clock | CL1 Second | CL1 Second | Y | Y | 400306 | UINT16 | 159383816 | R |  |  |  |  | 1
|  | Clocks | Clock | CL1 Millisecond | CL1 Millisecond | Y | Y | 400307 | UINT16 | 159383817 | R |  |  |  |  | 1
|  | Alarms | Alarm Status | Insulation Status Alarm | Insulation Status Alarm | Y | Y | 401111 | UINT32 | 153092097 | R | 0x0001
|  | Alarms | Alarm Status | Insulation Status Pre-Alarm | Insulation Status Pre-Alarm | Y | Y | 401111 | UINT32 | 160432386 | R | 0x0002
|  | Alarms | Alarm Status | Transient Alarm | Transient Alarm | Y | Y | 401111 | UINT32 | 160432387 | R | 0x0004
|  | Alarms | Alarm Status | Insulation Acknowledged Alarm | Insulation Acknowledged Alarm | Y | Y | 401111 | UINT32 | 160432388 | R | 0x0008
|  | Status | Product Status | Product Status | Product Status | Y | Y | 401111 | UINT32 | 161480962 | R | 0x1000000
|  | Status | Product Status | Self test | Self test | Y | Y | 401111 | UINT32 | 161480964 | R | 0x1000
|  | Status | Product Status | First measurement | First measurement | Y | Y | 401111 | UINT32 | 161480965 | R | 0x0100
|  | Status | Product Status | Network Filter | Network Filter | Y | Y | 403009 | UINT16 | 161480961 | R
|  | Status | Product Status | Network Frequency | Network Frequency | Y | Y | 403010 | UINT16 | 161480967 | R
|  | Status | Product Status | Transformer Primary DC Resistance | Transformer Primary DC Resistance | Y | Y | 403037 | UINT16 | 161480971 | R |  | 1000
|  | Status | Product Status | Number of Transformer | Number of Transformer | Y | Y | 403038 | UINT16 | 161480972 | R
|  | Status | Product Status | Open Circuit Detection | Open Circuit Detection | Y | Y | 403027 | UINT16 | 161480973 | R
|  | Status | Product Status | Fault Locating | Fault Locating | Y | Y | 403028 | UINT16 | 161480974 | R
|  | Status | Product Status | High Resistance Grounding | High Resistance Grounding | Y | Y | 403031 | UINT32 | 161480975 | R |  | 1000
|  | Status | Product Status | High Voltage Plate | High Voltage Plate | Y | Y | 403020 | UINT16 | 161480976 | R
|  | Status | Product Status | Alarm Relay Acknowledge | Alarm Relay Acknowledge | Y | Y | 403024 | UINT16 | 161480977 | R
|  | Status | Product Status | Self test with Relay | Self test with Relay | Y | Y | 403030 | UINT16 | 161480978 | R
|  | Status | Product Status | Insulation Alarm Relay | Insulation Alarm Relay | Y | Y | 403002 | UINT16 | 161480979 | R
|  | Status | Product Status | Insulation Pre-Alarm Relay | Insulation Pre-Alarm Relay | Y | Y | 403041 | UINT16 | 161480980 | R
|  | Status | System Status | System Status | System Status | Y | Y | 401111 | UINT32 | 161481473 | R | 0x40074000
|  | Status | System Status | Injection Disconnected | Injection Disconnected | Y | Y | 401111 | UINT32 | 153092103 | R | 0x10000
|  | Status | System Status | Injection Disabled | Injection Disabled | Y | Y | 401111 | UINT32 | 161481475 | R | 0x4000
|  | Status | System Status | Over limit capacitance | Over limit capacitance | Y | Y | 401111 | UINT32 | 161481476 | R | 0x20000
|  | Status | System Status | Over Voltage | Over Voltage | Y | Y | 401111 | UINT32 | 161481477 | R | 0x40000
|  | Status | System Status | HV1 and HV2 open | HV1 and HV2 open | Y | Y | 401111 | UINT32 | 161481478 | R | 0x40000000
|  | Diagnostics | Power Cycle Count | Cycle Count | Cycle Count | Y | Y | NA | HandledByPlugin | 162529537 | R
|  | Diagnostics | Product Model | Product Model | Product Model | Y | Y | 400161 | ASCII | 162530049 | R |  |  |  |  | 20
Monitoring Log | 900 | Monitoring | Resistance | Resistance | Resistance kohms | Y | Y | 401021 | F32-4321 | 181403649 | R |  | 1000
|  | Monitoring | Resistance | Resistance Equality | Resistance Equality | Y | Y | 401027 | UINT16 | 163578114 | R |  |  |  | REquality
Monitoring Log | 900 | Monitoring | Capacitance | Capacitance | Capacitance | Y |  | 401023 | F32-4321 | 163578625 | R |  |  | 1000000
|  | Monitoring | Capacitance | Capacitance Equality | Capacitance Equality | Y |  | 401028 | UINT16 | 163578626 | R |  |  |  | REquality
|  | Monitoring | Injection Status | Injection Status | Injection Status | Y | Y | 401032 | UINT16 | 163579649 | R
|  | Settings | Global Settings | Insulation Alarm Threshold kohms | Insulation Alarm Threshold kohms | Y | Y | 403003 | UINT32 | 182452226 | RW
|  | Settings | Global Settings | Insulation Pre-Alarm Threshold | Insulation Pre-Alarm Threshold | Y | Y | 403005 | UINT32 | 164626690 | RW
|  | Settings | Global Settings | Alarm Delay | Alarm Delay | Y | Y | 403008 | UINT16 | 164626691 | RW |  |  |  | AlarmDelay
|  | Settings | Global Settings | Insulation Pre-Alarm Delay | Insulation Pre-Alarm Delay | Y | Y | 403022 | UINT16 | 164626693 | RW |  |  |  | AlarmDelay
|  | Settings | Global Settings | Product Name | Product Name | Y | Y | 400141 | ASCII | 164626694 | RW |  |  |  |  | 20
|  | PeriodicTimer Modules | Periodic Tmr 900 1 | PT1 Trigger |  | Y | Y |  |  | 165675011 | R
|  | PeriodicTimer Modules | Periodic Tmr 900 1 | PT1 Period |  | Y | Y |  |  | 165675009 | R
|  | PeriodicTimer Modules | Periodic Tmr 900 1 | PT1 Sync Mode |  | Y | Y |  |  | 165675010 | R
|  | Feedback Modules | Feedback 1 | FBK1 Pulse Out |  | Y | Y |  |  | 166723585 | R
|  | DataRecorder Modules | Monitoring Log | RE1 Data Log |  | Y | Y |  |  | 167772161 | R
|  | DataRecorder Modules | Monitoring Log | RE1 Log State |  | Y | Y |  |  | 167772162 | R
|  | DataRecorder Modules | Monitoring Log | RE1 Records Left |  | Y | Y |  |  | 167772163 | R
|  | DataRecorder Modules | Monitoring Log | RE1 Record Complete |  | Y | Y |  |  | 167772164 | R
|  | DataRecorder Modules | Monitoring Log | RE1 Depth |  | Y | Y |  |  | 167772165 | R
|  | DataRecorder Modules | Monitoring Log | RE1 RecordMode |  | Y | Y |  |  | 167772166 | R
|  | DataRecorder Modules | Monitoring Log | RE1 Staleness Threshold |  | Y | Y |  |  | 167772167 | R
|  | DataRecorder Modules | Monitoring Log | RE1 Staleness Action |  | Y | Y |  |  | 167772168 | R
|  | Labels | Cause and Effect Ion Labels | Unknown |  | Y | Y |  |  | 10000 | R
|  | Labels | Cause and Effect Ion Labels | Preventive Insulation Status Alarm |  | Y | Y |  |  | 10001 | R
|  | Labels | Cause and Effect Ion Labels | Insulation Status Alarm |  | Y | Y |  |  | 10002 | R